## Sheet1
Issue/Observation | Resolution for Approved ADS Case | Timeline | Assignment | Recommendations | Persons Responsible | Expected completions date | Status
Some resources show different capacities in the PF and L&R data | To be decided by PCDS. To be discussed at 8-3-2022 PCDS meeting | 08-03: Decision at PCDS If changes needed, staff to implement by 08-12 |  | If close - no action, If grossly different - VAR Margin Ratio to reduce Pmax. If CC gen has duct burner, use PF Pmax or Nameplate | Jon, Tyler, BK, Bhavana, Stan | 2022-08-10 | In Progress. PCDS approved methodology for implementing capacities at 08-03-2022 meeting. Staff will implement. Data input expected to be complete by 08-10-2022.
The current case includes unserved energy (USE) for WACM, PSCO, CFE. The amount is very small (maximum hourly unserved load less than 6%, annual unserved load less than 0.01%) | Eliminate all unserved load |  |  | Validate that min up/down times, available generation, unit commitment are correct for each BA ) Transmission constraints. Look into ESL… CFE combined cylce plant 2 CTs and ST unit, only one CT in PCM case. Check CFE Thermal fuels | BK, Jon, Tyler | 2022-08-10 | Complete. The latest run increased USE. Per Hitachi, USE for those hours is due to insufficient resources in that hour including forced outages. Staff position is that the magnitude of USE is acceptable. Other stakeholders believe that USE should be zero.
The case includes significant congestion on Transmission Path 83, Path 1, and Path 42 (over 7,000 hours) | Explaination for high unserved load hours |  |  |  | Jon, Tyler, BK, Bhavana, Stan | 2022-08-10 | In Progress. Congestion in the case was scheduled but not discussed at 08-03-2022 PCDS. Current ratings for Path 42 are in the case.
Address the modeling of MATLB Phase Shifter (Path 83) (May need to be modeled to help flow to Alberta) | What is the desired resolution--explanation? |  |  | Not currently modeled in PF or PCM, model as phase shifter, Check with Nick. Update type -4 PS to type 4 in PCM. Tell Jin | Jon, Tyler | 2022-08-10 | Complete.
Alberta CO2 price is twice the value of other areas | Confirm with Alberta that the value is correct or change it to the value for other parts of the Western Interconnection | 08-03: Decision at PCDS If changes needed, staff to implement by 08-05 | Contact Alberta to validate CO2 price (who?) | Do we change it to California, BC, or other lower value? Account for Alberta Offsets, canadian dollars/exchange rate | Stan | 2022-08-05 | Complete. PCDS decided at 08-03-2022 PCDS meeting to keep the current Alberta CO2 values in the case, as they have been verified by AESO. WECC will also publish change cases with other values for stakeholders who want to use them.
LADWP non-firm DSM is much higher than other DSM in the SCE area | Either confirm with LADWP that values are correct or adjust to SCE-area values |  | Follow up with LADWP to validate DSM values (who?) | Reach out to LADWP, they say keep as is | Tyler | 2022-08-05 | Complete: LADWP has verified that this is correct--no changes.
Some 230 kv and above lines and transformers are not monitored | Monitor the lines and transformers in the case |  | Update the case to monitor all 230 kv and above lines and transformers |  | Jon | 2022-08-05 | Complete. WECC has verified that running a case with all 230 kv and above facilities monitored increases the run time significantly, if it is able to run at all. WECC tried to run a case with these facilities monitored, and the case crashed. The approved case will not include monitoring for the selected 230 kv and above facilities because the WECC case will not run with it. However, WECC will provide a change case for stakeholders who would like to apply it (Currenlty on the PCDS Team Site).
The daily operating range for BPA hydro units is three times that of the weekly operating ranges. (What is the effect on the dispatch?) | No additional changes needed |  |  | Already updated in case. Check inputs. It is what it is | BK, Bhavana | 2022-08-05 | Complete. BPA operating ranges have been verified in the case.
Clean out unreferenced DAT files, bus connection problems and unit IDs. | Unneeded files removed from the case |  | Remove unneeded files (who?) | Previous efforts to do this created issues with the case not solving. It may be acceptable to leave the files in the case. Unique bus number and IDs. Check to make sure they are in the Distrubution Table | Jon, BK | 2022-08-10 | In Progress. Files will be removed by 08-10-2022.
Many LMPs appear to be very high | Explain high LMPs |  |  | Look into transmission congestion and unserved load | BK, Stan | 2022-08-10 | Complete. High LMPs appear to be the result of congestion and USE. They are the result of the case based on inputs.
Investigate the Operation of Phase Shifters, Pump Storage, Batteries, etc. | Correct Path 83 phase shifter to MATLB |  | Clarify this issue in relation to the Alberta issue |  | BK, Jon, Tyler | 2022-08-10 | Complete. Phase shifer operations, pump storage performance and battery performance are the result of the case based on inputs.
Exports from BC to Alberta are very high | Explain why BC-to-Alberta exports are high |  | Validate the load/resource balance for Alberta (who) |  | Stan, Jon, BK, Bhavana | 2022-08-10 | Complete. Concern is the result of Alberta CO2 price. PCDS decided at 08-03-2022 PCDS meeting to keep the current Alberta CO2 values in the case, as they have been verified by AESO. WECC will also publish change cases with other values for stakeholders who want to use them.
Northwest to BC, Path 3, flows into BC |  |  |  | Investigate | Stan, Tyler, Jon, BK, Bhavana | 2022-08-05 | Complete. Concern is the result of the hydro energies in the monthly variable schedule in BC. The data is the best we have. There is a slight impact from the AESO CO2 prices.