## Sheet1
WECC Interconnection Daily Status Report
Date: | 2024-10-01
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 108.5 |  | 66 |  | 59.5 | 86.7
Low: |  | 70 |  | 37 |  | 48.8 | 68.3
Conditions: |  | Sunny |  | Partly Cloudy |  | Overcast | Partly Cloudy
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 63433.3151 | 18 | 9057.988 |  | 4123.1655 | 19946.67
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 22743.5357 | 17 | 1723 |  | 1478.3298 | 8734.09
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 46533.8878 | 18 | 4446.56 |  | 3387.56 | 16300.98
Includes CFE, CISO & LDWP
WI TOTAL |  | 132386.7588 | 18 | 15253.548 |  | 8051.18 | 43543.74
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 66628 | 17 | 13302
SRSG |  | 23025 | 16 | 4072
CAMX* |  | 42144 | 17 | 6395
WI TOTAL |  | 131634 | 17 | 23318
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW |  | 700 MW
|  |  | W>E | 1200 MW |  | 850 MW
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW |  | 1900 MW
|  |  | S>N | 3000 MW
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration
2024-09-30 | WACM | Path 36 |  | 4 | 9

## Map
Weather Information
Calgary, AB
High (F) | 66
Low (F) | 37
Partly Cloudy |  | 63433.3151 | 69.94% | 69.94% | 30.06% | 63,433 MW
|  | 22743.5357 | 76.76% | 76.76% | 23.24% | 22,744 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 79.9 | 46533.8878 | 75.79% | 75.79% | 24.21% | 46,534 MW
Low (F) | 52
Sunny
Billings, MT
High (F) | 74.1
Low (F) | 34
Sunny
Loveland, CO
High (F) | 72
Low (F) | 37.2
Sunny
Los Angeles, CA
High (F) | 69.1
Low (F) | 59.5
Partly Cloudy
Phoenix, AZ
High (F) | 111.7
Low (F) | 79.2
Sunny
Salt Lake City, UT
High (F) | 80.4
Low (F) | 42.1
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
63,433 MW
22,744 MW
46,534 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend