## Sheet1
WECC Interconnection Daily Status Report
Date: | 2024-10-02
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 110.5 |  | 58.5 |  | 57 | 83.1
Low: |  | 72.3 |  | 37.9 |  | 47.1 | 58.5
Conditions: |  | Sunny |  | Sunny |  | Partly Cloudy | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 63833.8879 | 18 | 13298.705 |  | 4149.2027 | 20609.76
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 21498.0588 | 17 | 1788 |  | 1309.68 | 8995.66
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 49757.5859 | 18 | 4257.68 |  | 3646.68 | 16912.91
Includes CFE, CISO & LDWP
WI TOTAL |  | 134785.2505 | 18 | 19370.385 |  | 8341.467 | 46257.33
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 67400 | 17 | 14271
SRSG |  | 23453 | 16 | 4214
CAMX* |  | 46366 | 17 | 5993
WI TOTAL |  | 136960 | 17 | 23715
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW |  | 0 MW | 2024-10-04
|  |  | W>E | 1200 MW |  | 0 MW | 2024-10-04
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW |  | 1200 MW | 2024-10-05
|  |  | S>N | 3000 MW
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 58.5
Low (F) | 37.9
Sunny |  | 63833.8879 | 70.38% | 70.38% | 29.62% | 63,834 MW
|  | 21498.0588 | 72.56% | 72.56% | 27.44% | 21,498 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 67.3 | 49757.5859 | 81.04% | 81.04% | 18.96% | 49,758 MW
Low (F) | 48.2
Partly Cloudy
Billings, MT
High (F) | 79.3
Low (F) | 44.6
Sunny
Loveland, CO
High (F) | 91.9
Low (F) | 44.8
Sunny
Los Angeles, CA
High (F) | 69.1
Low (F) | 60.6
Partly Cloudy
Phoenix, AZ
High (F) | 106.5
Low (F) | 79.9
Sunny
Salt Lake City, UT
High (F) | 84
Low (F) | 48.6
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
63,834 MW
21,498 MW
49,758 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend