## Sheet1
WECC Interconnection Daily Status Report
Date: | 2024-12-17
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 62.4 |  | 12.7 |  | 44.2 | 54.5
Low: |  | 46.6 |  | 5 |  | 39.7 | 50.2
Conditions: |  | Partly Cloudy |  | Partly Cloudy |  | Moderate rain | Patchy rain nearby
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 71097.6454 | 18 | 10578.7005 |  | 4621.347 | 17754
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 13813.7992 | 7 | 1781 |  | 897.8969 | 11350.18
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 34004.2681 | 19 | 4934.9 |  | 2796.9 | 23536.27
Includes CFE, CISO & LDWP
WI TOTAL |  | 118136.0359 | 18 | 17122.2705 |  | 7600.6205 | 52296.45
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 75783 | 18 | 14901
SRSG |  | 14183 | 7 | 3884
CAMX* |  | 34529 | 18 | 4847
WI TOTAL |  | 123647 | 18 | 23595
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 12.7
Low (F) | 5
Partly Cloudy |  | 71097.6454 | 74.53% | 74.53% | 25.47% | 71,098 MW
|  | 13813.7992 | 55.71% | 55.71% | 44.29% | 13,814 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 52 | 34004.2681 | 64.65% | 64.65% | 35.35% | 34,004 MW
Low (F) | 44.8
Moderate rain
Billings, MT
High (F) | 42.1
Low (F) | 25
Moderate snow
Loveland, CO
High (F) | 55.4
Low (F) | 25.5
Partly Cloudy
Los Angeles, CA
High (F) | 75.6
Low (F) | 50.5
Sunny
Phoenix, AZ
High (F) | 74.1
Low (F) | 40.6
Sunny
Salt Lake City, UT
High (F) | 40.6
Low (F) | 25
Cloudy
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
71,098 MW
13,814 MW
34,004 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend