## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-01-10
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 63.3 |  | 33.4 |  | 42.3 | 35.6
Low: |  | 46.2 |  | 23 |  | 38.3 | 29.8
Conditions: |  | Sunny |  | Moderate or heavy snow showers |  | Moderate rain | Moderate or heavy snow showers
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 69846.5073 | 9 | 14807.34 |  | 4533.206 | 17778.21
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 14697.4674 | 7 | 796 |  | 955.3354 | 10942.14
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 30756.8222 | 19 | 4418.36 |  | 2526.36 | 20704.92
Includes CFE, CISO & LDWP
WI TOTAL |  | 112957.5612 | 8 | 20296.7233 |  | 7955.8593 | 48896.27
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 73853 | 18 | 15539
SRSG |  | 13158 | 7 | 3779
CAMX* |  | 31396 | 9 | 5972
WI TOTAL |  | 117221 | 18 | 24907
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 33.4
Low (F) | 23
Moderate or heavy snow showers |  | 69846.5073 | 73.22% | 73.22% | 26.78% | 69,847 MW
|  | 14697.4674 | 59.27% | 59.27% | 40.73% | 14,697 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 48 | 30756.8222 | 58.48% | 58.48% | 41.52% | 30,757 MW
Low (F) | 36.9
Moderate rain
Billings, MT
High (F) | 35.8
Low (F) | 16
Overcast
Loveland, CO
High (F) | 39.2
Low (F) | 7.5
Sunny
Los Angeles, CA
High (F) | 68.5
Low (F) | 50.4
Sunny
Phoenix, AZ
High (F) | 62.8
Low (F) | 38.7
Sunny
Salt Lake City, UT
High (F) | 34
Low (F) | 14.9
Partly Cloudy
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
69,847 MW
14,697 MW
30,757 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend