## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-01-16
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 63.1 |  | 40.5 |  | 44.4 | 57
Low: |  | 42.8 |  | 21.7 |  | 36 | 28.8
Conditions: |  | Sunny |  | Sunny |  | Cloudy | Partly Cloudy
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 71646.8401 | 18 | 12026.7886 |  | 4558.6126 | 18791.01
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 13976.4943 | 7 | 1868 |  | 908.4721 | 10220.59
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 32126.4207 | 19 | 5079.97 |  | 2715.97 | 23399.76
Includes CFE, CISO & LDWP
WI TOTAL |  | 116757.3214 | 19 | 18760.1165 |  | 8012.3605 | 51757.36
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 75021 | 8 | 16432
SRSG |  | 15292 | 7 | 4162
CAMX* |  | 33569 | 9 | 6007
WI TOTAL |  | 122265 | 8 | 27105
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 40.5
Low (F) | 21.7
Sunny |  | 71646.8401 | 75.11% | 75.11% | 24.89% | 71,647 MW
|  | 13976.4943 | 56.36% | 56.36% | 43.64% | 13,976 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 38.1 | 32126.4207 | 61.08% | 61.08% | 38.92% | 32,126 MW
Low (F) | 32.5
Fog
Billings, MT
High (F) | 44.4
Low (F) | 25.3
Sunny
Loveland, CO
High (F) | 54.3
Low (F) | 24.1
Sunny
Los Angeles, CA
High (F) | 69.8
Low (F) | 49.3
Sunny
Phoenix, AZ
High (F) | 74.7
Low (F) | 40.8
Sunny
Salt Lake City, UT
High (F) | 41.2
Low (F) | 14
Partly Cloudy
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
71,647 MW
13,976 MW
32,126 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend