## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-01-28
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 57.9 |  | 34 |  | 41.7 | 59.4
Low: |  | 39.4 |  | 22.6 |  | 34.5 | 30.7
Conditions: |  | Sunny |  | Partly Cloudy |  | Partly Cloudy | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 76124.1247 | 8 | 12042.7001 |  | 4943.1741 | 18373.1
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 14350.3827 | 7 | 1519 |  | 932.7749 | 10744.29
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 33288.1863 | 19 | 4414.64 |  | 2806.64 | 24414.74
Includes CFE, CISO & LDWP
WI TOTAL |  | 121991.9724 | 8 | 18933.6101 |  | 8287.1241 | 53307.13
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 80048 | 8 | 14844
SRSG |  | 15251 | 8 | 3820
CAMX* |  | 32907 | 19 | 4763
WI TOTAL |  | 127788 | 8 | 24258
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 34
Low (F) | 22.6
Partly Cloudy |  | 76124.1247 | 79.8% | 79.8% | 20.2% | 76,124 MW
|  | 14350.3827 | 57.87% | 57.87% | 42.13% | 14,350 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 48.6 | 33288.1863 | 63.29% | 63.29% | 36.71% | 33,288 MW
Low (F) | 32.9
Sunny
Billings, MT
High (F) | 44.2
Low (F) | 18.9
Sunny
Loveland, CO
High (F) | 45.3
Low (F) | 12.7
Sunny
Los Angeles, CA
High (F) | 56.1
Low (F) | 47.3
Partly Cloudy
Phoenix, AZ
High (F) | 61
Low (F) | 42.3
Partly Cloudy
Salt Lake City, UT
High (F) | 35.1
Low (F) | 10.9
Partly Cloudy
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
76,124 MW
14,350 MW
33,288 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend