## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-02-06
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 50.4 |  | 19.6 |  | 39.2 | 73.2
Low: |  | 37.8 |  | -11.4 |  | 26.9 | 53.6
Conditions: |  | Moderate rain |  | Partly Cloudy |  | Sunny | Patchy rain nearby
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 73944.3936 | 8 | 13149.1717 |  | 4869.2187 | 17200.07
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 12698.0576 | 7 | 1689 |  | 825.3737 | 10502.83
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 32560.2993 | 19 | 4539.06 |  | 2717.06 | 24287.71
Includes CFE, CISO & LDWP
WI TOTAL |  | 118670.6874 | 19 | 17970.202 |  | 8134.731 | 51963.61
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 78549 | 18 | 14287
SRSG |  | 12922 | 18 | 3610
CAMX* |  | 32950 | 9 | 6284
WI TOTAL |  | 123658 | 18 | 23064
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration
02-05/02-06 |  | Path 80 |  | 4 | 14

## Map
Weather Information
Calgary, AB
High (F) | 19.6
Low (F) | -11.4
Partly Cloudy |  | 73944.3936 | 77.52% | 77.52% | 22.48% | 73,944 MW
|  | 12698.0576 | 51.21% | 51.21% | 48.79% | 12,698 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 42.4 | 32560.2993 | 61.91% | 61.91% | 38.09% | 32,560 MW
Low (F) | 30.2
Partly Cloudy
Billings, MT
High (F) | 34.3
Low (F) | 6.6
Partly Cloudy
Loveland, CO
High (F) | 47.1
Low (F) | 26.6
Sunny
Los Angeles, CA
High (F) | 58.3
Low (F) | 54.1
Patchy rain nearby
Phoenix, AZ
High (F) | 80.8
Low (F) | 45.5
Sunny
Salt Lake City, UT
High (F) | 45.3
Low (F) | 31.1
Overcast
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
73,944 MW
12,698 MW
32,560 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend