## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-03-25
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 85.3 |  | 54.7 |  | 64.9 | 82
Low: |  | 50.2 |  | 31.5 |  | 48 | 57.4
Conditions: |  | Sunny |  | Sunny |  | Moderate rain | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 60632.8307 | 19 | 13673.7961 |  | 4021.8561 | 20258.7
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 15089.0864 | 18 | 1431 |  | 980.7906 | 10071.19
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 33105.3764 | 20 | 3979.5 |  | 2780.5 | 28754.92
Includes CFE, CISO & LDWP
WI TOTAL |  | 108469.5762 | 20 | 20664.1198 |  | 7433.3098 | 58819.81
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 63397 | 19 | 15669
SRSG |  | 15398 | 18 | 4179
CAMX* |  | 31954 | 19 | 4668
WI TOTAL |  | 110655 | 19 | 23578
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 54.7
Low (F) | 31.5
Sunny |  | 60632.8307 | 63.56% | 63.56% | 36.44% | 60,633 MW
|  | 15089.0864 | 60.85% | 60.85% | 39.15% | 15,089 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 74.5 | 33105.3764 | 62.94% | 62.94% | 37.06% | 33,105 MW
Low (F) | 43.2
Fog
Billings, MT
High (F) | 69.4
Low (F) | 39
Partly Cloudy
Loveland, CO
High (F) | 72.5
Low (F) | 35.6
Sunny
Los Angeles, CA
High (F) | 63.1
Low (F) | 51.4
Mist
Phoenix, AZ
High (F) | 100.4
Low (F) | 59.2
Sunny
Salt Lake City, UT
High (F) | 64.8
Low (F) | 28.2
Partly Cloudy
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
60,633 MW
15,089 MW
33,105 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend