## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-05-05
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 83.8 |  | 60.3 |  | 65.7 | 77
Low: |  | 54.5 |  | 37.8 |  | 46.6 | 53.8
Conditions: |  | Sunny |  | Sunny |  | Sunny | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 58460.2182 | 19 | 14717.4687 |  | 3870.0387 | 24390.86
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 13609.0194 | 20 | 1446 |  | 884.5863 | 11545.98
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 31601.1033 | 21 | 3948.86 |  | 2617.86 | 23896.3
Includes CFE, CISO & LDWP
WI TOTAL |  | 102903.6951 | 20 | 20126.1681 |  | 7236.2281 | 59441.14
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 59406 | 20 | 16930
SRSG |  | 13602 | 16 | 5229
CAMX* |  | 28779 | 20 | 4687
WI TOTAL |  | 101516 | 20 | 25165
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration
05-04/05-05 | WACM | Path 30 |  | 4 | 10
05-04/05-05 | WACM | Path 31 |  | 4 | 3

## Map
Weather Information
Calgary, AB
High (F) | 60.3
Low (F) | 37.8
Sunny |  | 58460.2182 | 61.28% | 61.28% | 38.72% | 58,460 MW
|  | 13609.0194 | 54.88% | 54.88% | 45.12% | 13,609 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 74.8 | 31601.1033 | 60.08% | 60.08% | 39.92% | 31,601 MW
Low (F) | 43.3
Sunny
Billings, MT
High (F) | 49.6
Low (F) | 39.2
Moderate rain
Loveland, CO
High (F) | 66
Low (F) | 47.7
Patchy rain nearby
Los Angeles, CA
High (F) | 66.2
Low (F) | 57.2
Partly Cloudy
Phoenix, AZ
High (F) | 70.9
Low (F) | 57.2
Partly Cloudy
Salt Lake City, UT
High (F) | 52.5
Low (F) | 43
Patchy rain nearby
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
58,460 MW
13,609 MW
31,601 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend