## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-05-22
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 82.2 |  | 59.4 |  | 64.2 | 76.6
Low: |  | 54.5 |  | 33.3 |  | 49.8 | 61.7
Conditions: |  | Sunny |  | Partly Cloudy |  | Sunny | Overcast
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 60783.0826 | 19 | 14132.3882 |  | 4071.4842 | 20578.92
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 20196.1436 | 18 | 1308 |  | 1312.7493 | 11275.99
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 36596.845 | 20 | 5007.16 |  | 2961.16 | 23645.51
Includes CFE, CISO & LDWP
WI TOTAL |  | 116769.4882 | 19 | 20497.9782 |  | 7966.8042 | 54633.42
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 64116 | 19 | 15407
SRSG |  | 20317 | 17 | 4209
CAMX* |  | 38810 | 18 | 5999
WI TOTAL |  | 123125 | 18 | 26485
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 59.4
Low (F) | 33.3
Partly Cloudy |  | 60783.0826 | 63.72% | 63.72% | 36.28% | 60,783 MW
|  | 20196.1436 | 81.45% | 81.45% | 18.55% | 20,196 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 61.2 | 36596.845 | 69.58% | 69.58% | 30.42% | 36,597 MW
Low (F) | 46.4
Patchy rain nearby
Billings, MT
High (F) | 70
Low (F) | 32.4
Partly Cloudy
Loveland, CO
High (F) | 77.7
Low (F) | 41.9
Sunny
Los Angeles, CA
High (F) | 72.5
Low (F) | 57.9
Partly Cloudy
Phoenix, AZ
High (F) | 106.5
Low (F) | 67.8
Sunny
Salt Lake City, UT
High (F) | 86.5
Low (F) | 41.9
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
60,783 MW
20,196 MW
36,597 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend