## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-05-29
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 87.4 |  | 87.3 |  | 64.8 | 87.4
Low: |  | 55.4 |  | 55.8 |  | 52.6 | 65.7
Conditions: |  | Sunny |  | Sunny |  | Moderate rain | Thundery outbreaks in nearby
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 66360.1777 | 18 | 12031.438 |  | 4173.556 | 21698.55
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 19600.7205 | 18 | 1462 |  | 1274.0468 | 10561.91
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 36467.5537 | 21 | 4708.8 |  | 2868.8 | 22699.93
Includes CFE, CISO & LDWP
WI TOTAL |  | 120961.1652 | 19 | 17895.3913 |  | 8066.7493 | 54165.39
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 72234 | 17 | 15221
SRSG |  | 20339 | 16 | 4854
CAMX* |  | 34142 | 20 | 5292
WI TOTAL |  | 125199 | 17 | 26047
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration
2025-05-28 | WACM | Path 30 |  | 4 | 2

## Map
Weather Information
Calgary, AB
High (F) | 87.3
Low (F) | 55.8
Sunny |  | 66360.1777 | 69.57% | 69.57% | 30.43% | 66,360 MW
|  | 19600.7205 | 79.04% | 79.04% | 20.96% | 19,601 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 66.9 | 36467.5537 | 69.33% | 69.33% | 30.67% | 36,468 MW
Low (F) | 50.2
Patchy rain nearby
Billings, MT
High (F) | 81
Low (F) | 40.8
Sunny
Loveland, CO
High (F) | 70.3
Low (F) | 48
Partly Cloudy
Los Angeles, CA
High (F) | 69.4
Low (F) | 58.6
Partly Cloudy
Phoenix, AZ
High (F) | 98.2
Low (F) | 71.8
Cloudy
Salt Lake City, UT
High (F) | 87.3
Low (F) | 50.7
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
66,360 MW
19,601 MW
36,468 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend