## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-06-09
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 95 |  | 88.3 |  | 73.6 | 81.9
Low: |  | 63.5 |  | 57 |  | 57.6 | 72.9
Conditions: |  | Sunny |  | Sunny |  | Sunny | Patchy rain nearby
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 77300.9121 | 18 | 14848.6057 |  | 4664.8897 | 18055.08
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 21992.2992 | 18 | 1301 |  | 1429.4994 | 8965.33
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 38283.6049 | 20 | 5170.93 |  | 3042.93 | 19615.46
Includes CFE, CISO & LDWP
WI TOTAL |  | 136452.8704 | 18 | 21323.3457 |  | 8790.7197 | 45946.87
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 75315 | 18 | 14509
SRSG |  | 22509 | 17 | 5270
CAMX* |  | 34617 | 20 | 5595
WI TOTAL |  | 132285 | 18 | 24523
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 88.3
Low (F) | 57
Sunny |  | 77300.9121 | 85.23% | 85.23% | 14.77% | 77,301 MW
|  | 21992.2992 | 74.22% | 74.22% | 25.78% | 21,992 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 93.9 | 38283.6049 | 62.35% | 62.35% | 37.65% | 38,284 MW
Low (F) | 61.2
Sunny
Billings, MT
High (F) | 87.6
Low (F) | 42.4
Sunny
Loveland, CO
High (F) | 83.1
Low (F) | 48.9
Sunny
Los Angeles, CA
High (F) | 71.1
Low (F) | 59.7
Partly Cloudy
Phoenix, AZ
High (F) | 107.4
Low (F) | 74.5
Sunny
Salt Lake City, UT
High (F) | 89.4
Low (F) | 49.6
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
77,301 MW
21,992 MW
38,284 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend