## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-06-23
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 95.7 |  | 76.3 |  | 60.1 | 93.6
Low: |  | 60.3 |  | 51.3 |  | 51.8 | 77
Conditions: |  | Sunny |  | Sunny |  | Cloudy | Patchy rain nearby
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 68272.6041 | 18 | 14315.5754 |  | 4488.4844 | 18816.9
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 21397.1153 | 18 | 1989 |  | 1390.8125 | 7878.65
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 35404.6367 | 21 | 5026.99 |  | 2823.99 | 18629.09
Includes CFE, CISO & LDWP
WI TOTAL |  | 123666.7538 | 19 | 21409.3364 |  | 8324.0654 | 44343.64
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 65783 | 18 | 18242
SRSG |  | 21351 | 17 | 6541
CAMX* |  | 33396 | 21 | 5334
WI TOTAL |  | 120001 | 18 | 30358
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
95
Weather Information
Calgary, AB
High (F) | 76.3
Low (F) | 51.3
Sunny |  | 68272.6041 | 75.28% | 75.28% | 24.72% | 68,273 MW
|  | 21397.1153 | 72.21% | 72.21% | 27.79% | 21,397 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 69.1 | 35404.6367 | 57.66% | 57.66% | 42.34% | 35,405 MW
Low (F) | 46.2
Partly Cloudy
Billings, MT
High (F) | 93.4
Low (F) | 50.2
Sunny
Loveland, CO
High (F) | 95.9
Low (F) | 55.2
Sunny
Los Angeles, CA
High (F) | 72.9
Low (F) | 61.2
Partly Cloudy
Phoenix, AZ
High (F) | 117.9
Low (F) | 78.6
Sunny
Salt Lake City, UT
High (F) | 102.7
Low (F) | 58.3
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
68,273 MW
21,397 MW
35,405 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend