## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-06-27
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 103.5 |  | 73 |  | 59 | 97
Low: |  | 63.5 |  | 55.8 |  | 53.5 | 77.4
Conditions: |  | Sunny |  | Thundery outbreaks in nearby |  | Patchy rain nearby | Partly Cloudy
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 72063.1084 | 17 | 15338.7922 |  | 4436.5762 | 20662.94
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 22477.6454 | 18 | 1883 |  | 1461.047 | 8424.49
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 41026.7909 | 19 | 5010.98 |  | 3205.98 | 20273.18
Includes CFE, CISO & LDWP
WI TOTAL |  | 134624.2504 | 18 | 21485.9525 |  | 8734.4265 | 48249.61
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 75077 | 17 | 18388
SRSG |  | 22699 | 17 | 5173
CAMX* |  | 39386 | 18 | 6897
WI TOTAL |  | 136836 | 17 | 29834
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
95
Weather Information
Calgary, AB
High (F) | 73
Low (F) | 55.8
Thundery outbreaks in nearby |  | 72063.1084 | 79.46% | 79.46% | 20.54% | 72,063 MW
|  | 22477.6454 | 75.86% | 75.86% | 24.14% | 22,478 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 70.9 | 41026.7909 | 66.82% | 66.82% | 33.18% | 41,027 MW
Low (F) | 57
Partly Cloudy
Billings, MT
High (F) | 88
Low (F) | 50
Partly Cloudy
Loveland, CO
High (F) | 95.2
Low (F) | 57.2
Sunny
Los Angeles, CA
High (F) | 74.8
Low (F) | 61.2
Partly Cloudy
Phoenix, AZ
High (F) | 109.4
Low (F) | 76.1
Sunny
Salt Lake City, UT
High (F) | 94.6
Low (F) | 55.8
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
72,063 MW
22,478 MW
41,027 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend