## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-07-03
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 98.6 |  | 80.2 |  | 66.7 | 93
Low: |  | 63 |  | 56.3 |  | 52.9 | 79.3
Conditions: |  | Partly Cloudy |  | Sunny |  | Cloudy | Partly Cloudy
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 75700.288 | 17 | 14609.6154 |  | 4842.9304 | 19486.49
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 21290.3561 | 18 | 2327 |  | 1383.8731 | 9091.83
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 39492.9393 | 19 | 5247.29 |  | 3119.29 | 17609.54
Includes CFE, CISO & LDWP
WI TOTAL |  | 135133.5439 | 18 | 21883.9984 |  | 9032.0433 | 45204.86
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 81677 | 17 | 16823
SRSG |  | 23482 | 15 | 5872
CAMX* |  | 40813 | 18 | 6956
WI TOTAL |  | 145532 | 17 | 29723
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
95
Weather Information
Calgary, AB
High (F) | 80.2
Low (F) | 56.3
Sunny |  | 75700.288 | 83.47% | 83.47% | 16.53% | 75,700 MW
|  | 21290.3561 | 71.85% | 71.85% | 28.15% | 21,290 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 76.8 | 39492.9393 | 64.32% | 64.32% | 35.68% | 39,493 MW
Low (F) | 50.2
Partly Cloudy
Billings, MT
High (F) | 92.8
Low (F) | 57.2
Thundery outbreaks in nearby
Loveland, CO
High (F) | 95.2
Low (F) | 59.4
Sunny
Los Angeles, CA
High (F) | 72.1
Low (F) | 60.1
Partly Cloudy
Phoenix, AZ
High (F) | 108
Low (F) | 84.2
Sunny
Salt Lake City, UT
High (F) | 90.9
Low (F) | 59.2
Cloudy
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
75,700 MW
21,290 MW
39,493 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend