## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-08-07
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 104.4 |  | 71.1 |  | 66.7 | 100.8
Low: |  | 66.6 |  | 50.2 |  | 58.3 | 75.4
Conditions: |  | Sunny |  | Thundery outbreaks in nearby |  | Patchy rain nearby | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 76044.4143 | 17 | 11400.4677 |  | 4754.3407 | 21648.43
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 27461.9134 | 17 | 2510 |  | 1785.0244 | 8757.24
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 47814.533 | 19 | 4934.97 |  | 3416.97 | 17907.47
Includes CFE, CISO & LDWP
WI TOTAL |  | 150650.8269 | 18 | 19038.142 |  | 9730.155 | 47167.14
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 79897 | 16 | 17206
SRSG |  | 28833 | 17 | 3944
CAMX* |  | 48114 | 17 | 6884
WI TOTAL |  | 156802 | 17 | 26297
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration
2025-08-07 | WACM | Path 31 |  | 4 | 3

## Map
95
Weather Information
Calgary, AB
High (F) | 71.1
Low (F) | 50.2
Thundery outbreaks in nearby |  | 76044.4143 | 83.85% | 83.85% | 16.15% | 76,044 MW
|  | 27461.9134 | 92.68% | 92.68% | 7.317% | 27,462 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 72.1 | 47814.533 | 77.88% | 77.88% | 22.12% | 47,815 MW
Low (F) | 56
Partly Cloudy
Billings, MT
High (F) | 86.9
Low (F) | 56.8
Partly Cloudy
Loveland, CO
High (F) | 99.5
Low (F) | 61.3
Partly Cloudy
Los Angeles, CA
High (F) | 82.9
Low (F) | 65.1
Partly Cloudy
Phoenix, AZ
High (F) | 121.8
Low (F) | 87.8
Sunny
Salt Lake City, UT
High (F) | 99.1
Low (F) | 58.5
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
76,044 MW
27,462 MW
47,815 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend