## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-09-05
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 91.6 |  | 73.4 |  | 78.8 | 91.8
Low: |  | 58.8 |  | 45 |  | 62.6 | 76.8
Conditions: |  | Sunny |  | Sunny |  | Partly Cloudy | Thundery outbreaks in nearby
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 72124.3378 | 17 | 12259.0316 |  | 4502.1256 | 23302.61
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 19600.5003 | 17 | 3173 |  | 1184.82 | 7855.54
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 44708.2228 | 18 | 4049.45 |  | 3345.45 | 22201.84
Includes CFE, CISO & LDWP
WI TOTAL |  | 135971.0812 | 18 | 19648.9807 |  | 8969.4847 | 52330.99
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 76380 | 17 | 15943
SRSG |  | 19125 | 16 | 5165
CAMX* |  | 47882 | 17 | 7092
WI TOTAL |  | 143035 | 17 | 28901
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
95
Weather Information
Calgary, AB
High (F) | 73.4
Low (F) | 45
Sunny |  | 72124.3378 | 79.52% | 79.52% | 20.48% | 72,124 MW
|  | 19600.5003 | 66.15% | 66.15% | 33.85% | 19,601 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 89.6 | 44708.2228 | 72.82% | 72.82% | 27.18% | 44,708 MW
Low (F) | 63.3
Partly Cloudy
Billings, MT
High (F) | 73.6
Low (F) | 40.8
Sunny
Loveland, CO
High (F) | 70.7
Low (F) | 52.7
Partly Cloudy
Los Angeles, CA
High (F) | 80.1
Low (F) | 65.7
Partly Cloudy
Phoenix, AZ
High (F) | 97.9
Low (F) | 74.8
Partly Cloudy
Salt Lake City, UT
High (F) | 88.7
Low (F) | 54.5
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
72,124 MW
19,601 MW
44,708 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend