## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-11-03
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 79.7 |  | 49.6 |  | 57.4 | 70.5
Low: |  | 54 |  | 26.1 |  | 43.2 | 37.8
Conditions: |  | Sunny |  | Sunny |  | Sunny | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 57146.2552 | 18 | 4162.3278 |  | 3714.5066 | 20472.8
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 14881.2647 | 17 | 1760 |  | 967.2822 | 12706.79
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 33169.3209 | 18 | 4163.8 |  | 2761.8 | 24104.43
Includes CFE, CISO & LDWP
WI TOTAL |  | 105079.8931 | 18 | 10090.1278 |  | 6684.1678 | 56983.02
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 56818 | 18 | 12243
SRSG |  | 11353 | 17 | 3142
CAMX* |  | 29032 | 18 | 16874
WI TOTAL |  | 98340 | 17 | 35609
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration
2025-11-02 | WACM | Path 36 |  | 4 | 2

## Map
95
Weather Information
Calgary, AB
High (F) | 49.6
Low (F) | 26.1
Sunny |  | 57146.2552 | 59.91% | 59.91% | 40.09% | 57,146 MW
|  | 14881.2647 | 60.01% | 60.01% | 39.99% | 14,881 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 49.8 | 33169.3209 | 63.06% | 63.06% | 36.94% | 33,169 MW
Low (F) | 43.5
Heavy rain
Billings, MT
High (F) | 58.6
Low (F) | 32.9
Sunny
Loveland, CO
High (F) | 59.7
Low (F) | 34.5
Sunny
Los Angeles, CA
High (F) | 66.7
Low (F) | 57.7
Partly Cloudy
Phoenix, AZ
High (F) | 95.4
Low (F) | 57.4
Sunny
Salt Lake City, UT
High (F) | 74.8
Low (F) | 39.9
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
57,146 MW
14,881 MW
33,169 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend