## Sheet1
WECC Interconnection Daily Status Report
Date: | 2025-11-24
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 58.8 |  | 29.7 |  | 44.1 | 55.8
Low: |  | 45.3 |  | 17.6 |  | 37.2 | 47.7
Conditions: |  | Fog |  | Moderate snow |  | Patchy rain nearby | Heavy rain
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 67127.372 | 18 | 10416.4448 |  | 4363.2792 | 17874.74
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 13048.0707 | 18 | 2372 |  | 791.48 | 12979.97
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 31337.8271 | 18 | 4317.75 |  | 2713.75 | 19931.43
Includes CFE, CISO & LDWP
WI TOTAL |  | 111513.2699 | 18 | 17106.1948 |  | 7389.5508 | 50390.14
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 67395 | 18 | 16342
SRSG |  | 13046 | 18 | 4476
CAMX* |  | 29303 | 18 | 5704
WI TOTAL |  | 98340 | 18 | 26522
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
95
Weather Information
Calgary, AB
High (F) | 29.7
Low (F) | 17.6
Moderate snow |  | 67127.372 | 70.37% | 70.37% | 29.63% | 67,127 MW
|  | 13048.0707 | 52.62% | 52.62% | 47.38% | 13,048 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 51.3 | 31337.8271 | 59.58% | 59.58% | 40.42% | 31,338 MW
Low (F) | 38.8
Patchy rain nearby
Billings, MT
High (F) | 57.9
Low (F) | 31.2
Patchy rain nearby
Loveland, CO
High (F) | 62.8
Low (F) | 31.3
Sunny
Los Angeles, CA
High (F) | 69.3
Low (F) | 54
Mist
Phoenix, AZ
High (F) | 72.7
Low (F) | 50.7
Sunny
Salt Lake City, UT
High (F) | 55.2
Low (F) | 32.2
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
67,127 MW
13,048 MW
31,338 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend