## Sheet1
WECC Interconnection Daily Status Report
Date: | 2026-01-09
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 54.7 |  | 42.8 |  | 45.5 | 65.7
Low: |  | 36.5 |  | 16.2 |  | 37.4 | 52.6
Conditions: |  | Sunny |  | Sunny |  | Patchy rain nearby | Patchy rain nearby
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 61933.952 | 8 | 8118.9566 |  | 4025.7069 | 17809.63
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 14369.1311 | 7 | 2196 |  | 933.9935 | 9063.41
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 32022.7249 | 19 | 4043.83 |  | 2527.83 | 20417.67
Includes CFE, CISO & LDWP
WI TOTAL |  | 107304.0981 | 8 | 15251.3466 |  | 7067.5636 | 46819.71
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 76422 | 17 | 14094
SRSG |  | 14003 | 17 | 6039
CAMX* |  | 33248 | 14 | 6440
WI TOTAL |  | 121561 | 17 | 25704
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration
2026-01-08 | WACM | Path 36 |  | 4 | 6

## Map
95
Weather Information
Calgary, AB
High (F) | 42.8
Low (F) | 16.2
Sunny |  | 61933.952 | 64.93% | 64.93% | 35.07% | 61,934 MW
|  | 14369.1311 | 57.95% | 57.95% | 42.05% | 14,369 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 52.7 | 32022.7249 | 60.88% | 60.88% | 39.12% | 32,023 MW
Low (F) | 39.3
Partly Cloudy
Billings, MT
High (F) | 41.4
Low (F) | 26.6
Sunny
Loveland, CO
High (F) | 43.5
Low (F) | 13.5
Moderate or heavy snow showers
Los Angeles, CA
High (F) | 68.5
Low (F) | 41.9
Sunny
Phoenix, AZ
High (F) | 66.2
Low (F) | 38.5
Sunny
Salt Lake City, UT
High (F) | 35.6
Low (F) | 23.4
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
61,934 MW
14,369 MW
32,023 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend