## Sheet1
WECC Interconnection Daily Status Report
Date: | 2026-02-20
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 52.7 |  | 23 |  | 37.8 | 65.7
Low: |  | 36.3 |  | -13.7 |  | 29.3 | 42.3
Conditions: |  | Sunny |  | Sunny |  | Partly Cloudy | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 64265.4176 | 8 | 8292.0087 |  | 4219.3837 | 22581.65
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 13309.7328 | 7 | 1775 |  | 865.1326 | 10400.43
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 32501.7186 | 19 | 4100.44 |  | 2722.44 | 24784.15
Includes CFE, CISO & LDWP
WI TOTAL |  | 108773.9222 | 8 | 14498.0487 |  | 7584.1437 | 57166.23
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 77332 | 8 | 13210
SRSG |  | 14164 | 7 | 3599
CAMX* |  | 35468 | 9 | 6695
WI TOTAL |  | 125331 | 8 | 24409
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
95
Weather Information
Calgary, AB
High (F) | 23
Low (F) | -13.7
Sunny |  | 64265.4176 | 67.37% | 67.37% | 32.63% | 64,265 MW
|  | 13309.7328 | 53.67% | 53.67% | 46.33% | 13,310 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 43.9 | 32501.7186 | 61.79% | 61.79% | 38.21% | 32,502 MW
Low (F) | 32.1
Partly Cloudy
Billings, MT
High (F) | 42.3
Low (F) | 3.4
Sunny
Loveland, CO
High (F) | 30.4
Low (F) | 18.7
Moderate snow
Los Angeles, CA
High (F) | 61
Low (F) | 41.7
Sunny
Phoenix, AZ
High (F) | 64
Low (F) | 46
Sunny
Salt Lake City, UT
High (F) | 36.1
Low (F) | 22.1
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
64,265 MW
13,310 MW
32,502 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend