## Sheet1
WECC Interconnection Daily Status Report
Date: | 2026-03-23
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 86.4 |  | 49.6 |  | 52.9 | 70.3
Low: |  | 56.5 |  | 22.8 |  | 36.7 | 51.3
Conditions: |  | Sunny |  | Sunny |  | Partly Cloudy | Sunny
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 64030.0239 | 8 | 10093.4918 |  | 3908.5048 | 24485.71
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 17283.1154 | 18 | 2360 |  | 1082.51 | 15733.9
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 35952.7123 | 20 | 3239.07 |  | 2682.07 | 24547.7
Includes CFE, CISO & LDWP
WI TOTAL |  | 114989.8367 | 20 | 14983.9062 |  | 7409.4712 | 63576.31
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 65237 | 19 | 13201
SRSG |  | 19687 | 17 | 4824
CAMX* |  | 33040 | 18 | 5800
WI TOTAL |  | 116980 | 18 | 24249
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW*
|  |  | W>E | 1200 MW*
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW*
|  |  | S>N | 3000 MW*
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
95
Weather Information
Calgary, AB
High (F) | 49.6
Low (F) | 22.8
Sunny |  | 64030.0239 | 67.12% | 67.12% | 32.88% | 64,030 MW
|  | 17283.1154 | 69.7% | 69.7% | 30.3% | 17,283 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 58.1 | 35952.7123 | 68.36% | 68.36% | 31.64% | 35,953 MW
Low (F) | 41.9
Partly Cloudy
Billings, MT
High (F) | 64.4
Low (F) | 36.7
Sunny
Loveland, CO
High (F) | 71.6
Low (F) | 35.4
Cloudy
Los Angeles, CA
High (F) | 71.6
Low (F) | 56.1
Fog
Phoenix, AZ
High (F) | 103.1
Low (F) | 66.6
Sunny
Salt Lake City, UT
High (F) | 79.2
Low (F) | 48.6
Sunny
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
64,030 MW
17,283 MW
35,953 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend