## Gens
Gen
Area Num of Gen | Area Name of Gen | Owner Number 1 | Owner Name 1 | Data Maintainer | Number of Bus | ID | ID | CASE Gen Min>Max | CASE Missing BA | CASE Pmax>GovMWCap | CASE Unapp Gen Model | EXCEED Gen Limit | NERC At Mvar Limit | NERC Limit Power Fact | NERC PSS No Ex | NERC RX Ratio | NERC Unreas H | NERC Unreas Sat | POWER Gen at 0.0 | POWER Gen on HV | POWER Miss Tag | POWER Miss Turbine Type | POWER Missing Model | POWER Missing PS | POWER Missing Sub R/X | POWER No Owner | Min MW | Max MW | Min Mvar | Max Mvar | BA Num of Gen | MWCap-MWMax | Gov_MWCap | Motor1 Exempt? | Machine | Stabilizer | Governor | Exciter | Status | Gen MW | Gen Mvar | Unit Type Code | MVA Base | Gen Power Factor Violation | Use Capability Curve | R (Internal Resistance) | X (Internal Reactance) | Inertia (Unit Base) | H (system base) | S1 | S12 | Saturation Ratio | Nom kV of Bus | BES Exempt? | GE Long ID | Unit Type | ID | Netting Exempt? | PSS Exempt?
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10425 | 02 | 02 | [6 empty] | Limit Power Fact | [12 empty] | -52.944 | 52.944 | -37.693 | 37.693 | 130 | -52.944 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 65 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.9 |  |  | BA (Energy Storage, Battery) | 02
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10718 | 04 | 04 | [6 empty] | Limit Power Fact | [12 empty] | -52.944 | 52.944 | -37.693 | 37.693 | 130 | -52.944 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 65 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.9 |  |  | BA (Energy Storage, Battery) | 04
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10837 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -198.05 | 150 | -107.1 | 107.1 | 130 | -150 |  |  | REGC_A |  |  | REEC_C | Closed | -53 | 17.2983 | BA | 245.7 | PF<-0.85 | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.63 |  | BESS-1 | BA (Energy Storage, Battery) | 2
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10839 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -198.05 | 150 | -107.1 | 107.1 | 130 | -150 |  |  | REGC_A |  |  | REEC_C | Closed | -53 | 17.2983 | BA | 245.7 | PF<-0.85 | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.63 |  | BESS-2 | BA (Energy Storage, Battery) | 4
11 | EL PASO | 100 | Clearwater Power Company |  | 11320 | BS | BS | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | -50.4 | 50.4 | 0 | 0 | 125 | -50.4 | [6 empty] | Open | 0 | 0 | UN | 50.4 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 34.5 |  |  | UN (Unknown) | BS
11 | EL PASO | 100 | Clearwater Power Company |  | 11320 | PV | PV | [5 empty] | At Mvar Limit | [8 empty] | Miss Turbine Type | Missing Model | Missing PS |  |  | 0 | 121.41 | -40.8 | 58.801 | 125 | -121.41 | [6 empty] | Closed | 71 | -40.8 | UN | 134.9 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 34.5 |  |  | UN (Unknown) | PV
11 | EL PASO | 1 | No owner defined |  | 11332 | PV | PV |  | Missing BA | [13 empty] | Missing Model |  |  | No Owner | 0 | 79.2904 | -44.0811 | 44.0811 | 9999 | -79.2904 | [6 empty] | Closed | 37 | -3.4091 | PV | 90.72 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | Gen Type1 x 24 | PV (Photovoltaic) | PV
11 | EL PASO | 1 | No owner defined |  | 11333 | BS | BS |  | Missing BA | [16 empty] | No Owner | -41.1968 | 41.1968 | -22.8511 | 22.8511 | 9999 | -41.1968 | [6 empty] | Open | 0 | 0 | BA | 47.11 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | Gen Type2 x 14 | BA (Energy Storage, Battery) | BS
11 | EL PASO | 1 | No owner defined |  | 11334 | PV | PV |  | Missing BA | [16 empty] | No Owner | 0 | 75.9867 | -42.2444 | 42.2444 | 9999 | -75.9867 |  |  | REGC_A |  |  | REEC_A | Closed | 37 | -3.4091 | PV | 63.16 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | Gen Type1 x 23 | PV (Photovoltaic) | PV
11 | EL PASO | 1 | No owner defined |  | 11335 | BS | BS |  | Missing BA | [16 empty] | No Owner | -38.2542 | 38.2542 | -21.2189 | 21.2189 | 9999 | -38.2542 | [6 empty] | Open | 0 | 0 | BA | 43.745 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | Gen Type2 x 13 | BA (Energy Storage, Battery) | BS
11 | EL PASO | 1 | No owner defined |  | 11384 | PV | PV |  | Missing BA | [12 empty] | Miss Turbine Type | Missing Model | Missing PS |  | No Owner | 0 | 108 | -47 | 47 | 9999 | -108 | [6 empty] | Closed | 107 | 0 | UN | 108 |  | NO | 0 | 0.61 | 0 |  |  |  | NAN | 0.55 |  |  | UN (Unknown) | PV
11 | EL PASO | 1 | No owner defined |  | 11390 | PV | PV |  | Missing BA | [12 empty] | Miss Turbine Type | Missing Model | Missing PS |  | No Owner | 0 | 54 | -23.5 | 23.5 | 9999 | -54 | [6 empty] | Closed | 53 | 0 | UN | 54 |  | NO | 0 | 0.61 | 0 |  |  |  | NAN | 0.6 |  |  | UN (Unknown) | PV
11 | EL PASO | 1 | No owner defined |  | 11416 | BS | BS | [14 empty] | Miss Turbine Type |  | Missing PS |  | No Owner | -65.5 | 65.5 | -39.52 | 39.52 | 125 | -65.5 | [6 empty] | Open | 0 | 0 | UN | 76.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | UN (Unknown) | BS
11 | EL PASO | 100 | Clearwater Power Company |  | 11613 | PV | PV |  | Missing BA | [17 empty] | 0 | 50 | -24.21 | 24.21 | 9999 | -50 | [6 empty] | Open | 0 | 0 | P3 | 55.56 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | PV
11 | EL PASO | 100 | Clearwater Power Company |  | 11614 | PV | PV |  | Missing BA | [17 empty] | 0 | 50 | -24.21 | 24.21 | 9999 | -50 | [6 empty] | Open | 0 | 0 | P3 | 55.56 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | PV
10 | NEW MEXICO | 126 | LAC New Mexico |  | 13300 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12.6 | -8.3 | 8.3 | 130 | -2e-07 | 12.6 |  | GENTPJ |  | HYGOV | EXST1_GE | Closed | 8 | 2.4646 | HY | 12.6 | PF<-0.85 | NO | 0 | 0.2 | 3.8 | 0.4788 | 0.08 | 0.4 | 5 | 4.16 |  | COYOTE_J_4.16_ABIQUIU | HY (Hydro) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14812 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | 0.12022 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_W1 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14813 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | -1.9855 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_W2 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14814 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | -0.67253 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_W3 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14816 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | -5.2331 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_E1 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14817 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | 0.58025 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_E2 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14818 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | 1.7677 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_E3 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 2 | Arizona Public Service |  | 14837 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -17.3 | 17.3 | -10.95 | 10.95 | 2 | -17.3 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 20.475 | PF<-0.85 | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.434 |  | Q300 Cotton Center BESS | BA (Energy Storage, Battery) | 1
14 | APS | 2 | Arizona Public Service |  | 14840 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | -14 | 14 | -7.59 | 7.59 | 2 | -14 |  |  | REGC_A |  |  | REEC_C | Closed | -1 | -7.59 | BA | 15.925 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.434 |  | Q303 Hyder 2 BESS | BA (Energy Storage, Battery) | 1
14 | APS | 2 | Arizona Public Service |  | 14841 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -17 | 17 | -11.41 | 11.41 | 2 | -17 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 20.475 | PF<-0.85 | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.434 |  | Q305 Paloma BESS | BA (Energy Storage, Battery) | 1
14 | APS | 2 | Arizona Public Service |  | 14855 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | -100 | 100 | -16.434 | 16.434 | 2 | -100 |  |  | REGC_A |  |  | REEC_C | Closed | 11 | 16.434 | BA | 102 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Q239 BESS | BA (Energy Storage, Battery) | 1
14 | APS | 995 | Yuma Cogeneration Associates |  | 14938 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 40 | -4 | 21 | 2 | 9 | 49 |  | GENTPF |  | GGOV1 | EXST4B | Open | 0 | 0 | CS | 49 |  | NO | 0 | 0.2 | 5.85 | 2.8665 | 0.1429 | 0.3913 | 2.7383 | 13.8 |  | YUMACO_13.8_CT1 | CS (Combined Cycle Single Shaft) | 1
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 15145 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 162 | -65 | 125 | 80 | 4.8 | 166.8 |  | GENTPJ | PSS2A | GGOV3 | ESST4B | Closed | 160 | 39.3178 | CT | 234 | PF<0.8 | NO | 0.002 | 0.086 | 4.84 | 11.3256 | 0.098 | 0.31 | 3.1633 | 18 |  | ARLINGT_18_G1 | CT (Combined Cycle Combustion Turbine Part) | 1
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 15146 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 163 | -65 | 125 | 80 | 3.8 | 166.8 |  | GENTPJ | PSS2A | GGOV3 | ESST4B | Closed | 160 | 39.3178 | CT | 234 | PF<0.8 | NO | 0.002 | 0.086 | 4.84 | 11.3256 | 0.098 | 0.31 | 3.1633 | 18 |  | ARLINGT_18_G2 | CT (Combined Cycle Combustion Turbine Part) | 1
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 15147 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 255 | -100 | 200 | 80 | -255 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 245 | 60.259 | CA | 373 | PF<0.8 | NO | 0.003 | 0.245 | 2.91 | 10.8543 | 0.088 | 0.283 | 3.2159 | 18 |  | ARLINGT_18_ST | CA (Combined Cycle Steam Part) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15164 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 100 | 162 | -80 | 126 | 80 | 22 | 184 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 150 | 45.2947 | CT | 218 | PF<0.8 | NO | 0.001 | 0.064 | 5.2 | 11.336 | 0.07 | 0.311 | 4.4429 | 18 |  | MESQUITE_18_CT1 | CT (Combined Cycle Combustion Turbine Part) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15165 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 100 | 162 | -80 | 126 | 80 | 22 | 184 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 150 | 45.3195 | CT | 218 | PF<0.8 | NO | 0.001 | 0.064 | 5.2 | 11.336 | 0.08 | 0.312 | 3.9 | 18 |  | MESQUITE_18_CT2 | CT (Combined Cycle Combustion Turbine Part) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15845 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 20 | 0 | 0 | 80 | -20 | [6 empty] | Closed | 20 | 0 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | QueenCreek_Solar_1 | PV (Photovoltaic) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15906 | 1 | 1 | [16 empty] | Missing PS |  |  | 4 | 74 | -8 | 33 | 80 | 15.5 | 89.5 |  | GENTPJ |  | IEEEG1_GE | EXDC1 | Open | 0 | 0 | GT | 89.5 |  | NO | 0.002 | 0.209 | 7.8 | 6.981 | 0.182 | 0.641 | 3.522 | 13.8 |  | AGUAFRIA_13_U6_NET | GT (Gas Turbine) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15918 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 90 | 108 | -58 | 82 | 80 | -108 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 105 | 25.6448 | CA | 143.6 | PF<0.8 | NO | 0.001 | 0.077 | 4.44 | 6.3758 | 0.08 | 0.33 | 4.125 | 13.8 |  | KYRENE_13_KYRENE_U7S | CA (Combined Cycle Steam Part) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15919 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 90 | 151 | -76 | 114 | 80 | 6.36 | 157.36 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 150 | 46.9036 | CT | 200 | PF<0.8 | NO | 0.001 | 0.065 | 5.67 | 11.34 | 0.076 | 0.29 | 3.8158 | 18 |  | KYRENE_18_KYRENE_U7A | CT (Combined Cycle Combustion Turbine Part) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15928 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 90 | 208.2 | -70 | 98 | 80 | -16.071 | 192.129 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 155 | 98 | GT | 220 |  | NO | 0.001 | 0.064 | 5.18 | 11.396 | 0.07 | 0.254 | 3.6286 | 18 |  | SANTAN_18_GEN_5B | GT (Gas Turbine) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15973 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 80 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | CopperCrossing_PV_1 | PV (Photovoltaic) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 15974 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 80 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | CopperCrossing_PV2 | PV (Photovoltaic) | 1
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17000 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 30 | 0 | 0 | 4 | -30 |  |  | DER_A |  |  |  | Closed | 13.77 | 0 | BA | 30 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Apache_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17000 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 40.5 | 0 | 0 | 4 | -40.5 |  |  | DER_A |  |  |  | Closed | 26.73 | 0 | P3 | 40.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Apache_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17189 | 6 | 6 | [11 empty] | Gen at 0.0 | [7 empty] | 0 | 10.9 | 0 | 0 | 4 | -10.9 |  |  | GENTPF |  |  |  | Closed | 0 | 0 | HY | 11.5 |  | NO | 0.002 | 0.19 | 2.25 | 0.25875 | 0.34 | 1.08 | 3.1765 | 13.8 |  | N_WADDEL_13.8_U6 | HY (Hydro) | 6
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17300 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 30 | 0 | 0 | 4 | -30 |  |  | DER_A |  |  |  | Closed | 22.7 | 0 | BA | 30 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Longtin_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17300 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 31 | 0 | 0 | 4 | -31 |  |  | DER_A |  |  |  | Closed | 20.46 | 0 | P3 | 31 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Longtin_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17602 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 15 | 0 | 0 | 4 | -15 |  |  | DER_A |  |  |  | Closed | 8.4 | 0 | BA | 15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 24.9 |  | Marana_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17602 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 4 | -10 |  |  | DER_A |  |  |  | Closed | 6.6 | 0 | P3 | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 24.9 |  | Marana_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17607 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 4 | -10 |  |  | DER_A |  |  |  | Closed | 10 | 0 | P3 | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 24.9 |  | Sahuraita_Aggregate_Battery | P3 (Photovoltaic, Fixed) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17620 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 15 | 0 | 0 | 4 | -15 |  |  | DER_A |  |  |  | Closed | 8.4 | 0 | BA | 15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 115 | BES Exempt | ORACLE-AE_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17620 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 4 | -10 |  |  | DER_A |  |  |  | Closed | 6.6 | 0 | P3 | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 115 | BES Exempt | ORACLE-AE_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
18 | NEVADA | 18 | N3 Nevada |  | 18277 | ST | ST |  |  |  |  | Exceed Gen Limit | [11 empty] | Missing PS |  |  | 27.2 | 29.1 | -10.3748 | 16.0765 | 24 | -29.1 |  |  | GENROU |  |  | ESAC1A | Closed | 26.9977 | 8.9542 | CA | 33 |  | YES | 0 | 0.269 | 5.187 | 1.7117 | 0.11 | 0.455 | 4.1364 | 13.8 |  | PABCO_13.2_GEN4 | CA (Combined Cycle Steam Part) | ST
18 | NEVADA | 18 | N3 Nevada |  | 18282 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 14 | 38 | -14.275 | 30.7 | 24 | 4.8e-07 | 38 |  | GENROU |  | GGOV1 | ESST1A_GE | Closed | 26.75 | 9.1531 | CT | 45.2 | PF<0.8 | YES | 0.005 | 0.17 | 5.17 | 2.3368 | 0.04 | 0.357 | 8.925 | 13.8 |  | SAGUARO2_13.8_SAGUARO_1 | CT (Combined Cycle Combustion Turbine Part) | 1 |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18283 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 14 | 38 | -14.275 | 30.7 | 24 | 4.8e-07 | 38 |  | GENROU |  | GGOV1 | ESST1A_GE | Closed | 26.75 | 9.4186 | CT | 45.2 | PF<0.8 | YES | 0.005 | 0.17 | 5.17 | 2.3368 | 0.04 | 0.357 | 8.925 | 13.8 |  | SAGUARO2_13.8_SAGUARO_2 | CT (Combined Cycle Combustion Turbine Part) | 2 |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18699 | B | B | [9 empty] | Unreas H | [9 empty] | 20.3 | 43.2 | -14 | 64 | 24 | 2.96 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN3_2 | CT (Combined Cycle Combustion Turbine Part) | B
18 | NEVADA | 18 | N3 Nevada |  | 18700 | B | B | [9 empty] | Unreas H | [9 empty] | 18.9 | 45.1 | -14 | 64 | 24 | 1.06 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN2_2 | CT (Combined Cycle Combustion Turbine Part) | B
18 | NEVADA | 18 | N3 Nevada |  | 18702 | A | A | [9 empty] | Unreas H | [9 empty] | 19.3 | 43 | -12 | 57 | 24 | 3.16 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Closed | 40 | 6.9581 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN2_1 | CT (Combined Cycle Combustion Turbine Part) | A
18 | NEVADA | 18 | N3 Nevada |  | 18703 | A | A | [9 empty] | Unreas H | [9 empty] | 20.1 | 46 | -14 | 64 | 24 | 0.16 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN3_1 | CT (Combined Cycle Combustion Turbine Part) | A
18 | NEVADA | 23 | N9 Nevada |  | 18781 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 212.47 | -69.8 | 69.8 | 24 | -212.47 |  |  | REGC_A |  |  | REEC_A | Closed | 150 | -17.6612 | PV | 223.65 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | EGLESHDWG1_0.63_1 | PV (Photovoltaic) | 1
18 | NEVADA | 23 | N9 Nevada |  | 18782 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 95.76 | -31.5 | 31.5 | 24 | -95.76 |  |  | REGC_A |  |  | REEC_A | Closed | 50 | -17.6614 | PV | 100.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | EGLESHDWG2_0.63_2 | PV (Photovoltaic) | 1
18 | NEVADA | 18 | N3 Nevada |  | 18874 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 3 | 30 | -9.9 | 9.9 | 24 | -30 |  |  | WT4G |  |  | WT4E | Closed | 19.9693 | -9.2247 | PV | 32 |  | NO | 1 | 10 | 0 |  |  |  | NAN | 0.4 |  | SILVST_34.5_PV1 | PV (Photovoltaic) | 1 |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18875 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 3 | 28 | -9.9 | 9.9 | 24 | -28 |  |  | WT4G |  |  | WT4E | Closed | 18.6567 | -8.6115 | PV | 32 |  | NO | 1 | 10 | 0 |  |  |  | NAN | 0.4 |  | SILVST_34.5_PV2 | PV (Photovoltaic) | 2 |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18884 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 30 | -33.12 | 33.12 | 24 | -30 |  |  | REGC_A |  |  | REEC_A | Closed | 26.2475 | 0.19874 | PV | 33.12 | PF<0.8 | NO | 1 | 10 | 0 |  |  |  | NAN | 0.38 |  | SPECTRUM_0.38_GEN | PV (Photovoltaic) | 1 |  | PSS Exempt
19 | WAPA L.C. | 50 | US Bur Reclam |  | 19031 | A8 | A8 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 42 | -32 | 17 | 4 | 21 | 63 |  | GENTPJ | PSS2C | HYG3 | DC4C | Closed | 41 | 5.463 | HY | 63.077 | PF<-0.85 | NO | 0.003 | 0.162 | 2.5 | 1.5769 | 0.1 | 0.52 | 5.2 | 16.5 |  | HOOVER_16.5_HVA8 | HY (Hydro) | A8
19 | WAPA L.C. | 50 | US Bur Reclam |  | 19031 | A9 | A9 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 45 | -29 | 17 | 4 | 26 | 71 |  | GENTPJ | PSS2C | HYG3 | DC4C | Closed | 45 | 5.463 | HY | 70.256 | PF<-0.85 | NO | 0.003 | 0.175 | 3.6 | 2.5292 | 0.08 | 0.48 | 6 | 16.5 |  | HOOVER_16.5_HVA9 | HY (Hydro) | A9
19 | WAPA L.C. | 50 | US Bur Reclam |  | 19788 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 130 | -45 | 52 | 4 | 26.687 | 156.687 |  | GENTPJ | PSS2C | HYGOV4 |  | Closed | 115 | -13.9388 | HY | 173.684 |  | NO | 0.003 | 0.299 | 2.3 | 3.9947 | 0.17 | 0.72 | 4.2353 | 13.8 |  | GC_13.8_GC1 | HY (Hydro) | 1
19 | WAPA L.C. | 50 | US Bur Reclam |  | 19788 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 0 | 128 | -42 | 46 | 4 | 28.687 | 156.687 |  | GENTPJ | PSS2C | HYGOV4 |  | Closed | 115 | -13.9388 | HY | 173.684 |  | NO | 0.003 | 0.284 | 2.3 | 3.9947 | 0.12 | 0.57 | 4.75 | 13.8 |  | GC_13.8_GC2 | HY (Hydro) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20006 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 160 | -50 | 70 | 111 | -2.38e-06 | 160 |  | GENROU | PSS2A | TGOV1 | EXST1_GE | Open | 0 | 0 | GT | 177.78 |  | NO | 0 | 0.199 | 3.69 | 6.5601 | 0.0522 | 0.1439 | 2.7567 | 15 |  | PJZ230_15_UNIT_5 | GT (Gas Turbine) | 5
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20007 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 160 | -50 | 70 | 111 | -2.38e-06 | 160 |  | GENROU | PSS2A | TGOV1 | EXST1_GE | Open | 0 | 0 | GT | 177.78 |  | NO | 0 | 0.199 | 3.69 | 6.5601 | 0.0522 | 0.1439 | 2.7567 | 15 |  | PJZ230_15_UNIT_6 | GT (Gas Turbine) | 6
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20141 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 30 | -10 | 12 | 111 | -1.19e-06 | 30 |  | GENROU |  | GGOV1 | EXDC1 | Closed | 26.64 | 4.3649 | BT | 35.3 |  | NO | 0.003 | 0.231 | 6.3 | 2.2239 | 0.28 | 0.886 | 3.1643 | 13.8 |  | CPU_13.8_UNIT_5 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 5 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20143 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Closed | 24 | 0.14324 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT10 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20144 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Open | 0 | 0 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT11 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20145 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Closed | 24 | 0.14324 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT12 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20146 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Open | 0 | 0 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT13 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 4 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20416 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 93 | 189 | -85 | 105 | 111 | 1.43e-06 | 189 |  | GENROU | PSS2B | GGOV1 | EXST4B | Closed | 185.0675 | 47.3323 | CT | 210 |  | NO | 0.002 | 0.12 | 5.421 | 11.3841 | 0.0705 | 0.6205 | 8.8014 | 18 |  | BJT230_18_GTG | CT (Combined Cycle Combustion Turbine Part) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20578 | SV | SV | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 0 | -250 | 350 | 111 | 0 | [6 empty] | Open | 0 | 0 | OT | 600 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 20 |  | MSC230_2 | OT (Other) | SV
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20598 | 1 | 1 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U1 | JE (Jet Engine) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20599 | 2 | 2 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U2 | JE (Jet Engine) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20600 | 3 | 3 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U3 | JE (Jet Engine) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20601 | 4 | 4 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U4 | JE (Jet Engine) | 4
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20602 | 5 | 5 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U5 | JE (Jet Engine) | 5
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20603 | 6 | 6 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U6 | JE (Jet Engine) | 6
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20604 | 7 | 7 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U7 | JE (Jet Engine) | 7
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20605 | 8 | 8 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U8 | JE (Jet Engine) | 8
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20610 | 2 | 2 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 357.3 | 0 | 66 | 111 | -357.3 | [6 empty] | Closed | 300 | 27.3375 | IC | 100 |  | NO | 0 | 0.09 | 0 |  |  |  | NAN | 13.8 |  | MCI-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20611 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 119.1 | 0 | 22.2 | 111 | -119.1 | [6 empty] | Closed | 100 | 4.5715 | IC | 100 |  | NO | 0 | 1.331 | 0 |  |  |  | NAN | 13.8 |  | MCI-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20660 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 0 | -12.5 | 25 | 111 | 0 |  |  | GENROU |  |  | EXAC1 | Closed | 0 | 3.7547 | SC | 37.5 | PF<0.8 | NO | 0 | 0.267 | 3.9593 | 1.4847 | 0.1875 | 0.65 | 3.4667 | 13.2 |  | PPF-01-CS | SC (Synchronous Condenser) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20670 | 2 | 2 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 0 | -12.5 | 25 | 111 | 0 |  |  | GENROU |  |  | EXAC1 | Open | 0 | 0 | SC | 37.5 | PF<0.8 | NO | 0 | 0.267 | 3.9593 | 1.4847 | 0.1875 | 0.65 | 3.4667 | 13.2 |  | PPF-02-CS | SC (Synchronous Condenser) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20680 | 3 | 3 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 0 | -12.5 | 25 | 111 | 0 |  |  | GENROU |  |  | EXAC1 | Open | 0 | 0 | SC | 37.5 | PF<0.8 | NO | 0 | 0.267 | 3.9593 | 1.4847 | 0.1875 | 0.65 | 3.4667 | 13.2 |  | PPF-03-CS | SC (Synchronous Condenser) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20912 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 211.2 | 0 | 44.946 | 111 | -161.2 | 50 |  | (GENROU) |  | (GGOV1) | (ESAC7B) | Closed | 184.43 | 4.9699 | IC | 50 |  | NO | 0 | 0.79 | 0 |  | 0.11 | 0.5 | 4.5455 | 13.8 |  | PND-U1 | IC (Internal Combustion) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21012 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.375 | -2.6 | 2.6 | 16 | 7e-08 | 4.375 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 3.5649 | 0.78632 | ST | 4.375 |  | NO | 0 | 0.11 | 1.693 | 0.074069 | 0.05 | 1.18 | 23.6 | 13.8 |  | HEBER_6_HEBER1 | ST (Steam Turbine) | 12
21 | IID | 16 | Imperial Irrigation District |  | 21020 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 24 | 47 | -32 | 32 | 16 | 1.2e-07 | 47 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 40.7 | 5.6742 | CA | 54 | PF<-0.85 | NO | 0 | 0.14 | 5.5 | 2.97 | 0.075 | 0.22 | 2.9333 | 13.8 |  | ELCEN92_6_ELSTM.3 | CA (Combined Cycle Steam Part) | 1
21 | IID | 16 | Imperial Irrigation District |  | 21021 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 24 | 47 | -32 | 32 | 16 | 1.2e-07 | 47 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 40.7 | 5.5205 | CA | 54 | PF<-0.85 | NO | 0 | 0.14 | 5.5 | 2.97 | 0.075 | 0.22 | 2.9333 | 13.8 |  | ELCEN92_6_ELSTM.3 | CA (Combined Cycle Steam Part) | 1 |  | PSS Exempt
21 | IID | 211 | IID Independent Power Producer |  | 21026 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 20 | -2.82 | 2.82 | 16 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 16 | -2.82 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.42 |  | ELCEN92_6_SOL.GEN | PV (Photovoltaic) | 1 |  | PSS Exempt
21 | IID | 211 | IID Independent Power Producer |  | 21116 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -151.73 | 151.73 | -99.6 | 99.6 | 16 | -151.73 |  |  | REGC_A |  |  | REEC_C | Closed | 62.507 | 28.6904 | BA | 181.5 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 2
21 | IID | 16 | Imperial Irrigation District |  | 21649 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 14 | 58 | -40 | 40 | 16 | -58 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 30 | -3.586 | CA | 77.5 | PF<-0.85 | NO | 0 | 0.164 | 4.5 | 3.4875 | 0.101 | 0.585 | 5.7921 | 13.8 |  | ELCEN92_6_ELSTM.3 | CA (Combined Cycle Steam Part) | 1
21 | IID | 16 | Imperial Irrigation District |  | 21656 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 11.6 | -7.5 | 7.5 | 16 | -4.1e-07 | 11.6 |  | GENROU |  | HYGOV4 | ESST4B | Closed | 7 | 2.2214 | HY | 12.5 | PF<-0.85 | NO | 0 | 0.312 | 2.18 | 0.2725 | 0.124 | 0.398 | 3.2097 | 6.9 |  | DROP4_6_UNIT1 | HY (Hydro) | 1
21 | IID | 16 | Imperial Irrigation District |  | 21657 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 11.4 | -7.5 | 7.5 | 16 | 7.4e-07 | 11.4 |  | GENROU |  | HYGOV4 | ESST4B | Closed | 9 | 2.7091 | HY | 12 | PF<-0.85 | NO | 0 | 0.363 | 2.53 | 0.3036 | 0.0757 | 0.2226 | 2.9406 | 6.9 |  | DROP4_6_UNIT1 | HY (Hydro) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21666 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 24.2 | -7.44 | 8 | 16 | 0.48 | 24.68 |  | GENTPJ | PSS2A | GGOV1 |  | Closed | 24.2 | 2.3127 | BT | 25.47 |  | NO | 0 | 0.15 | 4 | 1.0188 | 0.05 | 0.4 | 8 | 13.8 |  | HEBER_6_HEBER1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21666 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 0 | 22.8 | -6.98 | 7.5 | 16 | 0.46 | 23.26 |  | GENTPJ | PSS2A | GGOV1 |  | Closed | 22.8 | 2.3127 | BT | 24 |  | NO | 0 | 0.15 | 4 | 0.96 | 0.05 | 0.4 | 8 | 13.8 |  | HEBER_6_HEBER1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
21 | IID | 211 | IID Independent Power Producer |  | 21706 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 58.32 | 0 | 11.6 | 16 | 2.21e-06 | 58.32 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 46 | 2.7098 | ST | 68.61 |  | NO | 0 | 0.267 | 6.6 | 4.5283 | 0.065 | 0.334 | 5.1385 | 13.8 |  | MIDWAY_6_SALTSEA.U5L | ST (Steam Turbine) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21962 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -21.1 | 21.1 | -13.36 | 13.36 | 16 | -21.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 26.082 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | NBRAWLEY_6_NBSOLR.BAT.G | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22088 | 27 | 27 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | BLVRDE_6_BLVBT1_WDAT 127 - BESS | BA (Energy Storage, Battery) | 27
22 | SANDIEGO | 167 | Landfill Generating Partners |  | 22120 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 0.67 | -0.23 | 0.23 | 999 | -0.67 |  |  | GENTPF |  |  |  | Open | 0 | 0 | IT | 1.1 |  | NO | 0.006 | 0.15 | 3 | 0.033 | 0 | 0 | NAN | 138 | BES Exempt | CARLTON_HILLS_138_UNIT_1 | IT (Internal Combustion Turbo Charged) | 1
22 | SANDIEGO | 167 | Landfill Generating Partners |  | 22120 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.52 | -0.49 | 0.49 | 999 | -1.52 |  |  | GENTPF |  |  |  | Open | 0 | 0 | IT | 2.1 |  | NO | 0.006 | 0.15 | 3 | 0.063 | 0 | 0 | NAN | 138 | BES Exempt | CARLTON_HILLS_138_UNIT_2 | IT (Internal Combustion Turbo Charged) | 2
22 | SANDIEGO | 136 | SDG&E |  | 22136 | 28 | 28 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | CLRMNT_6_CLEBT1_WDAT 128 - BESS | BA (Energy Storage, Battery) | 28
22 | SANDIEGO | 142 | Calpeak Power |  | 22149 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 18 | 60.5 | -16 | 16 | 999 | -18.5 | 42 |  | GENROU | IEEEST | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 71.18 |  | YES | 0.008 | 0.202 | 1.17 | 0.83281 | 0.1207 | 0.4943 | 4.0953 | 13.8 |  | BORDER_6_UNITA1 | GT (Gas Turbine) | 1
22 | SANDIEGO | 158 | CalPeak Power Enterprise LLC |  | 22153 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 18 | 58.9 | -16 | 16 | 999 | -10.9 | 48 |  | GENTPF | PSS2B | TGOV1 | EXAC1 | Open | 0 | 0 | GT | 71.889 |  | YES | 0.008 | 0.202 | 1.02 | 0.73327 | 0.1 | 0.4 | 4 | 13.8 |  | ESCNDO_6_UNITB1 | GT (Gas Turbine) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22216 | 29 | 29 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ELLIOT_6_ELIBT1_WDAT 129 - BESS | BA (Energy Storage, Battery) | 29
22 | SANDIEGO | 136 | SDG&E |  | 22256 | 10 | 10 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ESCNDO_6_EB1BT1_WDAT 110 - BESS | BA (Energy Storage, Battery) | 10
22 | SANDIEGO | 136 | SDG&E |  | 22256 | 11 | 11 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ESCNDO_6_EB3BT3_WDAT 111 - BESS | BA (Energy Storage, Battery) | 11
22 | SANDIEGO | 136 | SDG&E |  | 22256 | 12 | 12 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ESCNDO_6_EB2BT2_WDAT 112 - BESS | BA (Energy Storage, Battery) | 12
22 | SANDIEGO | 136 | SDG&E |  | 22372 | 25 | 25 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | KEARNY_6_NESBT1_WDAT 125 - BESS | BA (Energy Storage, Battery) | 25
22 | SANDIEGO | 136 | SDG&E |  | 22372 | 26 | 26 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | KEARNY_6_SESBT2_WDAT 126 - BESS | BA (Energy Storage, Battery) | 26
22 | SANDIEGO | 136 | SDG&E |  | 22440 | 22 | 22 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | MELRSE_6_MELBT1_WDAT 122 - BESS | BA (Energy Storage, Battery) | 22
22 | SANDIEGO | 136 | SDG&E |  | 22440 | 23 | 23 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | MELRSE_6_MELBT2_WDAT 123 - BESS | BA (Energy Storage, Battery) | 23
22 | SANDIEGO | 168 | Fortistar |  | 22448 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.42 | -1.45 | 1.45 | 999 | -4.42 |  |  | (GENTPF) |  |  |  | Open | 0 | 0 | IT | 3.5 |  | NO | 0.006 | 0.15 | 0 |  | 0 | 0 | NAN | 69 |  | MESA_HEIGHTS_69_UNIT_1 | IT (Internal Combustion Turbo Charged) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22486 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 48 | -23 | 72 | 999 | 1 | 49 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 71.72 | PF<0.8 | YES | 0.008 | 0.202 | 1.2 | 0.86064 | 0.158 | 0.89 | 5.6329 | 13.8 |  | MRGT_6_MMAREF | GT (Gas Turbine) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22487 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 48 | -20 | 71 | 999 | 1 | 49 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 71.72 | PF<0.8 | YES | 0.008 | 0.202 | 1.2 | 0.86064 | 0.158 | 0.89 | 5.6329 | 13.8 |  | MRGT_6_MEF2 | GT (Gas Turbine) | 1
22 | SANDIEGO | 148 | Customer Owned QF-in SDG&E Area |  | 22496 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 0.7 | -0.23 | 0.23 | 999 | -0.7 |  |  | (GENTPF) |  |  |  | Open | 0 | 0 | GT | 1 |  | NO | 0.006 | 0.15 | 0 |  | 0 | 0 | NAN | 69 |  | MSSION_2_QF | GT (Gas Turbine) | 1
22 | SANDIEGO | 148 | Customer Owned QF-in SDG&E Area |  | 22604 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2.8 | -0.92 | 0.92 | 999 | -2.8 |  |  | (GENTPF) |  |  |  | Open | 0 | 0 | IT | 3.1 |  | NO | 0.006 | 0.15 | 0 |  | 0 | 0 | NAN | 69 |  | OTAY_13.8_GNA1 | IT (Internal Combustion Turbo Charged) | 1
22 | SANDIEGO | 148 | Customer Owned QF-in SDG&E Area |  | 22604 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2.7 | -0.89 | 0.89 | 999 | -2.7 |  |  | (GENTPF) |  |  |  | Open | 0 | 0 | IT | 3.8 |  | NO | 0.006 | 0.15 | 0 |  | 0 | 0 | NAN | 69 |  | OTAY_69_UNIT_1_METHANE | IT (Internal Combustion Turbo Charged) | 3
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 22607 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 272 | -157 | 178 | 999 | -272 |  |  | GENROU | PSS2A |  | ESST4B | Closed | 216 | 62.5512 | CC | 323 |  | YES | 0.011 | 0.269 | 4.69 | 15.1487 | 0.21 | 1.15 | 5.4762 | 16 |  | OTMESA_2_STG3 | CC (Combined Cycle Generic) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22624 | 88 | 88 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | PALA_6_PGCBT1_WDAT 188 - BESS | BA (Energy Storage, Battery) | 88
22 | SANDIEGO | 136 | SDG&E |  | 22636 | 30 | 30 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 | [6 empty] | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | PARDSE_6_PESBT1_WDAT 130 - BESS | BA (Energy Storage, Battery) | 30
22 | SANDIEGO | 148 | Customer Owned QF-in SDG&E Area |  | 22704 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 3.27 | -1.08 | 1.08 | 999 | 8.73 | 12 |  | GENTPF |  | GGOV1 | EXST4B | Open | 0 | 0 | GT | 26 |  | NO | 0.006 | 0.15 | 3 | 0.78 | 0 | 0 | NAN | 12.5 |  | SAMPSON_12.5_GT_UNIT_1_KELCO | GT (Gas Turbine) | 1
22 | SANDIEGO | 148 | Customer Owned QF-in SDG&E Area |  | 22724 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.5 | -0.49 | 0.49 | 999 | -1.5 |  |  | (GENTPF) |  |  |  | Open | 0 | 0 | IT | 1.2 |  | NO | 0.006 | 0.15 | 0 |  | 0 | 0 | NAN | 69 |  | SMRCOS_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 1
22 | SANDIEGO | 137 | Sempra US Gas and Power |  | 22981 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 30 | 308 | -125.0659 | 227.9451 | 999 | -308 |  |  | GENROU | PSS2A |  | ESST4B | Closed | 255 | 48.8653 | CC | 365 |  | YES | 0.002 | 0.046 | 3.95 | 14.4175 | 0.037 | 0.103 | 2.7838 | 21 |  | TERMEX_2_STG | CC (Combined Cycle Generic) | 1
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 23162 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 50 | 111.3 | -59.3044 | 105.8261 | 999 | -5.06 | 106.24 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Closed | 93 | 15.5891 | CS | 155.07 | PF<0.8 | YES | 0.007 | 0.165 | 1.4 | 2.171 | 0.106 | 0.362 | 3.4151 | 13.8 |  | PIOPIC_2_CTG1 | CS (Combined Cycle Single Shaft) | 1
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 23163 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 50 | 112.7 | -59.3044 | 105.8261 | 999 | -6.46 | 106.24 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Closed | 93 | 15.5891 | CS | 155.07 | PF<0.8 | YES | 0.007 | 0.165 | 1.4 | 2.171 | 0.106 | 0.362 | 3.4151 | 13.8 |  | PIOPIC_2_CTG2 | CS (Combined Cycle Single Shaft) | 1
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 23164 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 50 | 112 | -59.3044 | 105.8261 | 999 | -5.76 | 106.24 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Closed | 93 | 14.3578 | CS | 155.07 | PF<0.8 | YES | 0.007 | 0.165 | 1.4 | 2.171 | 0.106 | 0.362 | 3.4151 | 13.8 |  | PIOPIC_2_CTG3 | CS (Combined Cycle Single Shaft) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23320 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 49 | -13 | 56 | 999 | -9.5e-07 | 49 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 72 | PF<0.8 | YES | 0.006 | 0.16 | 1.174 | 0.84528 | 0.121 | 0.36 | 2.9752 | 13.8 |  | ELCAJN_6_LM6K | GT (Gas Turbine) | 1
22 | SANDIEGO | 195 | CED Westside Canal Battery Stora |  | 23421 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -137 | 137.1 | -110.675 | 110.675 | 999 | -137.1 |  |  | REGC_A |  |  | REEC_C | Closed | 137.1 | 13.6343 | BA | 176.2 | PF<0.8 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.69 |  | WESCAN_2_BDSBT1 | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 195 | CED Westside Canal Battery Stora |  | 23425 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -123 | 123 | -102.3194 | 102.3194 | 999 | -123 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 256.9 | PF<0.8 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 195 | CED Westside Canal Battery Stora |  | 23584 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -103.7 | 103.7 | -70.8888 | 70.8888 | 999 | -103.7 | [6 empty] | Open | 0 | 0 | BA | 125.763 | PF<-0.85 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23701 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | -4.11 | -2.56 | -120 | 225 | 999 | 2.56 |  |  | GENTPJ |  |  | ESAC7B | Closed | -0.010795 | 72.1232 | SC | 225 | PF<0.8 | NO | 0 | 0.141 | 2.12 | 4.77 | 0.0168 | 0.2463 | 14.6607 | 17.5 |  | Synchronous condenser A | SC (Synchronous Condenser) | 1 |  | PSS Exempt
22 | SANDIEGO | 136 | SDG&E |  | 23871 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -50 | 51.4 | -49.215 | 49.215 | 999 | -51.4 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 71.2 | PF<0.8 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.66 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24009 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | 0 | 42 | 999 | 54.4 | 94.4 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 94.4 | PF<0.8 | NO | 0 | 0.296 | 6.7638 | 6.385 | 0.149 | 0.61 | 4.094 | 13.8 |  | APPGEN_13.8_GT1 | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24010 | R2 | R2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | 0 | 42 | 999 | 54.4 | 94.4 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 94.4 | PF<0.8 | NO | 0 | 0.296 | 6.7638 | 6.385 | 0.149 | 0.61 | 4.094 | 13.8 |  | APPGEN_13.8_GT2 | OT (Other) | R2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24018 | R1 | R1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 35 | -8 | 17 | 999 | -35 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | OT | 100 |  | NO | 0 | 0.18 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24022 | 1 | 1 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 38 | 0 | 19 | 999 | 52 | 90 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 38 | 0 | CT | 90 |  | NO | 0.005 | 0.173 | 5 | 4.5 | 0.102 | 0.39 | 3.8235 | 13.8 |  | CHEVMN_13.8_CHEVGEN1 | CT (Combined Cycle Combustion Turbine Part) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24023 | 2 | 2 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 38 | 0 | 19 | 999 | 52 | 90 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 38 | 0 | CT | 90 |  | NO | 0.005 | 0.173 | 5 | 4.5 | 0.102 | 0.39 | 3.8235 | 13.8 |  | CHEVMN_13.8_CHEVGEN2 | CT (Combined Cycle Combustion Turbine Part) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24045 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -50 | 75 | 999 | 180 | 180 |  | GENTPF |  | IEEEG1_GE | EXDC1 | Open | 0 | 0 | ST | 192 | PF<0.8 | NO | 0.003 | 0.175 | 3.3333 | 6.3999 | 0.107 | 0.461 | 4.3084 | 18 |  |  | ST (Steam Turbine) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24046 | R2 | R2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -50 | 75 | 999 | 180 | 180 |  | GENTPF |  | IEEEG1_GE | EXDC1 | Open | 0 | 0 | ST | 204 | PF<0.8 | NO | 0.003 | 0.175 | 3.1324 | 6.3901 | 0.115 | 0.473 | 4.113 | 18 |  |  | ST (Steam Turbine) | R2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24050 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -40 | 55 | 999 | 125 | 125 |  | GENROU |  | GGOV1 | IEEET1 | Open | 0 | 0 | ST | 153.125 | PF<0.8 | NO | 0.004 | 0.134 | 4.07 | 6.2322 | 0.0803 | 0.4512 | 5.6189 | 15.5 |  |  | ST (Steam Turbine) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24051 | R2 | R2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -40 | 55 | 999 | 125 | 125 |  | GENROU |  | GGOV1 | IEEET1 | Open | 0 | 0 | ST | 153.125 | PF<0.8 | NO | 0.004 | 0.134 | 4.07 | 6.2322 | 0.0803 | 0.4512 | 5.6189 | 15.5 |  |  | ST (Steam Turbine) | R2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24054 | R5 | R5 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -25 | 50 | 999 | 130 | 130 |  | GENROU |  | GGOV1 | REXS | Open | 0 | 0 | GT | 162.5 | PF<0.8 | NO | 0 | 0.112 | 2.75 | 4.4688 | 0.1683 | 0.735 | 4.3672 | 16 |  |  | GT (Gas Turbine) | R5 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24063 | R1 | R1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 50 | 0 | 25 | 999 | 50 | 100 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 100 |  | NO | 0 | 0.14 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | WALNUTCM_13.8_HILLGEN | ST (Steam Turbine) | R1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24066 | RL | RL | [10 empty] | Unreas Sat | [8 empty] | 0 | 107.5 | -30 | 70 | 999 | -107.5 |  |  | GENTPJ |  |  | EXDC1 | Open | 0 | 0 | OT | 128 |  | NO | 0 | 0.25 | 6.227 | 7.9706 | 0.041 | 0.156 | 3.8049 | 13.8 |  |  | OT (Other) | RL |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24067 | HP | HP | [16 empty] | Missing PS |  |  | 0 | 107.5 | -22 | 65 | 999 | 107.5 | 215 |  | GENTPJ |  | IEEEG1_GE | EXDC1 | Open | 0 | 0 | XC | 128 |  | NO | 0 | 0.171 | 2.375 | 3.04 | 0.074 | 0.311 | 4.2027 | 13.8 |  | HNTGBH_13.8_GN2 | XC (Cross Compound Steam) | HP
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24067 | LP | LP | [16 empty] | Missing PS |  |  | 0 | 107.5 | -30 | 65 | 999 | -107.5 |  |  | GENTPJ |  |  | EXDC1 | Open | 0 | 0 | XC | 128 |  | NO | 0 | 0.25 | 6.227 | 7.9706 | 0.041 | 0.156 | 3.8049 | 13.8 |  |  | XC (Cross Compound Steam) | LP
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24071 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 30 | 0 | 15 | 999 | 15 | 45 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | GT | 45 |  | NO | 0.005 | 0.173 | 2.1778 | 0.98001 | 0.102 | 0.39 | 3.8235 | 13.8 |  | ETIWND_66_GN30 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24094 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 21.6 | 0 | 20 | 999 | 24.4 | 46 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | GT | 45 | PF<0.8 | NO | 0.005 | 0.173 | 5 | 2.25 | 0.102 | 0.39 | 3.8235 | 13.8 |  | LAFRES_1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24107 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 750 | -20 | 202 | 999 | 0 | 750 |  | GENROU | PSS2A | GGOV1 | ESST4B | Open | 0 | 0 | ST | 896 |  | NO | 0.001 | 0.18 | 2.82 | 25.2672 | 0.208 | 0.384 | 1.8462 | 26 |  | W_ORMOND_26_GN1 | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24110 | D1 | D1 | [9 empty] | Unreas H | Unreas Sat | [5 empty] | Missing PS |  |  | 34 | 49.5 | -26 | 29 | 999 | 1 | 50.5 |  | GENTPJ |  | GGOV1 | ESAC2A | Open | 0 | 0 | JE | 57.4 |  | NO | 0 | 0.101 | 1.2 | 0.6888 | 0.22 | 0.733 | 3.3318 | 13.8 |  | SNCLRA_13.8_OXGEN | JE (Jet Engine) | D1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24118 | R1 | R1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 30 | 0 | 15 | 999 | 70 | 100 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | OT | 100 |  | NO | 0 | 0.18 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | SAUGUS_13.8_PTCHGN | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24139 | R1 | R1 | [16 empty] | Missing PS |  |  | 0 | 41.2 | -12.7903 | 19.81 | 999 | -41.2 | [6 empty] | Open | 0 | 0 | ST | 43.446 |  | YES | 0 | 0.115 | 0 |  |  |  | NAN | 12.47 |  | LBEACH_1 | ST (Steam Turbine) | R1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24140 | R1 | R1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 37 | 0 | 20 | 999 | 63 | 100 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | GT | 100 |  | NO | 0 | 0.179 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | CHINO_13.8_SIMPSN | GT (Gas Turbine) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24150 | R1 | R1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 41 | 0 | 9.8 | 999 | -41 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | OT | 100 |  | NO | 0 | 0.116 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24159 | D1 | D1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 14.15 | -10.6 | 0.3 | 999 | -14.15 |  |  | GENTPJ | PSS2B |  | ESST4B | Open | 0 | 0 | JE | 31.5 | PF<-0.85 | NO | 0.004 | 0.2 | 2.48 | 0.7812 | 0.096 | 0.383 | 3.9896 | 12.47 |  | SNCLRA_66_GN_QF | JE (Jet Engine) | D1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24170 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 56.3 | -15 | 30 | 999 | 13.7 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | LBEACH_13.8_LBECH1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24170 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 56.5 | -15 | 30 | 999 | 13.5 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | LBEACH_13.8_LBECH2 | GT (Gas Turbine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24171 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 56.5 | -15 | 30 | 999 | 13.5 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | LBEACH_13.8_LBECH3 | GT (Gas Turbine) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24171 | 4 | 4 | [16 empty] | Missing PS |  |  | 0 | 56.5 | -15 | 30 | 999 | 13.5 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | LBEACH_13.8_LBECH4 | GT (Gas Turbine) | 4
24 | SOCALIF | 74 | Southern California Edison |  | 24234 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | Gen on HV | [6 empty] | 0 | 0 | -100 | 50 | 999 | 0 |  |  | SVCWSC |  |  |  | Closed | 0 | -39.8074 | OT | 100 | PF<0.8 | NO | 0 | 0.2 | 0 |  |  |  | NAN | 230 |  | W_RECTOR_230_SVC | OT (Other) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24239 | C1 | C1 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 44 | -4.5 | 25 | 999 | 6 | 50 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 40 | -4.5 | CS | 50 |  | NO | 0 | 0.16 | 6.23 | 3.115 | 0.1 | 0.33 | 3.3 | 13.8 |  | VERNONCM_13.8_GN1 | CS (Combined Cycle Single Shaft) | C1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24240 | C2 | C2 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 44 | -4.5 | 25 | 999 | 6 | 50 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 40 | -4.5 | CS | 50 |  | NO | 0 | 0.16 | 6.23 | 3.115 | 0.1 | 0.33 | 3.3 | 13.8 |  | VERNONCM_13.8_GN2 | CS (Combined Cycle Single Shaft) | C2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24241 | S3 | S3 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 51.6 | -5.3 | 30.6 | 999 | -51.6 |  |  | GENTPJ |  |  | ESAC7B | Closed | 45 | -5.3 | CA | 58.8 |  | NO | 0 | 0.16 | 3.17 | 1.864 | 0.1 | 0.19 | 1.9 | 13.8 |  | VERNONCM_13.8_GN3 | CA (Combined Cycle Steam Part) | S3
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24242 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 20 | 49.68 | -26 | 50 | 999 | 1.32 | 51 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 45 | -8.7755 | GT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.193 | 0.84913 | 0.15455 | 0.41435 | 2.681 | 13.8 |  | RVSIDE_13.8_GNR1 | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24243 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 20 | 49.68 | -26 | 50 | 999 | 1.32 | 51 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 45 | -8.7755 | GT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.193 | 0.84913 | 0.15455 | 0.41435 | 2.681 | 13.8 |  | RVSIDE_13.8_GNR2 | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24299 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 20 | 49.68 | -26 | 50 | 999 | -5.4e-07 | 49.68 |  | GENTPJ | PSS2A | GGOV1 | ESAC7B | Closed | 45 | -9.4755 | GT | 71.176 | PF<0.8 | NO | 0 | 0.198 | 1.193 | 0.84913 | 0.167 | 0.2952 | 1.7677 | 13.8 |  |  | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24300 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 20 | 49.68 | -26 | 50 | 999 | -5.4e-07 | 49.68 |  | GENTPJ | PSS2A | GGOV1 | ESAC7B | Closed | 45 | -9.4755 | GT | 71.176 | PF<0.8 | NO | 0 | 0.198 | 1.193 | 0.84913 | 0.167 | 0.2952 | 1.7677 | 13.8 |  |  | GT (Gas Turbine) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24306 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 19.8 | -2.7 | 7.68 | 999 | -1.38e-06 | 19.8 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 15 | -2.7 | HY | 22 |  | NO | 0 | 0.285 | 6.4369 | 1.4161 | 0.1556 | 0.3214 | 2.0656 | 7.2 |  | BGCRK1_7.2_GN1 | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24306 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 15.75 | -2.12 | 7.5 | 999 | 1.75 | 17.5 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 15 | -2.12 | HY | 17.5 |  | NO | 0 | 0.185 | 7.3133 | 1.2798 | 0.1556 | 0.3214 | 2.0656 | 7.2 |  | BGCRK1_7.2_GN2 | HY (Hydro) | 2
24 | SOCALIF | 74 | Southern California Edison |  | 24309 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 15.75 | -2.53 | 3.74 | 999 | 4.25 | 20 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 15 | -2.53 | HY | 17.5 |  | NO | 0 | 0.215 | 4.3726 | 0.76521 | 0.2644 | 0.9704 | 3.6702 | 7.2 |  | BGCRK2_7.2_GN_3 | HY (Hydro) | 3
24 | SOCALIF | 74 | Southern California Edison |  | 24309 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 15.75 | -2.38 | 3.76 | 999 | 4.25 | 20 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 15 | -2.38 | HY | 17.5 |  | NO | 0 | 0.214 | 4.0798 | 0.71397 | 0.2647 | 0.9704 | 3.666 | 7.2 |  | BGCRK2_7.2_GN_4 | HY (Hydro) | 4
24 | SOCALIF | 74 | Southern California Edison |  | 24310 | 5 | 5 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 17.5 | -2.44 | 7 | 999 | 3e-07 | 17.5 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 15 | -2.44 | HY | 17.5 |  | NO | 0 | 0.209 | 4.2948 | 0.75159 | 0.2877 | 0.95 | 3.3021 | 7.2 |  | BGCRK2_7.2_GN_5 | HY (Hydro) | 5
24 | SOCALIF | 74 | Southern California Edison |  | 24310 | 6 | 6 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 17.5 | -2.3 | 2.57 | 999 | 3e-07 | 17.5 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 15 | -2.3 | HY | 17.5 |  | NO | 0 | 0.19 | 4.0475 | 0.70831 | 0.2942 | 1 | 3.399 | 7.2 |  | BGCRK2_7.2_GN_6 | HY (Hydro) | 6
24 | SOCALIF | 74 | Southern California Edison |  | 24311 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 34 | -2.12 | 3.83 | 999 | -3.6e-07 | 34 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 25 | 3.83 | HY | 34 |  | NO | 0 | 0.199 | 3.415 | 1.1611 | 0.1266 | 0.4737 | 3.7417 | 13.8 |  | BGCRK3_13.2_GN1 | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24311 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 34 | -3.73 | 11.22 | 999 | 0.5 | 34.5 |  | GENQEC | PSS2A | HYGOV4 | EXST4B | Closed | 25 | 11.22 | HY | 34 |  | NO | 0 | 0.219 | 3.22 | 1.0948 |  |  | NAN | 13.8 |  | BGCRK3_13.2_GN2 | HY (Hydro) | 2
24 | SOCALIF | 74 | Southern California Edison |  | 24312 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 34 | -2.46 | 5 | 999 | -3.6e-07 | 34 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 30 | 5 | HY | 34 |  | NO | 0 | 0.182 | 3.34 | 1.1356 | 0.1266 | 0.4737 | 3.7417 | 13.8 |  | BGCRK3_13.2_GN3 | HY (Hydro) | 3
24 | SOCALIF | 74 | Southern California Edison |  | 24312 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 36 | -4.25 | 8.42 | 999 | -1.43e-06 | 36 |  | GENTPJ | PSS2A | HYGOV4 | EXST4B | Closed | 35 | 8.42 | HY | 40 |  | NO | 0 | 0.21 | 3.23 | 1.292 | 0.375 | 1.036 | 2.7627 | 13.8 |  | BGCRK3_13.2_GN4 | HY (Hydro) | 4
24 | SOCALIF | 74 | Southern California Edison |  | 24323 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.5 | -0.9 | 4.3 | 999 | 3.3e-07 | 10.5 |  | GENTPJ |  | HYGOV4 | EXST1_GE | Open | 0 | 0 | HY | 12 |  | NO | 0 | 0.302 | 1.92 | 0.2304 | 0.247 | 0.549 | 2.2227 | 4.8 |  | BGCRK1_4.8_PORTAL | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24324 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 8 | 0 | 13 | 999 | 92 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  |  | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24325 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 12 | 0 | 17 | 999 | 88 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Closed | 10 | 0 | IC | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | ELLIS_66_ORCOGEN | IC (Internal Combustion) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24326 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20 | -14 | 28 | 999 | 80 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  |  | OT (Other) | S1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24329 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 21.6 | 0 | 20 | 999 | 78.4 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | ST | 100 | PF<0.8 | NO | 0.005 | 0.173 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_1 | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24330 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 17 | 0 | 20 | 999 | 83 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Closed | 15 | 1.0609 | CC | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_13.8_OUTFALL1 | CC (Combined Cycle Generic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24331 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 17 | 0 | 20 | 999 | 83 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Closed | 15 | 1.0609 | CC | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_13.8_OUTFALL2 | CC (Combined Cycle Generic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24332 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 13 | 0 | 20 | 999 | 87 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_13.8_PALOGEN | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24333 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 74 | -150 | 210 | 999 | -74 | [6 empty] | Open | 0 | 0 | ST | 100 | PF<0.8 | NO | 0.004 | 0.252 | 0 |  |  |  | NAN | 13.8 |  |  | ST (Steam Turbine) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24334 | R2 | R2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 74 | -150 | 210 | 999 | -74 | [6 empty] | Open | 0 | 0 | ST | 100 | PF<0.8 | NO | 0.004 | 0.252 | 0 |  |  |  | NAN | 13.8 |  |  | ST (Steam Turbine) | R2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24335 | R3 | R3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 74 | -150 | 210 | 999 | -74 | [6 empty] | Open | 0 | 0 | ST | 100 | PF<0.8 | NO | 0.004 | 0.252 | 0 |  |  |  | NAN | 13.8 |  |  | ST (Steam Turbine) | R3 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24336 | R4 | R4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 74 | -150 | 210 | 999 | -74 | [6 empty] | Open | 0 | 0 | ST | 100 | PF<0.8 | NO | 0.004 | 0.252 | 0 |  |  |  | NAN | 13.8 |  |  | ST (Steam Turbine) | R4 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24337 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.1 | 0 | 20 | 999 | 89.9 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | HY | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LACIEN_66_VENICE | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24341 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20 | 0 | 17 | 999 | 80 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | SANTGO_13.8_COYOTE | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24361 | R3 | R3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | 0 | 42 | 999 | 54.4 | 94.4 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 94.4 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.2656 | 0.05 | 0.3 | 6 | 13.8 |  | APPGEN_13.8_ST_3 | OT (Other) | R3 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24362 | G1 | G1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 29 | -14 | 28 | 999 | -29 | [6 empty] | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.28 | 0 |  |  |  | NAN | 13.8 |  | GOLETA_13.8_EXGEN | OT (Other) | G1
24 | SOCALIF | 74 | Southern California Edison |  | 24372 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 20.5 | -4.1 | 5.4 | 999 | 2.28 | 22.78 |  | GENTPJ |  | HYGOV4 | REXS | Closed | 18 | 5.4 | HY | 22.78 |  | NO | 0 | 0.31 | 2.013 | 0.45856 | 0.0486 | 0.1818 | 3.7407 | 11 |  | VESTAL_11_GNK1 | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24373 | 2 | 2 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 19.8 | -3.7 | 6.35 | 999 | 1.7 | 21.5 |  | GENTPJ |  | HYGOV4 | REXS | Closed | 18 | 6.35 | HY | 21.5 |  | NO | 0 | 0.25 | 2.108 | 0.45322 | 0.048 | 0.1818 | 3.7875 | 11 |  | VESTAL_11_GNK2 | HY (Hydro) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24456 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 10 | -2.5 | 5 | 999 | 90 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | HY | 100 |  | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 66 |  |  | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24457 | 1 | 1 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 21.8 | -8.9 | -8.9 | 999 | -21.8 |  |  | WT3G |  | WT3T | WT3E | Closed | 21.8 | -8.9 | W3 | 100 |  | NO | 0.002 | 0.15 | 0 |  |  |  | NAN | 66 |  | ARBWD_66_ARBWIND | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24458 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 95.13 | -34.6 | -34.6 | 999 | 4.87 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 66 |  | ENWIND_66_ENCANWIND | WT (Wind Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24459 | 1 | 1 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 40.8 | -11.5 | -11.5 | 999 | -40.8 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 100 |  | NO | 0.002 | 0.15 | 0 |  |  |  | NAN | 66 |  | FLOWD_66_FLOWIND | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24460 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 14 | -2.8 | -2.8 | 999 | -6e-08 | 14 |  | WT1G |  | WT1T |  | Closed | 12 | -2.8 | W1 | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 66 |  | DTCHWD_66_DUTCHWIND | W1 (Wind Turbine, Type 1) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24481 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 18 | -4.5 | -4.5 | 999 | -18 |  |  | WT3G |  | WT3T | WT3E | Closed | 10 | -4.5 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  | MIDWD_66_MIDWIND | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24482 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 6.6 | -2.1 | -2.1 | 999 | -6.6 |  |  | WT3G |  | WT3T | WT3E | Closed | 6.5 | -2.1 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24483 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 19.4 | -5 | -5 | 999 | -19.4 |  |  | WT3G |  | WT3T | WT3E | Closed | 10 | -5 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  | NZWIND_12_NORTHW | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24484 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 13.2 | -3.7 | -3.7 | 999 | -13.2 |  |  | WT3G |  | WT3T | WT3E | Closed | 12 | -3.7 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  | NZWIND_12_ZONDWD | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24485 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 12.8 | -3.7 | -3.7 | 999 | -12.8 |  |  | WT3G |  | WT3T | WT3E | Closed | 12 | -3.7 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24491 | 1 | 1 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 27.9 | -5.2 | -5.2 | 999 | -27.9 |  |  | WT3G |  | WT3T | WT3E | Closed | 20 | -5.2 | W3 | 100 |  | NO | 0.002 | 0.15 | 0 |  |  |  | NAN | 66 |  | OAKWD_66_SOUTH_OAK | W3 (Wind Turbine, Type 3) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24695 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | 0 | 0 | 999 | -21 |  |  | WT4G |  | WT4T | WT4E | Closed | 20 | 0 | W4 | 21 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 1 |  | WINDHUB_66_BRODIE_1 | W4 (Wind Turbine, Type 4) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24696 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | 0 | 0 | 999 | -21 |  |  | WT4G |  | WT4T | WT4E | Closed | 20 | 0 | W4 | 21 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 1 |  |  | W4 (Wind Turbine, Type 4) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24697 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 18 | 0 | 0 | 999 | -18 |  |  | WT4G |  | WT4T | WT4E | Closed | 18 | 0 | W4 | 18 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 1 |  |  | W4 (Wind Turbine, Type 4) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24698 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 18 | 0 | 0 | 999 | -18 |  |  | WT4G |  | WT4T | WT4E | Closed | 18 | 0 | W4 | 18 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 1 |  |  | W4 (Wind Turbine, Type 4) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24699 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 24 | 0 | 0 | 999 | -24 |  |  | WT4G |  | WT4T | WT4E | Closed | 13 | 0 | W4 | 24 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 1 |  | WINDHUB_66_BRODIE_2 | W4 (Wind Turbine, Type 4) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24711 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 24.45 | -1.6 | 8 | 999 | -24.45 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 24 | -1.6 | ST | 35.778 |  | NO | 0.003 | 0.135 | 5.98 | 2.1395 | 0.189 | 0.576 | 3.0476 | 13.8 |  | CALGEN_13.8_GN1 | ST (Steam Turbine) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24719 | R3 | R3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 108 | -41 | 58 | 999 | -108 |  |  | GENROU | PSS2A |  | TEXS | Open | 0 | 0 | CA | 133.333 |  | NO | 0 | 0.237 | 3 | 4 | 0.1442 | 0.613 | 4.251 | 13.8 |  |  | CA (Combined Cycle Steam Part) | R3 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24726 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 7.5 | -7.5 | 7.5 | 999 | 5 | 12.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 7.5 | -0.86532 | ST | 12.5 | PF<0.8 | NO | 0 | 0.18 | 4.733 | 0.59162 | 0.194 | 0.0928 | 0.47835 | 4.16 |  | CSA_DIAB_34.5_CASA_DIABLO | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24733 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 55 | -3 | 7 | 999 | 45 | 100 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 18 | -2.3408 | ST | 100 |  | NO | 0 | 0.195 | 1.92 | 1.92 | 0.194 | 0.194 | 1 | 13.8 |  | SEARLS_34.5_ARGUS | ST (Steam Turbine) | 1
24 | SOCALIF | 980 | Terra-Gen Dixie Valley, LLC |  | 24747 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 59 | -24 | 30 | 999 | 2.62e-06 | 59 |  | GENROU | IEEEST | GGOV1 | EXST1_GE | Closed | 50 | -5.3319 | ST | 67.23 |  | NO | 0.003 | 0.23 | 7.6 | 5.1095 | 0.32 | 0.68 | 2.125 | 13.8 |  | OXBOW_B_13.8_OXBOW | ST (Steam Turbine) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24783 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.5 | -1.1 | 0.7 | 999 | 2.4e-07 | 6.5 |  | GENTPJ |  | HYGOV4 | EXST4B | Open | 0 | 0 | HY | 7.957 |  | NO | 0.003 | 0.256 | 1.885 | 0.14999 | 0.192 | 0.469 | 2.4427 | 2.4 |  |  | HY (Hydro) | 2
24 | SOCALIF | 74 | Southern California Edison |  | 24784 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.5 | -0.5 | 0.5 | 999 | 3e-08 | 1.5 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 1 | 0 | HY | 1.875 |  | NO | 0.003 | 0.33 | 1.377 | 0.025819 | 0.0083 | 0.28 | 33.7349 | 2.4 |  | LEE_VINI_6.9_LUNDY | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24784 | 2 | 2 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.5 | -0.5 | 0.5 | 999 | 3e-08 | 1.5 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 1 | 0 | HY | 1.875 |  | NO | 0 | 1e-05 | 1.377 | 0.025819 | 0.0083 | 0.28 | 33.7349 | 2.4 |  |  | HY (Hydro) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 8.7 | -2.9 | -2.9 | 999 | 2.5e-07 | 8.7 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  | GARNETCM_34.5_PWEST | WT (Wind Turbine) | G1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | G2 | G2 | [12 empty] | Gen on HV | [6 empty] | 0 | 3 | -1 | -1 | 999 | 7e-08 | 3 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  | GARNETCM_34.5_GN_WIND | WT (Wind Turbine) | G2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | PC | PC | [12 empty] | Gen on HV | [6 empty] | 0 | 2.1 | -0.7 | -0.7 | 999 | 3e-08 | 2.1 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  |  | WT (Wind Turbine) | PC
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | QF | QF | [6 empty] | Limit Power Fact | [5 empty] | Gen on HV | [6 empty] | 0 | 101.4 | -72.4 | -72.4 | 999 | -5.82e-06 | 101.4 |  | WT1G |  | WT1T |  | Closed | 90 | -72.4 | WT | 162 | PF<-0.85 | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  | GARNETCM_34.5_QF | WT (Wind Turbine) | QF
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | W2 | W2 | [6 empty] | Limit Power Fact | [5 empty] | Gen on HV | [6 empty] | 0 | 6.5 | -5.5 | -5.5 | 999 | 2.4e-07 | 6.5 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 | PF<0.8 | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  |  | WT (Wind Turbine) | W2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | W3 | W3 | [12 empty] | Gen on HV | [6 empty] | 0 | 11.6 | -3.9 | -3.9 | 999 | -4.1e-07 | 11.6 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  |  | WT (Wind Turbine) | W3
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24840 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | RVSIDE_13.8_GNS1 | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24840 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | RVSIDE_13.8_GNS2 | GT (Gas Turbine) | 2
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24841 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | RVSIDE_13.8_GNS3 | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24841 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | RVSIDE_13.8_GNS4 | GT (Gas Turbine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24861 | 3 | 3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 105.7145 | -52.3068 | 52.3068 | 999 | -105.7145 |  |  | REGC_A |  |  | REEC_B | Closed | 90 | 6.5378 | PV | 120 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.55 |  | SILVERST_230_SOUTH_SOLAR2 | PV (Photovoltaic) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24862 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 24.275 | -8.7672 | 8.7672 | 999 | -24.275 |  |  | REGC_A |  |  | REEC_B | Closed | 14.562 | 3.521 | PV | 26.3 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.36 |  |  | PV (Photovoltaic) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24863 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 124.41 | -44.9319 | 44.9319 | 999 | -124.41 |  |  | REGC_A |  |  | REEC_B | Closed | 90 | 18.3909 | PV | 134.81 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.36 |  | SILVERST_230_SOUTH_SOLAR1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24878 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 40.7 | -15.7 | 28.7 | 999 | 0.5 | 41.2 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 40 | 3.3847 | BT | 52.235 |  | NO | 0 | 0.154 | 1.596 | 0.83367 | 0.029 | 0.123 | 4.2414 | 12.47 |  |  | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24968 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 18 | -11.3 | 11.3 | 999 | -18 |  |  | REGC_A |  |  | REEC_A | Closed | 15.54 | -8.2534 | PV | 25.9 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.315 |  | RED_BLUF_230_DSRT_SUNLIGHT4 | PV (Photovoltaic) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24974 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 41 | -44 | 44 | 999 | -41 |  |  | REGC_A |  |  | REEC_A | Closed | 30 | -2.3366 | PV | 44 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25038 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 50 | -56 | 56 | 999 | -50 |  |  | REGC_A |  |  | REEC_A | Closed | 45 | -2.989 | PV | 56 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25041 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 85 | -56.2 | 56.2 | 999 | -85 |  |  | REGC_A |  |  | REEC_A | Closed | 75 | -4.9918 | PV | 93.6 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.34 |  | COLRIVER_230_BLK_CREEK | PV (Photovoltaic) | 4 |  | PSS Exempt
24 | SOCALIF | 2402 | City of Pasadena Water and Power |  | 25042 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 44.83 | -6.3 | 12.5 | 999 | 15.67 | 60.5 |  | GENROU |  | GGOV1 | EXAC8B | Open | 0 | 0 | GT | 71.176 |  | NO | 0.001 | 0.181 | 1.193 | 0.84913 | 0.12 | 0.37 | 3.0833 | 13.8 |  | BRDWAY_13.8_GN3 | GT (Gas Turbine) | 1
24 | SOCALIF | 2402 | City of Pasadena Water and Power |  | 25043 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 42.42 | -6.3 | 12.5 | 999 | 18.08 | 60.5 |  | GENROU |  | GGOV1 | EXAC8B | Open | 0 | 0 | GT | 71.176 |  | NO | 0.001 | 0.181 | 1.193 | 0.84913 | 0.12 | 0.37 | 3.0833 | 13.8 |  | GLNARM_13.8_GN4 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25044 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 82 | -54.8 | 54.8 | 999 | -82 |  |  | REGC_A |  |  | REEC_A | Closed | 75 | -4.8553 | PV | 91.26 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.34 |  |  | PV (Photovoltaic) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25064 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20.9 | -2.05 | 2.05 | 999 | -20.9 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 100000 | 100000 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25065 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 14.6 | -1.43 | 1.43 | 999 | -14.6 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 15.4 |  | NO | 100000 | 100000 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25079 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21.72 | -8.27 | 8.27 | 999 | -21.72 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 21.72 |  | NO | 0 | 0.61 | 0 |  |  |  | NAN | 0.645 |  | DELSUR_66_GLDFGR | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25086 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.7 | 9.7 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.8 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25089 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 22.39 | -9.76 | 9.76 | 999 | -22.39 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22.39 |  | NO | 0 | 0.982 | 0 |  |  |  | NAN | 0.42 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25092 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.215 | 9.215 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 20 |  | NO | 100000000 | 100000000 | 0 |  |  |  | NAN | 0.8 |  |  | PV (Photovoltaic) | EQ
24 | SOCALIF | 137 | Sempra US Gas and Power |  | 25119 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 93.1 | -44.56 | 33.56 | 999 | -93.1 |  |  | REGC_A |  |  | REEC_A | Closed | 56.154 | 33.56 | PV | 103.4 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 0.385 |  | MERCHANT_34.5_CMS4 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25169 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 12.63 | -5.488 | 5.488 | 999 | -12.63 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 13.032 |  | NO | 0 | 0.61 | 0 |  |  |  | NAN | 0.645 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25196 | EQ | EQ | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.7 | -13.6 | 13.6 | 999 | -20.7 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 24.864 | PF<-0.85 | NO | 100000000 | 100000000 | 0 |  |  |  | NAN | 0.6 |  |  | PV (Photovoltaic) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25211 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.6681 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_13.8_GT1 | JE (Jet Engine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25212 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.7307 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_13.8_GT2 | JE (Jet Engine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25213 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.7307 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_13.8_GT3 | JE (Jet Engine) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25214 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.6681 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_13.8_GT4 | JE (Jet Engine) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25215 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -125 | 130.35 | -80.9684 | 80.9684 | 999 | -130.35 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 153.45 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25216 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -125 | 130.35 | -80.9684 | 80.9684 | 999 | -130.35 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 153.45 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25217 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -100 | 103.687 | -64.4066 | 64.4066 | 999 | -103.687 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 122.063 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25218 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -100 | 103.687 | -64.4066 | 64.4066 | 999 | -103.687 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 122.063 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 4
24 | SOCALIF | 74 | Southern California Edison |  | 25219 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  |  | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 25220 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  |  | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 25221 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  |  | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 25222 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  |  | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25257 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -50 | 50.571 | -39.81 | 39.81 | 999 | -50.571 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 53.01 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25302 | 4 | 4 |  | Missing BA | [12 empty] | Miss Turbine Type |  |  |  |  | 1 | 11.4 | -6.5 | 8.5 | 9999 | 2.85 | 14.25 |  | GENTPJ |  | GGOV1 | ESAC7B | Open | 0 | 0 | UN | 14.25 |  | NO | 0 | 1e-05 | 2.4 | 0.342 | 0.07 | 0.35 | 5 | 12 |  |  | UN (Unknown) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.276 | 0.823 | 2.9819 | 6.9 |  | EAGLMT_6.9_GN1 | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.302 | 0.886 | 2.9338 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.288 | 0.901 | 3.1285 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.272 | 0.853 | 3.136 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.284 | 0.868 | 3.0563 | 6.9 |  | EAGLMT_6.9_GN2 | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.41 | 1.13 | 2.7561 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.374 | 1.159 | 3.0989 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.359 | 1.157 | 3.2228 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.343 | 1.054 | 3.0729 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.32 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.17568 | 0.252 | 0.683 | 2.7103 | 6.9 |  |  | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.231 | 0.629 | 2.7229 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.228 | 0.65 | 2.8509 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.254 | 0.737 | 2.9016 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.257 | 0.655 | 2.5486 | 6.9 |  |  | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.54 | 0.18542 | 0.487 | 1.723 | 3.538 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.495 | 1.669 | 3.3717 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.495 | 1.669 | 3.3717 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.433 | 1.549 | 3.5774 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.32 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.17568 | 0.231 | 0.669 | 2.8961 | 6.9 |  |  | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.212 | 0.629 | 2.967 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.21 | 0.68 | 3.2381 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.212 | 2.4 | 0.1752 | 0.223 | 0.596 | 2.6726 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.231 | 0.647 | 2.8009 | 6.9 |  |  | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.54 | 0.18542 | 0.482 | 2.393 | 4.9647 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.5 | 2.423 | 4.846 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.446 | 1.584 | 3.5516 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.5 | 1.783 | 3.566 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25417 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.007 | 0.15 | 2.01 | 0.07035 | 0.244 | 0.713 | 2.9221 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25417 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.007 | 0.15 | 2.01 | 0.07035 | 0.25 | 0.786 | 3.144 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25417 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.169 | 2.01 | 0.07035 | 0.262 | 0.806 | 3.0763 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.169 | 2.01 | 0.07035 | 0.247 | 0.844 | 3.417 | 6.9 |  | IRONMT_6.9_PUMP2 | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.161 | 2.01 | 0.07035 | 0.256 | 0.825 | 3.2227 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.153 | 1.9 | 0.0665 | 0.238 | 0.761 | 3.1975 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.153 | 1.9 | 0.0665 | 0.196 | 0.711 | 3.6276 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.284 | 0.918 | 3.2324 | 6.9 |  | HINDS_6.9_PUMPS1 | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.274 | 0.91 | 3.3212 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.279 | 0.786 | 2.8172 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.28 | 0.844 | 3.0143 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.316 | 0.856 | 2.7089 | 6.9 |  | HINDS_6.9_PUMPS2 | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.41 | 1.129 | 2.7537 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.301 | 1.106 | 3.6744 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.354 | 1.156 | 3.2655 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.41 | 1.183 | 2.8854 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25424 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN2 | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25424 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN3 | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25424 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN4 | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25425 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN6 | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25425 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN7 | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25425 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN8 | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25426 | 10 | 10 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN10 | MP (Motor/Pump) | 10
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25426 | 11 | 11 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN11 | MP (Motor/Pump) | 11
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25426 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_6.9_GN12 | MP (Motor/Pump) | 12
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25633 | QF | QF | [12 empty] | Gen on HV | [6 empty] | 0 | 20 | -10 | -10 | 999 | 80 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | W4 | 100 |  | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 115 |  | CAPWD_115_QF | W4 (Wind Turbine, Type 4) | QF
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25634 | QF | QF |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 17.1 | -8.6 | -8.6 | 999 | -17.1 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | BUCKWD_115_QF | W3 (Wind Turbine, Type 3) | QF |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25634 | W5 | W5 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 3.7 | -1.2 | -1.2 | 999 | -3.7 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | BUCKWD_115_WINTCV | W3 (Wind Turbine, Type 3) | W5 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25636 | Q1 | Q1 | [12 empty] | Gen on HV | [6 empty] | 0 | 6.3 | -3.2 | -3.2 | 999 | -6.3 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Open | 0 | 0 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | RENWD_115_QF | W3 (Wind Turbine, Type 3) | Q1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25636 | Q2 | Q2 | [12 empty] | Gen on HV | [6 empty] | 0 | 6.6 | -3.3 | -3.3 | 999 | -6.6 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Open | 0 | 0 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  |  | W3 (Wind Turbine, Type 3) | Q2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25639 | QF | QF |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 27 | -13.5 | -13.5 | 999 | -27 |  |  | WT3G |  | WT3T | WT3E | Closed | 25 | -13.5 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | PANSEA_115_SEAWND | W3 (Wind Turbine, Type 3) | QF |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25640 | QF | QF | [12 empty] | Gen on HV | [6 empty] | 0 | 30 | -15 | -15 | 999 | 70 | 100 |  | WT1G |  | WT1T |  | Closed | 30 | -15 | W1 | 100 |  | NO | 0 | 0.177 | 0 |  |  |  | NAN | 115 |  | PANSEA_115_PANAERO | W1 (Wind Turbine, Type 1) | QF
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25645 | EU | EU |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 16.9 | -5.6 | -5.6 | 999 | -16.9 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 20 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  |  | W3 (Wind Turbine, Type 3) | EU |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25645 | Q1 | Q1 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 25.5 | -12.8 | -12.8 | 999 | -25.5 |  |  | WT3G |  | WT3T | WT3E | Closed | 25.5 | -12.8 | W3 | 35 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | VENWD_115_GNQF | W3 (Wind Turbine, Type 3) | Q1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25645 | Q2 | Q2 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 19.3 | -9.7 | -9.7 | 999 | -19.3 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 25 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  |  | W3 (Wind Turbine, Type 3) | Q2 |  | PSS Exempt
24 | SOCALIF | 362 | Department of Water Resources |  | 25657 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 11.5 | -3.59 | 3.59 | 999 | -2.1e-07 | 11.5 |  | GENTPJ |  | HYG3 |  | Closed | 10 | -3.59 | HY | 11.5 |  | NO | 0 | 0.18 | 2.06 | 0.2369 | 0.042 | 0.276 | 6.5714 | 13.8 |  | MOJAVE_13.8_GN1 | HY (Hydro) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25729 | EQ | EQ | [12 empty] | Gen on HV | [6 empty] | -35 | 35 | -11.5 | 11.5 | 999 | -35 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 50 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 66 |  |  | BA (Energy Storage, Battery) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25767 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -82.5 | 82.5 | -72.958 | 72.958 | 999 | -82.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 82.5 | PF<0.8 | NO | 0 | 9999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25771 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -20.625 | 20.625 | -18.239 | 18.239 | 999 | -20.625 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 20.625 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25773 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -74.25 | 74.25 | -65.662 | 65.662 | 999 | -74.25 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 74.25 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25776 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -53.625 | 53.625 | -47.422 | 47.422 | 999 | -53.625 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 53.625 | PF<0.8 | NO | 0 | 9999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25892 | 1 | 1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.8 | 0 | 0 | 999 | 0.375 | 3.175 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | UN | 3.175 |  | NO | 0 | 10000 | 2.4 | 0.0762 | 0.05 | 0.3 | 6 | 12.47 |  |  | UN (Unknown) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25961 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -78.7 | 78.7 | -58.3 | 58.3 | 999 | -78.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 97.956 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25967 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -163.2 | 163.2 | -121 | 121 | 999 | -163.2 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 203.168 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
26 | LADWP | 123 | Intermountain Power Agency |  | 26028 | 1 | 1 | [16 empty] | Missing PS |  |  | -3.5 | 0 | -187.5 | 375 | 81 | 0 |  |  | GENTPJ |  |  | ST6C | Closed | -3.143 | 1.6158 | SC | 375 | PF<0.8 | NO | 0.001 | 0.15 | 1.948 | 7.305 | 0.1055 | 0.3846 | 3.6455 | 19.5 |  | INTMTN_2 | SC (Synchronous Condenser) | 1
26 | LADWP | 123 | Intermountain Power Agency |  | 26029 | 2 | 2 | [16 empty] | Missing PS |  |  | -3.5 | 0 | -187.5 | 375 | 81 | 0 |  |  | GENTPJ |  |  | ST6C | Open | 0 | 0 | SC | 375 | PF<0.8 | NO | 0.001 | 0.15 | 1.948 | 7.305 | 0.1055 | 0.3846 | 3.6455 | 19.5 |  | INTMTN_2 | SC (Synchronous Condenser) | 2
26 | LADWP | 123 | Intermountain Power Agency |  | 26030 | 3 | 3 | [16 empty] | Missing PS |  |  | -3.5 | 0 | -187.5 | 375 | 81 | 0 |  |  | GENTPJ |  |  | ST6C | Closed | -3.143 | 1.6158 | SC | 375 | PF<0.8 | NO | 0.001 | 0.15 | 1.948 | 7.305 | 0.1055 | 0.3846 | 3.6455 | 19.5 |  | INTMTN_2 | SC (Synchronous Condenser) | 3
26 | LADWP | 81 | City of Los Angeles |  | 26032 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 37.5 | -1 | 2 | 81 | 0 | 37.5 |  | GENTPJ | PSS2B | HYGOV4 | ESDC4B | Closed | 34.5 | 2 | HY | 37.5 |  | NO | 0.002 | 0.182 | 3.81 | 1.4287 | 0.158 | 0.512 | 3.2405 | 11.5 |  | TOLUCA_18_MAG_CT | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 81 | City of Los Angeles |  | 26033 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 37.5 | -1 | 2 | 81 | 0 | 37.5 |  | GENTPJ | PSS2B | HYGOV4 | ESDC4B | Closed | 34.5 | 2 | HY | 37.5 |  | NO | 0.002 | 0.182 | 3.81 | 1.4287 | 0.158 | 0.512 | 3.2405 | 11.5 |  | TOLUCA_18_MAG_ST | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 81 | City of Los Angeles |  | 26034 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 37.5 | -1 | 2 | 81 | 0 | 37.5 |  | GENTPJ | PSS2B | HYGOV4 | ESDC4B | Closed | 34.5 | 2 | HY | 37.5 |  | NO | 0.002 | 0.182 | 3.81 | 1.4287 | 0.158 | 0.512 | 3.2405 | 11.5 |  | NOT IN WSM | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 123 | Intermountain Power Agency |  | 26035 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 454 | -225 | 386 | 81 | -2 | 452 |  | GENTPJ | PSS2B | GGOV1 | ESST1A_GE | Open | 0 | 0 | CS | 643 | PF<0.8 | NO | 0.001 | 0.19 | 5.67 | 36.4581 | 0.14 | 0.81 | 5.7857 | 22 |  | INTMTN_26_GN3 | CS (Combined Cycle Single Shaft) | 3
26 | LADWP | 123 | Intermountain Power Agency |  | 26036 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 210 | 454 | -225 | 386 | 81 | -2 | 452 |  | GENTPJ | PSS2B | GGOV1 | ESST1A_GE | Open | 0 | 0 | CS | 643 | PF<0.8 | NO | 0.001 | 0.19 | 5.67 | 36.4581 | 0.14 | 0.81 | 5.7857 | 22 |  | INTMTN_26_GN4 | CS (Combined Cycle Single Shaft) | 4
26 | LADWP | 81 | City of Los Angeles |  | 26166 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 47 | 0 | 0 | 81 | -47 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | HY | 53 |  | NO | 0.004 | 0.15 | 3.5 | 1.855 | 0.2534 | 0.703 | 2.7743 | 7.5 |  | PPLNT1_7.5_GN3 | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 81 | City of Los Angeles |  | 26290 | 14 | 14 | [16 empty] | Missing PS |  |  | -2 | 102 | -20 | 92 | 81 | -102 |  |  | GENTPJ |  |  | ESAC7B | Closed | -2 | 36.2482 | JE | 127.282 | PF<0.8 | NO | 0.002 | 0.125 | 2.73 | 3.4748 | 0.061 | 0.176 | 2.8852 | 13.8 |  | HARBOR_13.8_GN14 | JE (Jet Engine) | 14
26 | LADWP | 122 | LA Contracts |  | 26868 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 16.8 | -8 | 8 | 81 | -16.8 |  |  | REGC_A |  |  | REEC_A | Closed | 12 | 1.3188 | PV | 16 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 1
26 | LADWP | 122 | LA Contracts |  | 26870 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 21 | -10 | 10 | 81 | -21 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | -0.075604 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 2
26 | LADWP | 122 | LA Contracts |  | 26872 | 3 | 3 | [17 empty] | Missing Sub R/X |  | 0 | 28 | -15.84 | 15.84 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 23 | 4.3157 | PV | 30.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | FTPECK_13.8_G01 | PV (Photovoltaic) | 3
26 | LADWP | 122 | LA Contracts |  | 26874 | 4 | 4 | [17 empty] | Missing Sub R/X |  | 0 | 28 | -17.16 | 17.16 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 23 | 4.1814 | PV | 30.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | FTPECK_13.8_G02 | PV (Photovoltaic) | 4
26 | LADWP | 122 | LA Contracts |  | 26876 | 5 | 5 | [17 empty] | Missing Sub R/X |  | 0 | 21 | -10 | 10 | 81 | -21 |  |  | REGC_A |  |  | REEC_A | Closed | 19 | 3.54 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | FTPECK_13.8_G03 | PV (Photovoltaic) | 5
26 | LADWP | 122 | LA Contracts |  | 26878 | 6 | 6 | [17 empty] | Missing Sub R/X |  | 0 | 26.25 | -13 | 13 | 81 | -26.25 |  |  | REGC_A |  |  | REEC_A | Closed | 24 | 2.7157 | PV | 25 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | TIBER_12.5_G1 | PV (Photovoltaic) | 6
26 | LADWP | 122 | LA Contracts |  | 26880 | 7 | 7 | [17 empty] | Missing Sub R/X |  | 0 | 28 | -18.48 | 18.48 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 23 | 4.7066 | PV | 30.8 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | SANTAN_1 | PV (Photovoltaic) | 7
26 | LADWP | 122 | LA Contracts |  | 26882 | 8 | 8 | [17 empty] | Missing Sub R/X |  | 0 | 28 | -18.48 | 18.48 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | 5.1492 | PV | 30.8 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | 8
26 | LADWP | 122 | LA Contracts |  | 26884 | A | A | [17 empty] | Missing Sub R/X |  | 0 | 24 | -15.84 | 15.84 | 81 | -24 |  |  | REGC_A |  |  | REEC_A | Closed | 16 | 3.1736 | PV | 26.4 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | A
26 | LADWP | 122 | LA Contracts |  | 26886 | B | B | [17 empty] | Missing Sub R/X |  | 0 | 26 | -17.16 | 17.16 | 81 | -26 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | 0.99278 | PV | 28.6 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | B
26 | LADWP | 122 | LA Contracts |  | 26901 | B | B |  |  |  |  | Exceed Gen Limit | [6 empty] | Gen at 0.0 | [5 empty] | Missing Sub R/X |  | -20 | 20 | -15 | 15 | 81 | -20 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 15.9 | PV | 25 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.57 |  |  | PV (Photovoltaic) | B
26 | LADWP | 81 | City of Los Angeles |  | 26949 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 81 | -10 | [6 empty] | Closed | 3 | 0 | PV | 100 |  | NO | 0 | 0.003 | 0 |  |  |  | NAN | 0.26 | BES Exempt | HARBOR_13.8_GN5 | PV (Photovoltaic) | 1 |  | PSS Exempt
26 | LADWP | 122 | LA Contracts |  | 26980 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -92.4 | 81.4716 | -92.4 | 92.4 | 81 | -81.4716 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 22.348 | BA | 92.4 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1 |  | PSS Exempt
26 | LADWP | 122 | LA Contracts |  | 26998 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -95.7 | 84.3813 | -95.7 | 95.7 | 81 | -84.3813 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 18.5875 | BA | 95.7 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1 |  | PSS Exempt
26 | LADWP | 122 | LA Contracts |  | 27191 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -95.7 | 84.3813 | -95.7 | 95.7 | 81 | -84.3813 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 24.0294 | BA | 95.7 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1
26 | LADWP | 122 | LA Contracts |  | 27198 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -92.4 | 81.4716 | -92.4 | 92.4 | 81 | -81.4716 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 17.8866 | BA | 92.4 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1
26 | LADWP | 121 | BURBANK |  | 27253 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 48 | -10 | 40 | 81 | -4 | 44 |  | GENROU | PSS2A | GGOV1 | ESST6B | Open | 0 | 0 | ST | 62.5 | PF<0.8 | NO | 0.002 | 0.24 | 3.68 | 2.3 | 0.1562 | 0.4882 | 3.1255 | 13.8 |  |  | ST (Steam Turbine) | 1
26 | LADWP | 119 | City of Glendale |  | 27342 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -7.6 | 10.3 | 81 | 25 | 25 |  | GENTPF |  | IEEEG1_GE | EXDC4 | Open | 0 | 0 | CC | 25 | PF<0.8 | NO | 0 | 1 | 2.97 | 0.7425 | 0.047 | 0.37 | 7.8723 | 13.8 |  | NOT_IN_WSM | CC (Combined Cycle Generic) | 1 |  | PSS Exempt
26 | LADWP | 119 | City of Glendale |  | 27344 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -6.7 | 13.6 | 81 | 25 | 25 |  | GENTPF |  | IEEEG1_GE | REXS | Open | 0 | 0 | CC | 25 | PF<0.8 | NO | 0 | 1 | 3.52 | 0.88 | 0.091 | 0.461 | 5.0659 | 13.8 |  | NOT_IN_WSM | CC (Combined Cycle Generic) | 2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29004 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 48 | -14 | 28 | 999 | 3.57 | 51.57 |  | GENROU |  | GGOV1 | REXS | Open | 0 | 0 | GT | 63 |  | NO | 0 | 0.227 | 1.72 | 1.0836 | 0.297 | 0.711 | 2.3939 | 13.8 |  | GOLETA_13.8_ELLWOD | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29005 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 25 | -6.3 | 12.5 | 999 | 7.1 | 32.1 |  | GENROU |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 32.1 |  | NO | 0 | 0.2 | 2.3 | 0.7383 | 0.124 | 0.286 | 2.3065 | 13.8 |  | GLNARM_13.8_GN1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29006 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 25 | -6.3 | 12.5 | 999 | 7.1 | 32.1 |  | GENROU |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 32.1 |  | NO | 0 | 0.2 | 2.3 | 0.7383 | 0.124 | 0.286 | 2.3065 | 13.8 |  | GLNARM_13.8_GN2 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29009 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 42.2 | -26 | 26 | 999 | 6.494 | 48.694 |  | GENROU |  | GGOV1 | ESAC7B | Open | 0 | 0 | CT | 48.694 |  | NO | 0.009 | 0.097 | 1.42 | 0.69145 | 0 | 0 | NAN | 13.8 |  |  | CT (Combined Cycle Combustion Turbine Part) | 1
24 | SOCALIF | 2402 | City of Pasadena Water and Power |  | 29013 | CT | CT | [16 empty] | Missing PS |  |  | 0 | 56 | -21 | 36.63 | 999 | 3.1 | 59.1 |  | GENROU |  | GGOV1 | ESAC7B | Open | 0 | 0 | CT | 69.529 |  | NO | 0.005 | 0.177 | 1.68 | 1.1681 | 0.11 | 0.49 | 4.4545 | 13.8 |  | GLNARM_13.8_GN5 | CT (Combined Cycle Combustion Turbine Part) | CT
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29079 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -60.952 | 60.952 | -38.326 | 38.326 | 999 | -60.952 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 72 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29081 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -62.476 | 62.476 | -39.284 | 39.284 | 999 | -62.476 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 73.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29087 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -200 | 208.0694 | -158.165 | 158.165 | 999 | -208.0694 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 261.36 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.66 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29088 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -150 | 156.0521 | -118.6237 | 118.6237 | 999 | -156.0521 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 196.02 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.66 |  |  | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29168 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -12.15 | 12.15 | -8.538 | 8.538 | 999 | -12.15 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 14.85 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.434 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29170 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 61.255 | -24.969 | 24.969 | 999 | -61.255 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 66.15 |  | NO | 1000000 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29198 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 12.5 | -7.5 | 7.5 | 999 | 0 | 12.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 12.5 |  | NO | 0 | 0.105 | 4.733 | 0.59162 | 0.194 | 0.0928 | 0.47835 | 4.16 |  |  | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29199 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 14 | -11.25 | 11.25 | 999 | 4.75 | 18.75 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 18.75 | PF<0.8 | NO | 0 | 0.105 | 4.733 | 0.88744 | 0.194 | 0.0928 | 0.47835 | 4.16 |  |  | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29201 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.93 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 96 | 41.7998 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | ENERGYPK_13.8_GEN1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29202 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.32 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 96 | 41.8749 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | ENERGYPK_13.8_GEN2 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29203 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.53 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 96 | 41.7286 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | ENERGYPK_13.8_GEN3 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29204 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.25 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | ENERGYPK_13.8_GEN4 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29205 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 51.48 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | ENERGYPK_13.8_GEN5 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29287 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -137.1 | 137.1 | -91.8 | 91.8 | 999 | -137.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 165 | PF<-0.85 | NO | 999999 | 9999999 | 0 |  |  |  | NAN | 0.55 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29295 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | -105.2898 | 105.2898 | -53.6497 | 53.6497 | 999 | -105.2898 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 118.1704 |  | NO | 999999 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29296 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 133.4925 | -82.7312 | 82.7312 | 999 | -133.4925 |  |  | REGC_A |  |  | REEC_A | Closed | 130 | 13.1997 | PV | 157.05 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29297 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 120.911 | -76.5197 | 76.5197 | 999 | -120.911 |  |  | REGC_A |  |  | REEC_A | Closed | 115 | 10.4965 | PV | 143.09 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29338 | G1 | G1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 24 | -14 | 14 | 999 | 5.4e-07 | 24 |  | GENROU | PSS2B | GGOV1 | EXAC8B | Open | 0 | 0 | CT | 43.882 |  | NO | 0.003 | 0.27 | 1.2 | 0.52658 | 0.056 | 0.146 | 2.6071 | 12.47 |  | CORONS_12.4_CTG | CT (Combined Cycle Combustion Turbine Part) | G1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29340 | S1 | S1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 8.5 | -1.5 | 3.5 | 999 | -8.5 |  |  | GENROU |  |  | EXAC8B | Open | 0 | 0 | CA | 10.594 |  | NO | 0.003 | 0.27 | 2.89 | 0.30617 | 0.077 | 0.18 | 2.3377 | 12.47 |  | CORONS_12.4_STG | CA (Combined Cycle Steam Part) | S1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29360 | 1 | 1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | -54 | 53.6 | -43.4 | 43.4 | 999 | -53.6 |  |  | REGC_A |  |  | REEC_A, (REEC_C) | Open | 0 | 0 | BA | 135.14 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29363 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -37 | 36.3 | -30.1 | 30.1 | 999 | -36.3 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 47.19 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29366 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 40.837 | -16.646 | 16.646 | 999 | -40.837 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 44.01 |  | NO | 1000000 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29367 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -16.2 | 16.2 | -11.384 | 11.384 | 999 | -16.2 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 19.8 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.434 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29385 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 52.9051 | -35.0605 | 35.0605 | 999 | -52.9051 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 63.468 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29391 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 45.5 | -13 | 13 | 999 | -45.5 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 48.96 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.38 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29392 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | -10.2 | 10.2 | -4 | 4 | 999 | -10.2 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10.2 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.38 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29394 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -38.812 | 38.912 | -59.47 | 59.47 | 999 | -38.912 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29395 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -38.78 | 38.78 | -54.18 | 54.18 | 999 | -38.78 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 62.56 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29396 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -13.179 | 13.179 | -12.04 | 12.04 | 999 | -13.179 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 13.902 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29397 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -12.809 | 12.809 | -18.78 | 18.78 | 999 | -12.809 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 21.336 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29659 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 45.91 | -18.19 | 18.19 | 9999 | -45.91 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 49.49 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.418 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29711 | 3 | 3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 88.22 | -40.36 | 40.36 | 999 | -88.22 |  |  | REGC_A |  |  | REEC_B | Closed | 52.932 | -1.4764 | PV | 97.02 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.52 |  | TEDDY_34.5_SGS_AVF3 | PV (Photovoltaic) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29712 | 4 | 4 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 88.18 | -40.41 | 40.41 | 999 | -88.18 |  |  | REGC_A |  |  | REEC_B | Closed | 52.908 | 0.056218 | PV | 97.02 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.52 |  | TEDDY_34.5_SGS_AVF4 | PV (Photovoltaic) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29712 | 5 | 5 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20.05 | -12.27 | 12.27 | 999 | -20.05 |  |  | REGC_A |  |  | REEC_B | Closed | 12.03 | 0.056218 | PV | 23.52 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.52 |  |  | PV (Photovoltaic) | 5
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29763 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -52 | 51.6 | -37 | 37 | 999 | -51.6 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 64.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29764 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -77.5 | 77.5 | -49 | 49 | 999 | -77.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 93.15 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29792 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -103.9 | 103.9 | -77.4 | 77.4 | 999 | -103.9 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 129.6 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29801 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.5 | -14.6 | 14.6 | 999 | -20.5 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 24.6 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29827 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -60.5 | 60.5 | -43 | 43 | 999 | -60.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 74.8 | PF<-0.85 | NO | 0.01 | 0.2 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29849 | 1 | 1 | [6 empty] | Limit Power Fact |  | RX Ratio | [10 empty] | -10.773 | 10.773 | -15.65 | 15.65 | 999 | -10.773 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 17.778 | PF<0.8 | NO | 999999 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29850 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -40.1961 | 40.1961 | -59.47 | 59.47 | 999 | -40.1961 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29851 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -38.1694 | 38.1694 | -55.7402 | 55.7402 | 999 | -38.1694 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29852 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -35.7466 | 35.7466 | -47.0451 | 47.0451 | 999 | -35.7466 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 59.09 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29853 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -11.8401 | 11.8401 | -17.7464 | 17.7464 | 999 | -11.8401 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 21.336 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29854 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -9.6001 | 9.6001 | -14.9631 | 14.9631 | 999 | -9.6001 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 17.778 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29855 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -40.1961 | 40.1961 | -54.2968 | 54.2968 | 999 | -40.1961 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29900 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 66 | -21.7 | 21.7 | 999 | -66 |  |  | WT4G |  | WT4T | WT4E | Closed | 39.6 | -8.9451 | PV | 66 |  | NO | 0 | 0.909 | 0 |  |  |  | NAN | 0.48 |  | NEENCH_66_ALPHINE_SOLAR | PV (Photovoltaic) | EQ |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29914 | 1 | 1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | 0 | 10 | -11.19 | 11.19 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 11.19 | PF<0.8 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.42 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29917 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.7 | 9.7 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.8 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29921 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -6.8415 | 6.8415 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | ANTLPE_66_PLAINVIEW | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29952 | D1 | D1 | [16 empty] | Missing PS |  |  | 0 | 28 | -7 | 14 | 999 | -28 |  |  | GENROU |  |  | EXST4B | Closed | 26.2 | 5.1977 | CC | 35.8 |  | NO | 0 | 0.18 | 2.4 | 0.8592 | 0.05 | 0.3 | 6 | 13.8 |  |  | CC (Combined Cycle Generic) | D1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | GT (Gas Turbine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | GT (Gas Turbine) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | GT (Gas Turbine) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | GT (Gas Turbine) | 5
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29965 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -90.1 | 90.1 | -71.8 | 71.8 | 999 | -90.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 115.1865 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 30464 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 54 | -22 | 32.3 | 9999 | -54 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | JE | 64.35 |  | NO | 0 | 1e-05 | 4.11 | 2.6448 | 0.126 | 0.357 | 2.8333 | 12.47 |  | WEBER_6_FORWRD | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31150 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 17.25 | -5.7 | 8.6 | 9999 | 2.05 | 19.3 |  | GENROU |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 19 |  | NO | 0 | 1 | 2.9474 | 0.56001 | 0.152 | 0.59 | 3.8816 | 13.8 |  | FAIRHV_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31152 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 12.5 | -12.4 | 17.2 | 9999 | 0 | 12.5 |  | GENTPJ |  | GGOV1 | ESAC7B | Open | 0 | 0 | ST | 25 | PF<0.8 | NO | 0 | 0.155 | 4.35 | 1.0875 | 0.091 | 0.325 | 3.5714 | 13.8 |  | PACLUM_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31152 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 12.5 | -12.4 | 17.2 | 9999 | 0 | 12.5 |  | GENTPJ |  | GGOV1 | ESAC7B | Open | 0 | 0 | ST | 25 | PF<0.8 | NO | 0 | 0.155 | 4.35 | 1.0875 | 0.091 | 0.325 | 3.5714 | 13.8 |  | PACLUM_6_UNIT | ST (Steam Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31153 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 7.5 | -3 | 5.5 | 9999 | -3e-07 | 7.5 |  | GENTPJ |  | GGOV1 | ESAC7B | Open | 0 | 0 | ST | 9.375 |  | NO | 0 | 0.155 | 4.35 | 0.40781 | 0.091 | 0.325 | 3.5714 | 2.4 |  | PACLUM_6_UNIT | ST (Steam Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31156 | MB | MB |  | Missing BA | [12 empty] | Miss Turbine Type |  |  |  |  | 0 | 12 | -4.31 | 4.31 | 9999 | -12 | [6 empty] | Open | 0 | 0 | UN | 13.8 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.47 |  | BLULKE_6_BLUELK | UN (Unknown) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31158 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 25 | -8.3 | 12.5 | 9999 | 2 | 27 |  | GENROU |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 52 |  | NO | 0 | 1 | 2.9474 | 1.5326 | 0.152 | 0.59 | 3.8816 | 12.47 |  | LAPAC_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31166 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 4.95 | -2.72 | 3.71 | 9999 | -4.95 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 0.3 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 4.16 |  | KEKAWK_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 4 | 4 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 9999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.7 | 7.1329 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 5 | 5 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 9999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.7 | 7.1329 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 5
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 6 | 6 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 9999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.7 | 7.1329 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 6
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 7 | 7 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 9999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.7 | 7.1329 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 7
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31181 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.5 | 9999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -1.9284 | IC | 20.8 | PF<0.8 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 1 | IC (Internal Combustion) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31181 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 9999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -1.9284 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 2 | IC (Internal Combustion) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31181 | 3 | 3 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 9999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -1.9284 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 3 | IC (Internal Combustion) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31182 | 10 | 10 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.4 | 9999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -1.9451 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 10 | IC (Internal Combustion) | 10
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31182 | 8 | 8 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 9999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -1.9451 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 8 | IC (Internal Combustion) | 8
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31182 | 9 | 9 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 9999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -1.9451 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 9 | IC (Internal Combustion) | 9
30 | PG AND E | 470 | Calpine Corp. |  | 31400 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 15.8 | 32.3 | -16.1 | 32.3 | 9999 | -32.3 |  |  | GENTPJ | PSS2A |  | ESAC7B | Closed | 32.3 | 3.55 | ST | 98 | PF<0.8 | NO | 0.004 | 0.276 | 4.3 | 4.214 | 0.104 | 0.588 | 5.6538 | 13.8 |  | SANTFG_7_UNITS | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31401 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 13.5 | 33.7 | -13.5 | 32 | 9999 | -33.7 |  |  | GENTPJ | PSS2A |  | ESAC7B | Closed | 32.3 | 3.55 | ST | 98 | PF<0.8 | NO | 0.004 | 0.276 | 4.3 | 4.214 | 0.104 | 0.588 | 5.6538 | 13.8 |  | SANTFG_7_UNITS | ST (Steam Turbine) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 31402 | R1 | R1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 10 | -3.3 | 5 | 9999 | 2 | 12 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 12 |  | NO | 0 | 1 | 5.3268 | 0.63922 | 0.267 | 0.763 | 2.8577 | 13.8 |  | BEARCN_2_UNITS | OT (Other) | R1
30 | PG AND E | 470 | Calpine Corp. |  | 31402 | R2 | R2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 10 | -3.3 | 5 | 9999 | 2 | 12 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 12 |  | NO | 0 | 1 | 5.3268 | 0.63922 | 0.267 | 0.763 | 2.8577 | 13.8 |  | BEARCN_2_UNITS | OT (Other) | R2
30 | PG AND E | 470 | Calpine Corp. |  | 31406 | 1 | 1 |  | Missing BA | [17 empty] | 13.2 | 42.6 | -15.86 | 13.1 | 9999 | -42.6 |  |  | GENTPJ | PSS2A |  | EXST4B | Closed | 42.6 | 2.1241 | ST | 66 |  | NO | 0.004 | 0.221 | 3.86 | 2.5476 | 0.1697 | 0.4693 | 2.7655 | 13.8 |  | GYS5X6_7_UNITS | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31406 | 2 | 2 |  | Missing BA | [17 empty] | 13.1 | 44 | -17.8 | 21 | 9999 | -44 |  |  | GENTPJ | PSS2A |  | EXST4B | Closed | 43.9 | 2.1241 | ST | 66 |  | NO | 0.004 | 0.221 | 3.86 | 2.5476 | 0.1697 | 0.4693 | 2.7655 | 13.8 |  | GYS5X6_7_UNITS | ST (Steam Turbine) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 31408 | 1 | 1 |  | Missing BA | [17 empty] | 19.5 | 40 | -18.44 | 20.48 | 9999 | -40 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 40 | 2.2612 | ST | 66 |  | NO | 0.004 | 0.208 | 5 | 3.3 | 0.089 | 0.243 | 2.7303 | 13.8 |  | GYS7X8_7_UNITS | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31408 | 2 | 2 |  | Missing BA | [17 empty] | 13.1 | 40.6 | -15.69 | 17.33 | 9999 | -40.6 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 40.6 | 2.2612 | ST | 66 |  | NO | 0.004 | 0.208 | 5 | 3.3 | 0.089 | 0.243 | 2.7303 | 13.8 |  | GYS7X8_7_UNITS | ST (Steam Turbine) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 31412 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 76.6 | -26.11 | 51.01 | 9999 | -76.6 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 72.1 | 4.6474 | ST | 132 |  | NO | 0.001 | 0.234 | 3.83 | 5.0556 | 0.063 | 0.297 | 4.7143 | 13.8 |  | GEYS11_7_UNIT11 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31414 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 27 | 48 | -10 | 40 | 9999 | -48 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 48 | -4.3518 | ST | 132 | PF<0.8 | NO | 0.001 | 0.234 | 3.83 | 5.0556 | 0.075 | 0.293 | 3.9067 | 13.8 |  | GEYS12_7_UNIT12 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31416 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 27.6 | 55.7 | -34.6 | 32.8 | 9999 | -55.7 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 55.7 | 3.9499 | ST | 155.3 | PF<-0.85 | NO | 0.004 | 0.189 | 4.7 | 7.2991 | 0.072 | 0.22 | 3.0556 | 13.8 |  | GEYS13_7_UNIT13 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31418 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 109 | -47.8 | 90 | 9999 | -109 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 70 | 18.7989 | BT | 137.8 | PF<0.8 | NO | 0 | 1 | 4.8 | 6.6144 | 0.113 | 0.304 | 2.6903 | 13.8 |  | GEYS14_7_UNIT14 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31420 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 29.3 | 48.2 | -33.46 | 68.89 | 9999 | -48.2 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 48.2 | -8.119 | ST | 137.8 | PF<0.8 | NO | 0.002 | 0.258 | 3.75 | 5.1675 | 0.06 | 0.2 | 3.3333 | 13.8 |  | GEYS16_7_UNIT16 | ST (Steam Turbine) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 31421 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 2 | 55 | -15.886 | 26.64 | 9999 | 166.4 | 221.4 |  | GENTPF | IEEEST | GGOV1 | REXS | Open | 0 | 0 | BT | 221.4 |  | NO | 0 | 1e-05 | 5.52 | 12.2213 | 0.216 | 0.74 | 3.4259 | 13.8 |  | GEYS17_2_BOTRCK | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31422 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 27.7 | 64 | -22 | 49.5 | 9999 | -64 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 64 | -3.9156 | ST | 137.8 | PF<0.8 | NO | 0.002 | 0.258 | 3.75 | 5.1675 | 0.06 | 0.2 | 3.3333 | 13.8 |  | GEYS17_7_UNIT17 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31424 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 21.6 | 62.8 | -24 | 58 | 9999 | -62.8 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 62.8 | 8.1919 | ST | 137.8 | PF<0.8 | NO | 0 | 0.227 | 3.85 | 5.3053 | 0.095 | 0.308 | 3.2421 | 13.8 |  | GEYS18_7_UNIT18 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31426 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 26.2 | 45.8 | -29 | 83 | 9999 | -45.8 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 45.8 | 6.9631 | ST | 137.8 | PF<0.8 | NO | 0.002 | 0.258 | 3.75 | 5.1675 | 0.06 | 0.2 | 3.3333 | 13.8 |  | GEYS20_7_UNIT20 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31430 | 1 | 1 |  | Missing BA | [17 empty] | 15 | 64.5 | -23.6 | 20 | 9999 | -64.5 |  |  | GENTPJ | PSS2A |  | ESAC7B | Closed | 51.3 | 6.9279 | ST | 86.667 |  | NO | 0.004 | 0.135 | 8.1 | 7.02 | 0.0738 | 0.2844 | 3.8537 | 13.8 |  | SMUDGO_7_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31433 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5.5 | -1 | 2.75 | 9999 | -5.5 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 4 |  | NO | 0 | 1e-05 | 4.64 | 0.1856 | 0.152 | 0.59 | 3.8816 | 2.4 |  | POTTER_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31433 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 2.5 | -0.5 | 1.1875 | 9999 | -2.5 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 2 |  | NO | 0 | 1e-05 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 2.4 |  | POTTER_6_UNITS | HY (Hydro) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31433 | 4 | 4 |  | Missing BA | [17 empty] | 0 | 2.5 | -0.5 | 1.1875 | 9999 | -2.5 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 2 |  | NO | 0 | 1e-05 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 2.4 |  | POTTER_6_UNITS | HY (Hydro) | 4
30 | PG AND E | 470 | Calpine Corp. |  | 31435 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 3.95 | 11.35 | -3.7 | 6.7 | 9999 | -11.35 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 11.35 | 0.2049 | ST | 13.89 |  | NO | 0 | 0.08 | 5 | 0.6945 | 0.193 | 0.47 | 2.4352 | 13.8 |  | ADLIN_1_UNITS | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31436 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 2.9 | 0 | 0 | 9999 | -2.9 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.03 | 0 | HY | 3 |  | NO | 0 | 1 | 4.64 | 0.1392 | 0.152 | 0.59 | 3.8816 | 9.11 |  | INDVLY_1_UNITS | HY (Hydro) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31437 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 3.91 | 9 | -4.4 | 7.7 | 9999 | -9 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 9 | 0.15121 | ST | 13.89 | PF<0.8 | NO | 0 | 0.08 | 5 | 0.6945 | 0.157 | 0.376 | 2.3949 | 13.8 |  | ADLIN_1_UNITS | ST (Steam Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31446 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 6 | 0 | 0 | 9999 | -6 |  |  | GENROU |  |  | EXST1_GE | Closed | 3.24 | 0 | ST | 6 |  | NO | 0 | 1 | 2.9474 | 0.17684 | 0.152 | 0.59 | 3.8816 | 9.11 |  | SNMALF_6_UNITS | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31465 | 1 | 1 |  | Missing BA | [17 empty] | 3.33 | 18.8 | -6.18 | 6.18 | 9999 | 0.99 | 19.79 |  | GENROU |  | IEEEG1_GE | ESAC8B_GE | Closed | 13.49 | 1.1381 | ST | 19.79 |  | NO | 0.01 | 0.15 | 3.5 | 0.69265 | 0.08 | 0.36 | 4.5 | 12.47 |  | WSENGY_1_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31465 | 2 | 2 |  | Missing BA | [17 empty] | 3.33 | 18.8 | -6.18 | 6.18 | 9999 | 0.99 | 19.79 |  | GENROU |  | IEEEG1_GE | ESAC8B_GE | Closed | 13.49 | 1.1381 | ST | 19.79 |  | NO | 0.01 | 0.15 | 3.5 | 0.69265 | 0.08 | 0.36 | 4.5 | 12.47 |  | WSENGY_1_UNIT 1 | ST (Steam Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31465 | 3 | 3 |  | Missing BA | [17 empty] | 3.33 | 18.8 | -6.18 | 6.18 | 9999 | 0.99 | 19.79 |  | GENROU |  | IEEEG1_GE | ESAC8B_GE | Closed | 13.49 | 1.1381 | ST | 19.79 |  | NO | 0.01 | 0.15 | 3.5 | 0.69265 | 0.08 | 0.36 | 4.5 | 12.47 |  | WSENGY_1_UNIT 1 | ST (Steam Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31550 | BV | BV |  | Missing BA | [17 empty] | 0 | 7.5 | -2.27 | 4.54 | 9999 | -7.5 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | ST | 5.55 |  | NO | 0 | 1e-05 | 2.7027 | 0.15 | 0.124 | 0.55 | 4.4355 | 60 |  | MCARTH_6_BIGVAL | ST (Steam Turbine) | BV
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 1 | 1 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  | REDBLF_6_UNIT | IC (Internal Combustion) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 10 | 10 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 10
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 11 | 11 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 11
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 12 | 12 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 12
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 13 | 13 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 13
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 14 | 14 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 14
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 15 | 15 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 15
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 16 | 16 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 16
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 2 | 2 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 3 | 3 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 4 | 4 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 5 | 5 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 6 | 6 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 6
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 7 | 7 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 7
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 8 | 8 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 8
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31621 | 9 | 9 |  | Missing BA | [17 empty] | 1 | 2.8 | -0.93 | 2.1 | 9999 | -2.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 1.1 | 0.48525 | IC | 3.55 | PF<0.8 | NO | 0.012 | 0.176 | 1.24 | 0.04402 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | IC (Internal Combustion) | 9
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31750 | 1 | 1 |  | Missing BA | [17 empty] | 4 | 30.15 | -9.91 | 14.6 | 9999 | 7.4e-07 | 30.15 |  | GENTPJ | PSS2B | IEEEG1_GE | ESAC6A | Closed | 25.01 | 5.8246 | ST | 36.7 |  | NO | 0 | 0.152 | 3.3 | 1.2111 | 0.17 | 0.35 | 2.0588 | 12.5 |  |  | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31763 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 2.2 | -0.33 | 1.66 | 9999 | -2.2 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.2 | 1.3584 | IT | 3 | PF<0.8 | NO | 0 | 1e-05 | 3.6963 | 0.11089 | 0.126 | 0.357 | 2.8333 | 4.16 |  | ESQUON_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31763 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 2.2 | -0.33 | 1.66 | 9999 | -2.2 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.2 | 1.3584 | IT | 3 | PF<0.8 | NO | 0 | 1e-05 | 3.6963 | 0.11089 | 0.126 | 0.357 | 2.8333 | 4.16 |  | ESQUON_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31764 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 32.5 | -10 | 16 | 9999 | -1.5 | 31 |  | GENTPJ |  | HYG3 | ESST1A_GE | Closed | 10.57 | -0.72362 | HY | 34.3 |  | NO | 0 | 1 | 1.72 | 0.58996 | 0.1 | 0.2 | 2 | 13.8 |  | MALCHQ_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31766 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 47.5 | -25.06 | 25.06 | 9999 | 2.5 | 50 |  | GENTPJ |  | HYGOV4 | ESDC1A | Closed | 47 | 1.9274 | HY | 57.5 |  | NO | 0.001 | 0.27 | 3.09 | 1.7767 | 0.1 | 0.3 | 3 | 13.8 |  | PIT4_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31766 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 47.5 | -25.06 | 25.06 | 9999 | 2.5 | 50 |  | GENTPJ |  | HYGOV4 | ESDC1A | Closed | 47 | 1.9274 | HY | 57.5 |  | NO | 0.001 | 0.27 | 3.09 | 1.7767 | 0.1 | 0.3 | 3 | 13.8 |  | PIT4_7_PL1X2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31768 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 86 | -40.46 | 40.46 | 9999 | -4 | 82 |  | GENTPJ | PSS2B | HYGOV4 | ESAC7B | Closed | 75 | 1.7653 | HY | 94.6 |  | NO | 0.006 | 0.3 | 3.538 | 3.3469 | 0.08 | 0.39 | 4.875 | 13.8 |  | BLACK_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31770 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 86 | -41.21 | 41.21 | 9999 | -4 | 82 |  | GENTPJ | PSS2B | HYGOV4 | ESAC7B | Closed | 75 | 1.9694 | HY | 94.6 |  | NO | 0.006 | 0.3 | 3.538 | 3.3469 | 0.08 | 0.39 | 4.875 | 13.8 |  | BLACK_7_UNIT 2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31772 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 40 | -19.18 | 19.18 | 9999 | -0.46 | 39.54 |  | GENTPJ | PSS2B | HYGOV | ESAC7B | Closed | 20 | -0.45166 | HY | 44 |  | NO | 0.003 | 0.3 | 2.63 | 1.1572 | 0.15 | 0.4 | 2.6667 | 13.8 |  | PIT6_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31774 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 40 | -17.62 | 17.62 | 9999 | -0.46 | 39.54 |  | GENTPJ | PSS2B | HYGOV | ESAC7B | Closed | 40 | -0.62052 | HY | 44 |  | NO | 0.003 | 0.3 | 2.63 | 1.1572 | 0.15 | 0.4 | 2.6667 | 13.8 |  | PIT6_7_UNIT 2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31776 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 56 | -21.3 | 21.3 | 9999 | -3.8 | 52.2 |  | GENTPJ | PSS2B | HYGOV | ESAC7B | Closed | 48 | 1.4913 | HY | 60 |  | NO | 0.003 | 0.274 | 2.6 | 1.56 | 0.1458 | 0.452 | 3.1001 | 13.8 |  | PIT7_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31778 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 56 | -18.97 | 18.97 | 9999 | -3.8 | 52.2 |  | GENTPJ | PSS2B | HYGOV | ESAC7B | Closed | 55.5 | 2.3604 | HY | 60 |  | NO | 0.003 | 0.274 | 2.6 | 1.56 | 0.1458 | 0.452 | 3.1001 | 13.8 |  | PIT7_7_UNIT 2 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31780 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 40 | -19.35 | 19.35 | 9999 | -6e-07 | 40 |  | GENTPJ | PSS2B | HYGOV | ESST4B | Closed | 40 | 7.4239 | HY | 44.4 |  | NO | 0.003 | 0.25 | 2.95 | 1.3098 | 0.1037 | 0.397 | 3.8284 | 13.8 |  | BUTTVL_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31782 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 60 | -20.92 | 20.92 | 9999 | -60 |  |  | GENTPJ | PSS2B | H6E | ESST4B | Closed | 59.25 | -1.2921 | HY | 67 |  | NO | 0.002 | 0.24 | 2.78 | 1.8626 | 0.1024 | 0.2751 | 2.6865 | 13.8 |  | CARBOU_7_PL4X5 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31782 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 60 | -21.69 | 21.69 | 9999 | -60 |  |  | GENTPJ | PSS2B | H6E | ESST4B | Closed | 59.25 | -1.2921 | HY | 67 |  | NO | 0.002 | 0.229 | 2.78 | 1.8626 | 0.1024 | 0.2751 | 2.6865 | 13.8 |  | CARBOU_7_PL4X5 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31784 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 125 | -10.3 | 38.3 | 9999 | -7.1 | 117.9 |  | GENTPJ | PSS2B | HYGOV | ESST4B | Closed | 65 | 3.1922 | HY | 131 |  | NO | 0.004 | 0.33 | 4.238 | 5.5518 | 0.0564 | 0.219 | 3.883 | 13.8 |  | BELDEN_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31786 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 55 | -40 | 40 | 9999 | -55 |  |  | GENTPJ | PSS2A | H6E | ESST4B | Closed | 54.25 | 2.3872 | HY | 70 | PF<-0.85 | NO | 0 | 0.19 | 4.8 | 3.36 | 0.096 | 0.277 | 2.8854 | 13.8 |  | RCKCRK_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31788 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 55 | -40.16 | 40.16 | 9999 | -55 |  |  | GENTPJ | PSS2A | H6E | ESST4B | Closed | 54.25 | 8.1529 | HY | 70 | PF<-0.85 | NO | 0 | 0.19 | 4.8 | 3.36 | 0.096 | 0.277 | 2.8854 | 13.8 |  | RCKCRK_7_UNIT 2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31790 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 60 | -9.21 | 9.21 | 9999 | -60 |  |  | GENTPJ | PSS1A | H6E | ESST1A_GE | Closed | 59 | 7.1033 | HY | 70 |  | NO | 0.002 | 0.246 | 3.804 | 2.6628 | 0.147 | 0.309 | 2.102 | 13.8 |  | POEPH_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31792 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 60 | -14.5 | 26.125 | 9999 | -60 |  |  | GENTPJ | PSS1A | H6E | ESST1A_GE | Closed | 44 | 26.125 | HY | 70 |  | NO | 0.002 | 0.216 | 3.804 | 2.6628 | 0.147 | 0.309 | 2.102 | 13.8 |  | POEPH_7_UNIT 2 | HY (Hydro) | 1
30 | PG AND E | 3002 | S. Feather Water & Power Agency |  | 31794 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 65.5 | -23.55 | 23.55 | 9999 | -0.5 | 65 |  | GENTPJ |  | HYGOV4 | ESDC1A | Closed | 56 | -7.0323 | HY | 65 |  | NO | 0.005 | 0.27 | 2.71 | 1.7615 | 0.12 | 0.47 | 3.9167 | 13.8 |  | WDLEAF_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 906 | Burney Forest Products |  | 31798 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 8 | 31.75 | -5.49 | 13.07 | 9999 | 0.01 | 31.76 |  | GENTPJ |  | GGOV1 | EXST1_GE | Closed | 31.66 | 0.10482 | ST | 34.23 |  | NO | 0 | 0.209 | 2.7353 | 0.93629 | 0.126 | 0.357 | 2.8333 | 13.2 |  | BURNYF_2_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31800 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 42 | -14 | 21 | 9999 | 2 | 44 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | JE | 46.6 |  | NO | 0 | 1 | 2.7039 | 1.26 | 0.124 | 0.55 | 4.4355 | 12.47 |  | SMPAND_7_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31802 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 23.7 | -12.95 | 12.95 | 9999 | 6 | 29.7 |  | GENTPJ |  | HYGOV | ESDC2A | Closed | 23 | -0.19294 | HY | 29.7 |  | NO | 0.003 | 0.24 | 2.388 | 0.70924 | 0.11 | 0.25 | 2.2727 | 11.5 |  | PIT3_7_PL1X3 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31802 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 23.7 | -12.95 | 12.95 | 9999 | 6 | 29.7 |  | GENTPJ |  | HYGOV | ESDC2A | Closed | 23 | -0.19294 | HY | 29.7 |  | NO | 0.003 | 0.24 | 2.388 | 0.70924 | 0.11 | 0.25 | 2.2727 | 11.5 |  | PIT3_7_PL1X3 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31802 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 23.7 | -12.95 | 12.95 | 9999 | 6 | 29.7 |  | GENTPJ |  | HYGOV | ESDC2A | Closed | 23 | -0.19294 | HY | 29.7 |  | NO | 0.003 | 0.24 | 2.388 | 0.70924 | 0.11 | 0.25 | 2.2727 | 11.5 |  | PIT3_7_PL1X3 | HY (Hydro) | 3 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31804 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 40.5 | -15.4 | 15.4 | 9999 | -0.5 | 40 |  | GENTPJ |  | HYGOV | ESDC1A | Closed | 40 | -0.18854 | HY | 44 |  | NO | 0.003 | 0.18 | 3.93 | 1.7292 | 0.0611 | 0.2131 | 3.4877 | 11.5 |  | PIT5_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31804 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 40.5 | -15.4 | 15.4 | 9999 | -0.5 | 40 |  | GENTPJ |  | HYGOV | ESDC1A | Closed | 40 | -0.18854 | HY | 44 |  | NO | 0.003 | 0.18 | 3.93 | 1.7292 | 0.0611 | 0.2131 | 3.4877 | 11.5 |  | PIT5_7_PL1X2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31806 | 3 | 3 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 39.14 | -14 | 14 | 9999 | 0.86 | 40 |  | GENTPF |  | HYGOV | REXS | Closed | 35 | -0.44115 | HY | 40 |  | NO | 0.004 | 0.208 | 3.3673 | 1.3469 | 0.1011 | 0.2688 | 2.6588 | 11.5 |  | PIT5_7_PL3X4 | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31806 | 4 | 4 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 43.3 | -15.6 | 15.6 | 9999 | 6.7 | 50 |  | GENTPF |  | HYGOV | REXS | Closed | 35 | -0.44115 | HY | 40 |  | NO | 0.004 | 0.23 | 3.3673 | 1.3469 | 0.1011 | 0.2688 | 2.6588 | 11.5 |  | PIT5_7_PL3X4 | HY (Hydro) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31808 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 25 | -13.29 | 13.29 | 9999 | 2.7 | 27.7 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 25 | 2.8311 | HY | 30.5 |  | NO | 0.002 | 0.307 | 3.084 | 0.94062 | 0.202 | 0.529 | 2.6188 | 11.5 |  | CARBOU_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31808 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 25 | -12.16 | 12.16 | 9999 | 2.7 | 27.7 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 25 | 2.8311 | HY | 27.7 |  | NO | 0.002 | 0.307 | 3.1 | 0.8587 | 0.202 | 0.529 | 2.6188 | 11.5 |  | CARBOU_7_PL2X3 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31810 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 25 | -8 | 7.6 | 9999 | 2.45 | 27.45 |  | GENTPJ |  | HYGOV | EXST1_GE | Closed | 25 | 7.6 | HY | 26.5 |  | NO | 0.002 | 0.266 | 3.084 | 0.81726 | 0.2017 | 0.5287 | 2.6212 | 11.5 |  | CARBOU_7_PL2X3 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31812 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 35 | -24.19 | 24.19 | 9999 | -0.31 | 34.69 |  | GENTPJ |  | HYGOV | EXDC4 | Closed | 35 | 5.3572 | HY | 43 | PF<-0.85 | NO | 0 | 0.184 | 3.29 | 1.4147 | 0.1156 | 0.4926 | 4.2612 | 11.5 |  | CRESTA_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31812 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 35 | -20.425 | 20.425 | 9999 | -0.31 | 34.69 |  | GENTPJ |  | HYGOV | EXDC4 | Closed | 26 | 5.3572 | HY | 41 |  | NO | 0 | 0.175 | 3.29 | 1.3489 | 0.1156 | 0.4926 | 4.2612 | 11.5 |  | CRESTA_7_PL1X2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 3002 | S. Feather Water & Power Agency |  | 31814 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 39 | -6 | 13 | 9999 | 1.64 | 40.64 |  | GENTPJ |  | HYGOV4 | ESDC1A | Closed | 7.89 | -3.8329 | HY | 40.5 |  | NO | 0.005 | 0.243 | 2.14 | 0.8667 | 0.15 | 0.55 | 3.6667 | 11.5 |  | FORBST_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31818 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 30.5 | -16.8 | 16.8 | 9999 | -0.7 | 29.8 |  | GENTPJ |  | HYG3 | EXDC2_GE | Closed | 20 | 4.6358 | HY | 38.5 |  | NO | 0.003 | 0.301 | 2.685 | 1.0337 | 0.0418 | 0.246 | 5.8852 | 11 |  | PIT1_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31818 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 30.5 | -16.8 | 16.8 | 9999 | -0.7 | 29.8 |  | GENTPJ |  | HYG3 | EXDC2_GE | Closed | 20 | 4.6358 | HY | 38.5 |  | NO | 0.003 | 0.301 | 2.685 | 1.0337 | 0.0418 | 0.246 | 5.8852 | 11 |  | PIT1_7_UNIT 2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31820 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 30 | -21.78 | 21.78 | 9999 | 2.7 | 32.7 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 29 | 5.0331 | HY | 36.3 | PF<-0.85 | NO | 0 | 0.2 | 2.426 | 0.88064 | 0.0847 | 0.2636 | 3.1122 | 11 |  | BUCKCK_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31820 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 30 | -21.78 | 21.78 | 9999 | 2.7 | 32.7 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 30 | 5.0331 | HY | 36.3 | PF<-0.85 | NO | 0 | 0.2 | 2.426 | 0.88064 | 0.0847 | 0.2636 | 3.1122 | 11 |  | BUCKCK_7_PL1X2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31822 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.7 | -1 | 2 | 9999 | -3.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 4.11 |  | NO | 0 | 1 | 2.7007 | 0.111 | 0.124 | 0.55 | 4.4355 | 9.11 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31824 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 9 | -2 | 3 | 9999 | -9 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.83 | 3 | HY | 9 |  | NO | 0 | 1 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 9.11 |  | VOLTA_2_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31824 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 0.9 | -0.2 | 0.57 | 9999 | -0.9 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.04 | 0.57 | HY | 0.9 |  | NO | 0 | 1 | 4.64 | 0.04176 | 0.152 | 0.59 | 3.8816 | 9.11 |  | VOLTA_2_UNIT 2 | HY (Hydro) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31826 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 7 | -2.9 | 3.8 | 9999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.12 | -0.085651 | HY | 7 |  | NO | 0 | 1 | 4.64 | 0.3248 | 0.152 | 0.59 | 3.8816 | 4.16 |  | SOUTH_2_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31828 | MB | MB |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 1.6 | 0 | 0 | 9999 | -1.6 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | KILARC_2_UNIT 1 | HY (Hydro) | MB
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31830 | MB | MB |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 2.4 | -0.4 | 0.6 | 9999 | -2.4 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 2.4 |  | HMLTBR_6_UNITS | HY (Hydro) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31832 | 1 | 1 |  | Missing BA | [17 empty] | 0.2 | 12.15 | -3.993 | 5.88 | 9999 | 1.05 | 13.2 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 12.15 | -3.1854 | HY | 13.5 |  | NO | 0.005 | 0.38 | 2.52 | 0.3402 | 0.1 | 0.26 | 2.6 | 6.6 |  | SLYCRK_1_UNIT1 | HY (Hydro) | 1
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 31834 | 1 | 1 |  | Missing BA | [17 empty] | 0.1 | 9.69 | -4.79 | 4.79 | 9999 | 1.31 | 11 |  | GENTPJ |  | HYGOV4 | ESDC1A | Closed | 9.69 | -1.1975 | HY | 11 |  | NO | 0.005 | 0.243 | 2.87 | 0.3157 | 0.152 | 0.59 | 3.8816 | 4.16 |  | KELYRG_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31836 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 1.5 | 0 | 0 | 9999 | -1.5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.59 | 0 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 9.11 |  | TOADTW_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31840 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 6.1 | -0.95 | 1.4 | 9999 | -6.1 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.5 | 1.4 | HY | 6 |  | NO | 0 | 1 | 4.64 | 0.2784 | 0.152 | 0.59 | 3.8816 | 9.11 |  | BLCKBT_2_STONEY | HY (Hydro) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 31842 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 4.8 | -1 | 2 | 9999 | -4.8 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.48 | -0.11904 | HY | 4 |  | NO | 0 | 1 | 4.64 | 0.1856 | 0.152 | 0.59 | 3.8816 | 9.11 |  | ELKCRK_6_STONYG | HY (Hydro) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 31842 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 0.4 | 0 | 0 | 9999 | -0.4 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.22 | 0 | HY | 4 |  | NO | 0 | 1 | 4.64 | 0.1856 | 0.152 | 0.59 | 3.8816 | 9.11 |  | ELKCRK_6_STONYG | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31846 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 7 | -2.3 | 3.5 | 9999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.27 | 0.84956 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 13.8 |  | COVERD_2_QFUNTS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31846 | 4 | 4 |  | Missing BA | [17 empty] | 0 | 5 | -1.7 | 2.5 | 9999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.58 | 0.84956 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 13.8 |  | COVERD_2_QFUNTS | HY (Hydro) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31847 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 2.6 | -0.8 | 1.3 | 9999 | -2.6 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.6 | 1.3 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31848 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 2 | -0.7 | 1 | 9999 | -2 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.07 | 0.15 | HY | 7 |  | NO | 0 | 1 | 4.64 | 0.3248 | 0.152 | 0.59 | 3.8816 | 4.16 |  |  | HY (Hydro) | 2
30 | PG AND E | 3006 | Trinity Public Utility District |  | 31850 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 0.3 | -0.1 | 0.2 | 9999 | -0.3 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 0.4 |  | NO | 0 | 1 | 4.64 | 0.01856 | 0.152 | 0.59 | 3.8816 | 9.11 |  | GRSCRK_6_BGCKWW | HY (Hydro) | 1
30 | PG AND E | 3006 | Trinity Public Utility District |  | 31850 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 4.8 | -1.6 | 2.4 | 9999 | -4.8 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 9.11 |  | GRSCRK_6_BGCKWW | HY (Hydro) | 2
30 | PG AND E | 3006 | Trinity Public Utility District |  | 31852 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 0.8 | -0.3 | 0.4 | 9999 | -0.8 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 0.89 |  | NO | 0 | 1 | 4.64 | 0.041296 | 0.152 | 0.59 | 3.8816 | 9.11 |  | LEWSTN_7_WEBRFL | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31854 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5 | -2.08 | 2.42 | 9999 | 0.65 | 5.65 |  | GENTPJ |  | HYGOV | ESAC7B | Closed | 2.31 | -0.44068 | HY | 5.556 |  | NO | 0 | 0.199 | 2 | 0.11112 | 0.111 | 0.267 | 2.4054 | 4.16 |  | OLSEN_60_GN1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31855 | 3 | 3 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 3 | -1 | 1.5 | 9999 | -3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.35 | -1 | HY | 3 |  | NO | 0 | 1 | 4.64 | 0.1392 | 0.152 | 0.59 | 3.8816 | 9.11 |  | OLSEN_2_UNIT | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31856 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 0.9 | 0 | 0 | 9999 | -0.9 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.47 | 0 | HY | 0.9 |  | NO | 0 | 1 | 4.64 | 0.04176 | 0.152 | 0.59 | 3.8816 | 2.4 |  | COWCRK_2_UNIT unit 1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31856 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 0.9 | 0 | 0 | 9999 | -0.9 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.47 | 0 | HY | 0.9 |  | NO | 0 | 1 | 4.64 | 0.04176 | 0.152 | 0.59 | 3.8816 | 2.4 |  | COWCRK_2_UNIT unit 2 | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31862 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 2 | -0.7 | 1 | 9999 | -2 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.15 | 0.15 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 9.11 |  | DEADCK_1_UNIT | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31868 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 2 | -0.7 | 1 | 9999 | -2 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.69 | 0.15 | HY | 6 |  | NO | 0 | 1 | 4.64 | 0.2784 | 0.152 | 0.59 | 3.8816 | 4.16 |  | HATLOS_6_QFUNTS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31870 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 11.6 | -3.8 | 5.8 | 9999 | -11.6 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 10 | -3.8 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 9.11 |  | FORKBU_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31870 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 1.7 | -0.6 | 0.9 | 9999 | -1.7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.7 | -0.6 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 9.11 |  | FORKBU_6_UNIT | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31872 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 1 | -0.3 | 0.5 | 9999 | -1 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.22 | 0.1 | HY | 1 |  | NO | 0 | 1 | 4.64 | 0.0464 | 0.152 | 0.59 | 3.8816 | 9.11 |  | CLOVER_2_UNIT | HY (Hydro) | 1
30 | PG AND E | 187 | Sierra Pacific Industries |  | 31874 | 1 | 1 |  | Missing BA | [17 empty] | 1.7 | 20 | -12.39 | 12.39 | 9999 | 3.53 | 23.53 |  | GENTPJ |  | IEEEG1_GE | ESAC8B_GE | Open | 0 | 0 | ST | 23.53 |  | NO | 0 | 0.23 | 2.7 | 0.63531 | 0.12 | 0.4 | 3.3333 | 13.8 |  | SPBURN_2_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31888 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 8.12 | -6 | 6 | 9999 | 2.38 | 10.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 8.02 | 4.4279 | GT | 9 | PF<-0.85 | NO | 0 | 0.206 | 4.3022 | 0.3872 | 0.14 | 0.574 | 4.1 | 4.16 |  | OROVIL_12_GN1 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31890 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 9 | -2.5 | 4 | 9999 | 11 | 20 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 20 |  | NO | 0 | 1 | 2.7 | 0.54 | 0.126 | 0.357 | 2.8333 | 9.11 |  | PACORO_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31890 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 9 | -2.5 | 4 | 9999 | -9 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | ST | 20 |  | NO | 0 | 1 | 2.7 | 0.54 | 0.126 | 0.357 | 2.8333 | 9.11 |  |  | ST (Steam Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31892 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 10.5 | -3.8 | 5.7 | 9999 | 2 | 12.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 11 |  | NO | 0 | 1 | 2.909 | 0.31999 | 0.126 | 0.357 | 2.8333 | 9.11 |  | MTNLAS_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31895 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 5.625 | -1.95 | 2.72 | 999 | 0.625 | 6.25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 5.32 | 2.72 | ST | 6.25 |  | NO | 0 | 1e-05 | 1 | 0.0625 | 0.227 | 0.779 | 3.4317 | 13.8 |  | COLPIN_6_COLPBM | ST (Steam Turbine) | 1
30 | PG AND E | 187 | Sierra Pacific Industries |  | 31896 | 1 | 1 |  | Missing BA | [17 empty] | 10.3 | 35.27 | -3.1 | 17.07 | 9999 | 3.915 | 39.185 |  | GENTPJ | PSS2B | IEEEG1_GE | ESAC6A | Closed | 35.27 | 5.2441 | ST | 39.185 |  | NO | 0 | 0.143 | 3.68 | 1.442 | 0.082 | 0.25 | 3.0488 | 13.8 |  | SPQUIN_6_SRPCQU | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31898 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 18.804 | -8.15 | 8.15 | 9999 | -0.154 | 18.65 |  | GENTPJ |  | HYGOV | ESDC4B | Closed | 10 | -0.92019 | HY | 20.5 |  | NO | 0 | 0.243 | 2.75 | 0.56375 | 0.06 | 0.28 | 4.6667 | 6.9 |  | DSABLA_7_UNIT | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31900 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 20 | -4 | 7 | 9999 | 2 | 22 |  | GENTPJ |  | HYG3 | EXST1_GE | Closed | 20 | 2.7738 | HY | 22 |  | NO | 0 | 1 | 2.466 | 0.54252 | 0.0484 | 0.2027 | 4.188 | 6.9 |  | GRIZLY_1_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31902 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 8.5 | -0.77 | 0.77 | 9999 | -8.5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 8.5 | 0 | HY | 9 |  | NO | 0.005 | 0.243 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 6.6 |  | HATCR1_7_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31904 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 8.59 | -9 | 9 | 9999 | 0.41 | 9 |  | GENTPJ |  | HYGOV | EXST1_GE | Closed | 5 | 0.93908 | HY | 9 | PF<0.8 | NO | 0.005 | 0.338 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 6.6 |  | HATCR2_7_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31906 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 13 | -5 | 7 | 9999 | -13 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 4.52 | -2.6465 | HY | 14 |  | NO | 0 | 1 | 2.46 | 0.3444 | 0.04 | 0.2577 | 6.4425 | 6.6 |  | COLEMN_2_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31908 | MB | MB |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 8 | -2.5 | 4.5 | 9999 | -8 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 4.16 |  | INSKIP_2_UNIT | HY (Hydro) | MB
30 | PG AND E | 339 | Hatchet Ridge Wind, LLC |  | 31914 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 24 | -12 | 8.28 | 9999 | -24 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 7.2 | -2.2493 | W4 | 26.67 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 1
30 | PG AND E | 339 | Hatchet Ridge Wind, LLC |  | 31914 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 24 | -12 | 8.28 | 9999 | -24 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 7.2 | -2.2493 | W4 | 26.67 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 2
30 | PG AND E | 339 | Hatchet Ridge Wind, LLC |  | 31914 | 3 | 3 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 24 | -12 | 8.28 | 9999 | -24 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 7.2 | -2.2493 | W4 | 26.67 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 3
30 | PG AND E | 339 | Hatchet Ridge Wind, LLC |  | 31914 | 4 | 4 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 19.2 | -9.6 | 6.62 | 9999 | -19.2 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 5.76 | -2.2493 | W4 | 21.33 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 4
30 | PG AND E | 339 | Hatchet Ridge Wind, LLC |  | 31914 | 5 | 5 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 12 | -6 | 4.41 | 9999 | -12 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 3.6 | -2.2493 | W4 | 13.33 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 5
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31923 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 167.4 | -66.7 | 112.5 | 9999 | 6.86 | 174.26 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 66.4 | -2.4122 | CT | 213.5 |  | NO | 0 | 0.18 | 5.64 | 12.0414 | 0.064 | 0.238 | 3.7187 | 18 |  | COLUSA_2_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31924 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 167.4 | -66.7 | 112.5 | 9999 | 6.86 | 174.26 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 150 | 6.6172 | CT | 213.5 |  | NO | 0 | 0.18 | 5.64 | 12.0414 | 0.064 | 0.238 | 3.7187 | 18 |  | COLUSA_2_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31925 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 327.9 | -128.3 | 216.5 | 9999 | -327.9 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 84.6794 | 5.3119 | CA | 411 |  | NO | 0 | 0.265 | 2.78 | 11.4258 | 0.061 | 0.27 | 4.4262 | 18 |  | COLUSA_2_PL1X3 | CA (Combined Cycle Steam Part) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31926 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 8.418 | 1.9368 | 1.9368 | 999 | -8.418 | [6 empty] | Closed | 5.8926 | 1.9368 | PV | 9.9 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2042-RD | PV (Photovoltaic) | RE
30 | PG AND E | 142 | Calpeak Power |  | 32150 | 1 | 1 |  | Missing BA | [17 empty] | 18 | 60.5 | -14 | 37.49 | 9999 | 10.676 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 60.5 | -0.14655 | JE | 71.176 |  | NO | 0 | 0.18 | 2 | 1.4235 | 0.13 | 0.45 | 3.4615 | 13.8 |  | VACADX_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32154 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 29.07 | -5.3 | 14.07 | 9999 | -0.42 | 28.65 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 27.5 | -3.3049 | ST | 32.3 |  | NO | 0 | 0.17 | 3.6 | 1.1628 | 0.08 | 0.25 | 3.125 | 13.8 |  | WADHAM_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32156 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 28 | -11 | 13 | 9999 | 0.0099999 | 28.01 |  | GENTPJ |  | IEEEG1_GE | ESAC1A | Closed | 19.62 | 4.4974 | ST | 37 |  | NO | 0.001 | 0.148 | 4.97 | 1.8389 | 0.08 | 0.36 | 4.5 | 13.8 |  | BIOMAS_1_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32162 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.1 | -1 | 1.5 | 9999 | -3.1 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 3 |  | NO | 0 | 1 | 4.2467 | 0.1274 | 0.126 | 0.357 | 2.8333 | 9.11 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32164 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 0.8 | -0.3 | 0.4 | 9999 | -0.8 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | ST | 2 |  | NO | 0 | 1 | 4.73 | 0.0946 | 0.126 | 0.357 | 2.8333 | 9.11 |  | SUISUN_7_CTYFAI | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32164 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 1.5 | -0.5 | 0.8 | 9999 | -1.5 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | ST | 2 |  | NO | 0 | 1 | 4.73 | 0.0946 | 0.126 | 0.357 | 2.8333 | 9.11 |  | SUISUN_7_CTYFAI | ST (Steam Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32166 | RN | RN |  | Missing BA | [17 empty] | 0 | 14 | 0 | 0 | 9999 | -14 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 3.88 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32172 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 160.2 | -56.85 | 56.85 | 9999 | -160.2 |  |  | WT2G |  | WT2T | WT2E | Closed | 75 | -27.8181 | W2 | 169.99 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BRDSLD_2_HIWIND | W2 (Wind Turbine, Type 2) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32172 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 1.79 | -0.575 | 0.575 | 9999 | -1.79 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 0.537 | -0.575 | W3 | 1.88 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 32173 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [9 empty] | 20 | 48 | -7.9 | 21.5 | 9999 | 3.25 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 48 | 1.0139 | JE | 71.176 |  | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.103 | 0.359 | 3.4854 | 13.8 |  | LMBEPK_2_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32174 | 3 | 3 |  | Missing BA | [7 empty] | Unreas H | [9 empty] | 20.5 | 48.7 | -11.6 | 27.83 | 9999 | 2.55 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 48.5 | 0.92142 | JE | 71.176 |  | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.13 | 0.384 | 2.9538 | 13.8 |  |  | JE (Jet Engine) | 3
30 | PG AND E | 470 | Calpine Corp. |  | 32175 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  | Unreas H | [9 empty] | 20 | 46 | -11.2918 | 27 | 9999 | 5.25 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 46 | -11.2918 | JE | 71.176 |  | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.093 | 0.349 | 3.7527 | 13.8 |  |  | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32179 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 78.2 | -30.3 | 30.3 | 9999 | -78.2 |  |  | WT4G |  |  | WT4E | Closed | 23.46 | -30.3 | W4 | 78.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BRDSLD_2_MTZUM2 | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32181 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 150 | -72.65 | 49.3 | 9999 | -150 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 50 | -6.1063 | W3 | 167 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  | BRDSLD_2_SHILO1 | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32185 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [7 empty] | Missing Sub R/X |  | 0 | 60.5 | -22.2 | 37.5 | 9999 | -9.25 | 51.25 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 48.5 | 10.4973 | JE | 71.176 |  | NO | 0 | 1e-05 | 1.17 | 0.83276 | 0.1 | 0.285 | 2.85 | 13.8 |  | WOLFSK_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32188 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 36.8 | -14.26 | 14.26 | 9999 | -36.8 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 11.04 | -14.26 | W4 | 39.47 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | WNDSTR_2_WIND | W4 (Wind Turbine, Type 4) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32191 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 101.5 | 0 | 0 | 9999 | -101.5 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 30.45 | 0 | W3 | 118.8 |  | NO | 0 | 0.45 | 0 |  |  |  | NAN | 0.575 |  | BRDSLD_2_SHLO3A | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32194 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 101.5 | 0 | 0 | 9999 | -101.5 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 35 | 0 | W3 | 118.8 |  | NO | 0 | 0.45 | 0 |  |  |  | NAN | 0.575 |  | BRDSLD_2_SHLO3B | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32450 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 170.5 | -45 | 57 | 9999 | 4.5 | 175 |  | GENTPJ | PSS2B | HYG3 | ESDC4B | Closed | 120 | 55.7087 | HY | 175 |  | NO | 0 | 1e-05 | 2.87 | 5.0225 | 0.15 | 0.35 | 2.3333 | 13.8 |  | COLGAT_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32451 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [9 empty] | 0 | 50 | -16.4 | 31 | 9999 | 0 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Open | 0 | 0 | JE | 71.2 |  | NO | 0 | 0.247 | 1.17 | 0.83304 | 0.112 | 0.461 | 4.1161 | 13.8 |  | BOGUE_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32452 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 170.5 | -45 | 60 | 9999 | 4.5 | 175 |  | GENTPJ | PSS2B | HYG3 | ESDC4B | Open | 0 | 0 | HY | 175 |  | NO | 0 | 1e-05 | 2.87 | 5.0225 | 0.15 | 0.35 | 2.3333 | 13.8 |  | COLGAT_7_UNIT 2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32454 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 50.64 | -30.275 | 30.275 | 9999 | -1.64 | 49 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 48.1 | -3.597 | HY | 59 |  | NO | 0 | 1 | 3.17 | 1.8703 | 0.28 | 0.47 | 1.6786 | 13.8 |  | DRUM_7_UNIT 5 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 3001 | Placer County Water Agency |  | 32456 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 63 | -25.6 | 25.6 | 9999 | 5 | 68 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 35 | 15.6151 | HY | 68 |  | NO | 0.004 | 0.243 | 2.867 | 1.9496 | 0.17 | 0.29 | 1.7059 | 13.8 |  | MIDFRK_13.8_GN1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 3001 | Placer County Water Agency |  | 32456 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 64 | -23 | 23 | 9999 | 4 | 68 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 35 | 15.6151 | HY | 68 |  | NO | 0.004 | 0.243 | 2.867 | 1.9496 | 0.17 | 0.29 | 1.7059 | 13.8 |  | MIDFRK_13.8_GN2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 3001 | Placer County Water Agency |  | 32458 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 83 | -30 | 30 | 9999 | 5 | 88 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 75 | 24.8045 | HY | 88 |  | NO | 0.003 | 0.24 | 2.9 | 2.552 | 0.15 | 0.3 | 2 | 13.8 |  | RALSTN_13.8_GN1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32460 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 12.174 | -6.96 | 6.96 | 9999 | -12.174 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 3.29 | 3.0373 | HY | 14.1 |  | NO | 0 | 0.24 | 3.36 | 0.47376 | 0.1 | 0.22 | 2.2 | 13.2 |  | NWSCTL_7_UNIT1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32462 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 40 | -8 | 16 | 9999 | 1.5002 | 41.5002 |  | GENTPF |  | HYGOV | EXST4B | Closed | 28.06 | 0.64517 | HY | 41 |  | NO | 0 | 1 | 2.3073 | 0.94599 | 0.1793 | 0.595 | 3.3185 | 11.5 |  | CHICPK_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32464 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 22.13 | -16.32 | 16.32 | 9999 | -22.13 |  |  | GENTPJ |  | H6E | ESDC4B | Closed | 20.78 | -0.82462 | HY | 27.5 | PF<-0.85 | NO | 0 | 0.172 | 2.78 | 0.7645 | 0.0726 | 0.313 | 4.3113 | 11 |  | DUTCH1_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32466 | 1 | 1 |  | Missing BA | [17 empty] | 1.1 | 10.7 | -4.9 | 5.43 | 9999 | -10.7 |  |  | GENTPJ |  |  | ESST4B | Open | 0 | 0 | HY | 12 |  | NO | 0.005 | 0.26 | 2.95 | 0.354 | 0.08 | 0.31 | 3.875 | 11 |  | NAROW1_2_UNIT | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32468 | 1 | 1 |  | Missing BA | [17 empty] | 7.5 | 53.3 | -10.3 | 11.1 | 9999 | -53.3 |  |  | GENTPJ |  |  | ESDC1A | Closed | 53.3 | -7.6362 | HY | 55 |  | NO | 0 | 0.205 | 4.9 | 2.695 | 0.09 | 0.34 | 3.7778 | 13.8 |  | NAROW2_2_UNIT | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32470 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 6.5 | -3 | 4 | 9999 | -6.5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 5.6 | 1.0049 | HY | 7 |  | NO | 0 | 1 | 4.64 | 0.3248 | 0.152 | 0.59 | 3.8816 | 9.11 |  | CAMPFW_7_FARWST | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32472 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 7 | -2.9 | 3.5 | 9999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.73 | 2.1499 | HY | 19 |  | NO | 0 | 1 | 4.64 | 0.8816 | 0.152 | 0.59 | 3.8816 | 9.11 |  | SPAULD_6_UNIT12 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32472 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 4.4 | -1 | 1.9 | 9999 | -4.4 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.71 | 1.9 | HY | 19 |  | NO | 0 | 1 | 4.64 | 0.8816 | 0.152 | 0.59 | 3.8816 | 9.11 |  | SPAULD_6_UNIT12 | HY (Hydro) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32472 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 5.8 | -2 | 4 | 9999 | -5.8 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.53 | 2.1499 | HY | 19 |  | NO | 0 | 1 | 4.64 | 0.8816 | 0.152 | 0.59 | 3.8816 | 9.11 |  | SPAULD_6_UNIT 3 | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32474 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5.783 | 0 | 0 | 9999 | -5.783 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.41 | 0 | HY | 6.875 |  | NO | 0 | 0.243 | 4.64 | 0.319 | 0.152 | 0.59 | 3.8816 | 2.3 |  | DEERCR_6_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32476 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 12.2 | -5.78 | 5.78 | 9999 | -12.2 |  |  | GENTPJ |  |  | ESST4B | Closed | 8.3 | 4.4025 | HY | 13.5 |  | NO | 0 | 1 | 2.52 | 0.3402 | 0.1 | 0.36 | 3.6 | 6.6 |  | ROLLIN_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32478 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 10.4 | -10.07 | 10.07 | 9999 | -10.4 |  |  | GENTPJ |  | H6E | ESST4B | Open | 0 | 0 | HY | 17 | PF<0.8 | NO | 0 | 0.29 | 3.5 | 0.595 | 0.11 | 0.242 | 2.2 | 6.6 |  | HALSEY_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32480 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.6 | -1 | 2 | 9999 | -3.6 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.18 | 1.5168 | HY | 4 |  | NO | 0 | 1 | 4.64 | 0.1856 | 0.152 | 0.59 | 3.8816 | 9.11 |  | BOWMN_6_HYDRO | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32484 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 6 | -2 | 1.9 | 9999 | -6 |  |  | GENTPF |  |  | EXDC1 | Closed | 2.92 | 1.9 | HY | 7 |  | NO | 0 | 1 | 2.2713 | 0.15899 | 0.1904 | 0.548 | 2.8782 | 9.11 |  | OXBOW_6_DRUM | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32486 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 0.5 | 0 | 0 | 9999 | -0.5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.47 | 0 | HY | 0.56 |  | NO | 0 | 1 | 4.64 | 0.025984 | 0.152 | 0.59 | 3.8816 | 9.11 |  | FMEADO_6_HELLHL | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32488 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 6 | -2 | 3 | 9999 | -6 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.4 | 0.73236 | HY | 9 |  | NO | 0 | 1 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 9.11 |  | HAYPRS_6_HAYHD1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32488 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 8.7 | -2.5 | 4.3 | 9999 | -8.7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.93 | 0.73236 | HY | 6 |  | NO | 0 | 1 | 4.64 | 0.2784 | 0.152 | 0.59 | 3.8816 | 9.11 |  | HAYPRS_6_HAYHD2 | HY (Hydro) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 32490 | 1 | 1 |  | Missing BA | [17 empty] | 6.29 | 30.35 | -12.8 | 17.9 | 9999 | 9.65 | 40 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Open | 0 | 0 | JE | 41.111 |  | NO | 0 | 0.126 | 1.8 | 0.74 | 0.08 | 0.264 | 3.3 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32491 | 2 | 2 |  | Missing BA | [17 empty] | 6.29 | 30.35 | -12.8 | 17.9 | 9999 | 9.65 | 40 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Open | 0 | 0 | JE | 41.111 |  | NO | 0 | 0.126 | 1.8 | 0.74 | 0.08 | 0.264 | 3.3 | 13.8 |  |  | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32492 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 49.5 | -14 | 22 | 9999 | -3.5 | 46 |  | GENROU |  | GGOV1 | ESAC1A | Closed | 49.2 | -4.5869 | JE | 49.5 |  | NO | 0 | 1 | 2.15 | 1.0643 | 0.13 | 0.4 | 3.0769 | 13.8 |  | GRNLF2_1_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32494 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 20.4 | 49.9 | -18 | 24.16 | 9999 | -1.29e-06 | 49.9 |  | GENTPJ |  | GGOV1 | ESAC1A | Closed | 49 | -2.4411 | JE | 55.448 |  | NO | 0 | 0.155 | 2 | 1.109 | 0.2 | 0.6 | 3 | 13.8 |  | YUBACT_1_SUNSWT | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32496 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 20.4 | 49.04 | -16.95 | 51.5 | 9999 | 2.21 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.18 | 0.371 | 2.0611 | 13.8 |  | YUBACT_6_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 187 | Sierra Pacific Industries |  | 32498 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 18.3 | -5.1 | 11.2 | 9999 | 3.34 | 21.64 |  | GENTPJ |  | IEEEG1_GE | ESAC6A | Closed | 9.55 | 7.4074 | ST | 21.64 |  | NO | 0 | 1 | 2.7 | 0.58428 | 0.1 | 0.25 | 2.5 | 12.5 |  | SPILI_2_UNIT1 | ST (Steam Turbine) | 1
30 | PG AND E | 963 | Rio Bravo Rocklin |  | 32500 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 16 | 27.65 | -10 | 17.35 | 9999 | 0.35 | 28 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 23.38 | 9.2514 | ST | 32.94 |  | NO | 0 | 0.17 | 4.2 | 1.3835 | 0.092 | 0.275 | 2.9891 | 12.47 |  | ULTRCK_2_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32502 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 24.57 | -4.9 | 10.8 | 9999 | -24.57 |  |  | GENTPJ | PSS2B |  | ESDC4B | Closed | 17.2 | -2.0492 | HY | 27.3 |  | NO | 0.002 | 0.322 | 2.5 | 0.6825 | 0.198 | 0.51 | 2.5758 | 6.9 |  | DUTCH2_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32504 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 13.08 | -7.34 | 7.34 | 9999 | -13.08 |  |  | GENTPJ |  |  | ESST4B | Closed | 5.2 | 2.2192 | HY | 15 |  | NO | 0 | 0.28 | 3.884 | 0.5826 | 0.1 | 0.25 | 2.5 | 6.6 |  | DRUM_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32504 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 13.08 | -7.34 | 7.34 | 9999 | -13.08 |  |  | GENTPJ |  |  | ESST4B | Closed | 5.2 | 2.2192 | HY | 15 |  | NO | 0 | 0.28 | 3.884 | 0.5826 | 0.1 | 0.25 | 2.5 | 6.6 |  | DRUM_7_PL1X2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32506 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 13.838 | -5.785 | 5.785 | 9999 | -13.838 |  |  | GENTPJ |  |  | ESST4B | Closed | 6.09 | 2.2348 | HY | 15 |  | NO | 0 | 0.26 | 3.884 | 0.5826 | 0.1 | 0.25 | 2.5 | 6.6 |  | DRUM_7_PL3X4 | HY (Hydro) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32506 | 4 | 4 |  | Missing BA | [17 empty] | 0 | 15.222 | -6.364 | 6.364 | 9999 | -15.222 |  |  | GENTPJ |  |  | ESST4B | Closed | 6.71 | 2.2348 | HY | 16.5 |  | NO | 0 | 0.3 | 4.376 | 0.72204 | 0.12 | 0.29 | 2.4167 | 6.6 |  | DRUM_7_PL3X4 | HY (Hydro) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32508 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 16 | -5.7 | 5.7 | 9999 | -16 |  |  | GENTPJ |  |  | ESST2A | Closed | 14 | -3.9406 | HY | 17 |  | NO | 0.003 | 0.15 | 3.6 | 0.612 | 0.129 | 0.263 | 2.0388 | 4.16 |  | FMEADO_4.16_GN1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32512 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 20.1 | -6 | 9 | 9999 | -20.1 |  |  | GENTPF |  |  | EXDC1 | Closed | 8.85 | 9 | HY | 25 |  | NO | 0 | 1 | 2.612 | 0.653 | 0.169 | 0.556 | 3.2899 | 12.47 |  | WISE_1_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32513 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 10 | -3.3 | 7.5 | 9999 | -10 |  |  | GENTPJ |  |  |  | Closed | 7.4 | 4.0131 | HY | 12.5 | PF<0.8 | NO | 0 | 1e-05 | 4.64 | 0.58 | 0.152 | 0.59 | 3.8816 | 21.6 |  | ELDORO_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32514 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 10 | -3.3 | 7.5 | 9999 | -10 |  |  | GENTPJ |  |  |  | Closed | 7.78 | 4.0289 | HY | 12.5 | PF<0.8 | NO | 0 | 1e-05 | 4.64 | 0.58 | 0.152 | 0.59 | 3.8816 | 21.6 |  | ELDORO_7_UNIT 2 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32700 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 5 | 0 | 0 | 9999 | -5 |  |  | GENTPF |  |  | EXAC1 | Closed | 3.66 | 0 | HY | 5 |  | NO | 0 | 1 | 2.6998 | 0.13499 | 0.5 | 1.22 | 2.44 | 9.11 |  | MONTPH_7_UNITS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32700 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 5 | 0 | 0 | 9999 | -5 |  |  | GENTPF |  |  | EXAC1 | Closed | 3.66 | 0 | HY | 5 |  | NO | 0 | 1 | 2.6998 | 0.13499 | 0.5 | 1.22 | 2.44 | 9.11 |  | MONTPH_7_UNITS | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32700 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 1.5 | 0 | 0 | 9999 | -1.5 |  |  | GENTPF |  |  | EXAC1 | Closed | 1.11 | 0 | HY | 1 |  | NO | 0 | 1 | 3.54 | 0.0354 | 0.5 | 1.22 | 2.44 | 9.11 |  | MONTPH_7_UNITS | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32741 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 17.1 | 23.04 | -9 | 16.9 | 9999 | 5.76 | 28.8 |  | GENROU |  | GGOV1 | ESAC8B_GE | Closed | 17.1 | 16.9 | CT | 28.8 |  | NO | 0 | 0.175 | 2 | 0.576 | 0.04 | 0.18 | 4.5 | 12.47 |  | GRZZLY_1_BERKLY | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32741 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0.3 | 5.5 | -3 | 4.1 | 9999 | -5.5 |  |  | GENROU |  |  | ESAC1A | Closed | 3.32 | 4.1 | CA | 6.88 |  | NO | 0 | 0.199 | 1.15 | 0.07912 | 0.08 | 0.23 | 2.875 | 12.47 |  |  | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32741 | RN | RN |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 0.326 | 0 | 0 | 9999 | -0.326 |  |  | DER_A |  |  |  | Closed | 0.2282 | 0 | PV | 0.326 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32900 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 240 | -62.5 | 66.785 | 9999 | 5 | 245 |  | GENROU | PSS2A | GGOV1 | ESST4B | Closed | 226.42 | 64.129 | ST | 290.6 |  | NO | 0 | 1 | 4.986 | 14.4893 | 0.068 | 0.25 | 3.6765 | 18 |  | CROKET_7_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 437 | Dynegy Inc. |  | 32901 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 14.8 | 54 | -23.2 | 26.15 | 9999 | -2.15e-06 | 54 |  | GENROU |  | GGOV1 | REXS | Open | 0 | 0 | JE | 74.5 |  | NO | 0 | 0.134 | 2.17 | 1.6167 | 0.17 | 0.568 | 3.3412 | 13.8 |  | OAK C_7_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 437 | Dynegy Inc. |  | 32903 | 3 | 3 |  | Missing BA | [14 empty] | Missing PS |  |  | 15 | 54 | -23.2 | 32.4 | 9999 | -2.15e-06 | 54 |  | GENROU |  | GGOV1 | REXS | Closed | 54 | 4.0556 | JE | 74.5 |  | NO | 0 | 0.234 | 2.17 | 1.6167 | 0.17 | 0.568 | 3.3412 | 13.8 |  | OAK C_7_ | JE (Jet Engine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32910 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 16.7 | -13 | 19.7 | 9999 | 2 | 18.7 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 11.75 | 19.7 | GT | 16 | PF<0.8 | NO | 0 | 1 | 4.2706 | 0.6833 | 0.126 | 0.357 | 2.8333 | 12 |  | UNOCAL_1_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32910 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 16.6 | -13 | 19.7 | 9999 | 2 | 18.6 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 11.69 | 19.7 | GT | 16 | PF<0.8 | NO | 0 | 1 | 4.2706 | 0.6833 | 0.126 | 0.357 | 2.8333 | 12 |  | UNOCAL_1_UNITS | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32910 | 3 | 3 |  | Missing BA |  |  |  | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 16.6 | -12.9 | 19.6 | 9999 | 2 | 18.6 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 11.69 | 19.6 | GT | 16 | PF<0.8 | NO | 0 | 1 | 4.2706 | 0.6833 | 0.126 | 0.357 | 2.8333 | 12 |  | UNOCAL_1_UNITS | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32920 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 27.4 | -8.55 | 13 | 9999 | 2 | 29.4 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 30 |  | NO | 0 | 1 | 3.7667 | 1.13 | 0.126 | 0.357 | 2.8333 | 9.11 |  | UNCHEM_1_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32921 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 20 | 54 | -15 | 32.49 | 9999 | 2 | 56 |  | GENTPF |  | GGOV1 | EXDC1 | Closed | 54 | 28.0225 | GT | 51 |  | NO | 0 | 1 | 5.098 | 2.6 | 0.1929 | 0.711 | 3.6858 | 13.8 |  | STOILS_1_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32922 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 20 | 54 | -15 | 32.49 | 9999 | 2 | 56 |  | GENTPF |  | GGOV1 | EXDC1 | Closed | 54 | 27.9771 | GT | 51 |  | NO | 0 | 1 | 5.098 | 2.6 | 0.1929 | 0.711 | 3.6858 | 13.8 |  | STOILS_1_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32923 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 20 | 25 | -15 | 7.809 | 9999 | 1 | 26 |  | GENTPF |  | GGOV1 | EXDC1 | Closed | 25 | 1.6498 | GT | 25 |  | NO | 0 | 1 | 5.098 | 1.2745 | 0.1929 | 0.711 | 3.6858 | 13.8 |  | STOILS_1_UNITS | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33102 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 19.2 | 0.1 | 4.3 | 9999 | -19.2 |  |  | WT4G |  |  | WT4E | Closed | 13.44 | 0.1 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33103 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 999 | -10 | [6 empty] | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21.6 |  | 1787-RD | PV (Photovoltaic) | RE
30 | PG AND E | 470 | Calpine Corp. |  | 33107 | 1 | 1 |  | Missing BA | [17 empty] | 70 | 283.1 | -41.4 | 109.5 | 9999 | -283.1 |  |  | GENTPJ | PSS2A |  | ESST1A_GE | Open | 0 | 0 | CA | 360 |  | NO | 0 | 1e-05 | 4.21 | 15.156 | 0.118 | 0.298 | 2.5254 | 18 |  | DELTA_2_PL1X4 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33108 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 122.8 | 179.6 | -64.8 | 84.4 | 9999 | 6.4 | 186 |  | GENTPJ | PSS2B | GGOV3 | ESST6B | Open | 0 | 0 | CT | 250 |  | NO | 0 | 1e-05 | 5.92 | 14.8 | 0.068 | 0.182 | 2.6765 | 18 |  | DELTA_2_PL1X4 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33109 | 1 | 1 |  | Missing BA | [17 empty] | 122.9 | 166.9 | -66.9 | 70.1 | 9999 | 19.1 | 186 |  | GENTPJ | PSS2B | GGOV3 | ESST6B | Open | 0 | 0 | CT | 250 |  | NO | 0 | 1e-05 | 4.953 | 12.3825 | 0.067 | 0.204 | 3.0448 | 18 |  | DELTA_2_PL1X4 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33110 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 122.6 | 166.9 | -60.7 | 89.6 | 9999 | 19.1 | 186 |  | GENTPJ | PSS2B | GGOV3 | ESST6B | Open | 0 | 0 | CT | 250 |  | NO | 0 | 1e-05 | 5.92 | 14.8 | 0.068 | 0.182 | 2.6765 | 18 |  | DELTA_2_PL1X4 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33111 | 1 | 1 |  | Missing BA | [17 empty] | 85 | 169 | -66 | 117 | 9999 | 0.59999 | 169.6 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 90 | 36.4228 | GT | 234 |  | NO | 0 | 0.534 | 4.76 | 11.1384 | 0.075 | 0.269 | 3.5867 | 18 |  | LMEC_1_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33112 | 1 | 1 |  | Missing BA | [17 empty] | 85 | 169 | -66 | 117 | 9999 | 0.59999 | 169.6 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 90 | 36.4228 | GT | 234 |  | NO | 0 | 0.534 | 4.76 | 11.1384 | 0.075 | 0.269 | 3.5867 | 18 |  | LMEC_1_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33113 | 1 | 1 |  | Missing BA | [17 empty] | 45 | 249 | -66 | 117 | 9999 | -249 |  |  | GENTPJ | PSS2B |  | ESST4B | Open | 0 | 0 | GT | 330 |  | NO | 0 | 0.822 | 3.41 | 11.253 | 0.11 | 0.274 | 2.4909 | 18 |  | LMEC_1_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33118 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 207 | -69 | 104 | 9999 | -207 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 150 | 30.935 | GT | 251 |  | NO | 0 | 0.201 | 3.9 | 9.789 | 0.063 | 0.42 | 6.6667 | 18 |  | GATWAY_2_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33119 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 196 | -65 | 98 | 9999 | -22 | 174 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 150 | 29.3777 | GT | 239 |  | NO | 0 | 0.201 | 4.7 | 11.233 | 0.068 | 0.58 | 8.5294 | 18 |  | GATWAY_2_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33120 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 196 | -65 | 98 | 9999 | -22 | 174 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 150 | 29.3777 | GT | 239 |  | NO | 0 | 0.201 | 4.7 | 11.233 | 0.068 | 0.58 | 8.5294 | 18 |  | GATWAY_2_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33136 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 4.4 | -0.7 | 2.2 | 9999 | -4.4 |  |  | GENTPF |  |  | EXST1_GE | Closed | 4.4 | 2.2 | GT | 4 |  | NO | 0 | 4.297 | 5.01 | 0.2004 | 0.124 | 0.55 | 4.4355 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33139 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 4 | -0.95 | 2 | 9999 | -4 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | ST | 4 |  | NO | 0 | 1 | 4.11 | 0.1644 | 0.126 | 0.357 | 2.8333 | 9.11 |  | STAUFF_1_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33141 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 23.5 | -6.5 | 15 | 9999 | 2 | 25.5 |  | GENTPF | WSCCST | GGOV1 | EXST1_GE | Closed | 22.9 | 12.2669 | GT | 23 |  | NO | 0 | 1 | 3.0143 | 0.69329 | 0.0833 | 0.146 | 1.7527 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33142 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 43.6 | -13 | 30 | 9999 | 2 | 45.6 |  | GENTPF | WSCCST | GGOV1 | EXST1_GE | Closed | 22.9 | 16.3991 | GT | 43 |  | NO | 0 | 1 | 6.6463 | 2.8579 | 0.0615 | 0.154 | 2.5041 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33143 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 43.6 | -13 | 30 | 9999 | 2 | 45.6 |  | GENTPF | WSCCST | GGOV1 | EXST1_GE | Closed | 43.6 | 15.9965 | GT | 43 |  | NO | 0 | 1 | 6.6463 | 2.8579 | 0.0615 | 0.154 | 2.5041 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33151 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 46 | -18.4 | 27.6 | 9999 | 2 | 48 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 46 | 14.7873 | GT | 50 |  | NO | 0 | 0.326 | 4.0998 | 2.0499 | 0.124 | 0.55 | 4.4355 | 12.47 |  | TIDWTR_2_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33151 | 2 | 2 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 46 | -18.4 | 27.6 | 9999 | 2 | 48 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 46 | 14.7873 | GT | 50 |  | NO | 0 | 0.326 | 4.0998 | 2.0499 | 0.124 | 0.55 | 4.4355 | 12.47 |  | TIDWTR_2_UNITS | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33151 | 3 | 3 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 35 | -14 | 21 | 9999 | 2 | 37 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 35 | 14.7873 | GT | 40 |  | NO | 0 | 0.428 | 4.1 | 1.64 | 0.124 | 0.55 | 4.4355 | 12.47 |  | TIDWTR_2_UNITS | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33171 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 28 | 0 | 0 | 9999 | -9.2 | 18.8 |  | WT1G |  | WT1T |  | Closed | 8.4 | 0 | W1 | 18.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 9.11 |  | JVENTR_2_QFUNTS | W1 (Wind Turbine, Type 1) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33171 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 15.5 | 0 | 0 | 9999 | -5.1 | 10.4 |  | WT1G |  | WT1T |  | Closed | 4.65 | 0 | W1 | 10.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 9.11 |  | JVENTR_2_QFUNTS | W1 (Wind Turbine, Type 1) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33173 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [14 empty] | 0 | 38 | -0.79 | -0.79 | 9999 | 4.218 | 42.218 |  | WT1G |  | WT1T |  | Closed | 11.4 | -0.79 | W1 | 42.218 |  | YES | 0 | 0.178 | 0 |  |  |  | NAN | 0.6 |  | WNDMAS_2_UNIT 1 | W1 (Wind Turbine, Type 1) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33178 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 20 | 46 | -15 | 39 | 9999 | 4 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Open | 0 | 0 | JE | 67.5 | PF<0.8 | NO | 0 | 0.19 | 1.21 | 0.81675 | 0.086 | 0.369 | 4.2907 | 13.8 |  | RVRVEW_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33188 | 1 | 1 |  | Missing BA | [17 empty] | 122.7 | 207 | -68 | 100.25 | 9999 | 3 | 210 |  | GENROU | PSS2B | GGOV1 | ESST6B | Closed | 180 | 21.8555 | JE | 230 |  | NO | 0 | 0.182 | 6.38 | 14.674 | 0.064 | 0.371 | 5.7969 | 16.5 |  | COCOPP_2_CTG1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33189 | 2 | 2 |  | Missing BA | [17 empty] | 122.7 | 207 | -68 | 100.25 | 9999 | 3 | 210 |  | GENROU | PSS2B | GGOV1 | ESST6B | Open | 0 | 0 | JE | 230 |  | NO | 0 | 0.182 | 6.38 | 14.674 | 0.064 | 0.371 | 5.7969 | 16.5 |  | COCOPP_2_CTG2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33190 | 3 | 3 |  | Missing BA | [17 empty] | 122.7 | 207 | -68 | 100.25 | 9999 | 3 | 210 |  | GENROU | PSS2B | GGOV1 | ESST6B | Closed | 180 | 21.8555 | JE | 230 |  | NO | 0 | 0.182 | 6.38 | 14.674 | 0.064 | 0.371 | 5.7969 | 16.5 |  | COCOPP_2_CTG3 | JE (Jet Engine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33191 | 4 | 4 |  | Missing BA | [17 empty] | 122.7 | 207 | -68 | 100.25 | 9999 | 3 | 210 |  | GENROU | PSS2B | GGOV1 | ESST6B | Open | 0 | 0 | JE | 230 |  | NO | 0 | 0.182 | 6.38 | 14.674 | 0.064 | 0.371 | 5.7969 | 16.5 |  | COCOPP_2_CTG4 | JE (Jet Engine) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33250 | 1 | 1 | [14 empty] | Miss Turbine Type | Missing Model |  | Missing Sub R/X |  | 0 | 13.4 | 0 | 0 | 999 | -13.4 | [6 empty] | Closed | 9.38 | 0 | UN | 13.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2192-WD | UN (Unknown) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33450 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.978 | 0 | 0 | 999 | -1.978 | [6 empty] | Closed | 1.3846 | 0 | PV | 2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | RE
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33460 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 0 | -15 | 40 | 9999 | 0 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0 | -15 | SC | 48 | PF<0.8 | NO | 0 | 1 | 1.5583 | 0.74798 | 0.167 | 0.33 | 1.976 | 13.2 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33468 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 6 | -1 | 2.85 | 9999 | -6 |  |  | GENTPF |  |  | EXST1_GE | Closed | 5.07 | 2.85 | JE | 6 |  | NO | 0 | 1 | 4.555 | 0.2733 | 0.124 | 0.55 | 4.4355 | 9.11 |  | SRINTL_6_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 9999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 0.7 | 0.99684 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 2 | 2 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 9999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 0.7 | 0.99684 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 3 | 3 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 9999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 0.7 | 0.99684 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 4 | 4 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 9999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 0.7 | 0.99684 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 5 | 5 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 9999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 0.7 | 0.99684 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 6 | 6 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 9999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 0.7 | 0.99684 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 6
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 7 | 7 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 9999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 0.7 | 0.99684 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 7
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33687 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 1.5 | -0.2 | 0.5 | 9999 | -1.5 |  |  | GENROU |  |  |  | Closed | 1.5 | 0.15 | ST | 2 |  | NO | 0 | 1 | 2.9474 | 0.058948 | 0.152 | 0.59 | 3.8816 | 60 |  |  | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33800 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 8.6 | -4.16 | 7.41 | 9999 | -8.6 |  |  | GENTPJ |  |  | REXS | Closed | 4.98 | 5.7235 | HY | 14.5 | PF<0.8 | NO | 0 | 1 | 2.233 | 0.32379 | 0.2183 | 0.4419 | 2.0243 | 11 |  | SALTSP_7_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33800 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 33 | -5 | 8.55 | 9999 | 1.2 | 34.2 |  | GENTPJ |  | HYG3 | EXAC8B | Closed | 19.12 | 5.7235 | HY | 38 |  | NO | 0 | 1 | 3.0207 | 1.1479 | 0.0759 | 0.2343 | 3.087 | 11 |  | SALTSP_7_UNITS | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33803 | 1 | 1 |  | Missing BA | [17 empty] | -20 | 20 | 0 | 0 | 9999 | -20 | [6 empty] | Open | 0 | 0 | BA | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | 2389-WD | BA (Energy Storage, Battery) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33804 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 0 | -15 | 40 | 9999 | 0 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | SC | 48 | PF<0.8 | NO | 0 | 1 | 1.5583 | 0.74798 | 0.167 | 0.33 | 1.976 | 13.8 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 930 | GWF Energy LLC |  | 33805 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 96.14 | -18 | 59.6 | 9999 | -1.14 | 95 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | CT | 113.1 |  | NO | 0 | 1e-05 | 6.1 | 6.8991 | 0.073 | 0.395 | 5.411 | 13.8 |  | SCHLTE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 930 | GWF Energy LLC |  | 33807 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 96.14 | -18 | 59.6 | 9999 | -1.14 | 95 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | CT | 113.1 |  | NO | 0 | 1e-05 | 6.1 | 6.8991 | 0.073 | 0.395 | 5.411 | 13.8 |  | SCHLTE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33810 | 1 | 1 |  | Missing BA | [17 empty] | 31.6 | 49.5 | -10.5 | 30 | 9999 | 2.5 | 52 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 58.2 |  | NO | 0 | 1 | 2.16 | 1.2571 | 0.118 | 0.679 | 5.7542 | 13.8 |  | SMPRIP_1_SMPSON | GT (Gas Turbine) | 1
30 | PG AND E | 930 | GWF Energy LLC |  | 33811 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 103.7 | -58 | 103.7 | 9999 | -103.7 |  |  | GENTPJ | PSS2B |  | ESST4B | Open | 0 | 0 | CA | 196.88 | PF<0.8 | NO | 0 | 1e-05 | 2.3 | 4.5282 | 0.17 | 0.35 | 2.0588 | 18 |  | SCHLTE_1_PL1X3 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33812 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 31.2 | -15.6 | 15.6 | 9999 | -31.2 |  |  | GENQEC | PSS2C | H6E | DC4C | Closed | 20.98 | 5.5054 | HY | 33.9 |  | NO | 0 | 0.26 | 3.52 | 1.1933 |  |  | NAN | 13.8 |  | ELECTR_7_PL1X3 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33812 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 31.2 | -15.6 | 15.6 | 9999 | -31.2 |  |  | GENQEC | PSS2C | H6E | DC4C | Closed | 20.98 | 5.5054 | HY | 33.9 |  | NO | 0 | 0.43 | 3.52 | 1.1933 |  |  | NAN | 13.8 |  | ELECTR_7_PL1X3 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33812 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 32.3 | -12.6 | 18.5 | 9999 | -32.3 |  |  | GENTPJ | PSS2B | H6E | ESDC4B | Closed | 21.72 | 5.5054 | HY | 41.1 |  | NO | 0 | 1 | 3.3 | 1.3563 | 0.2 | 0.366 | 1.83 | 13.8 |  | ELECTR_7_PL1X3 | HY (Hydro) | 3 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33813 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 9999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Closed | 49.51 | 1.2898 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | MARIPOS_13.8_CTG6 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33815 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 9999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Closed | 49.51 | 1.3306 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | MARIPOS_13.8_CTG7 | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33816 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 20.5 | -3 | 9.28 | 9999 | 1.8e-07 | 20.5 |  | GENROU | PSS2A | TGOV1 | EXST4B | Open | 0 | 0 | ST | 22.5 |  | NO | 0 | 1e-05 | 1.54 | 0.3465 | 0.05 | 0.3 | 6 | 13.8 |  |  | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33817 | 3 | 3 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 9999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | MARIPOS_13.8_CTG8 | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33818 | 1 | 1 |  | Missing BA | [17 empty] | 36 | 50 | -11 | 30.94 | 9999 | 8.82 | 58.82 |  | GENROU | PSS2A | IEEEG1_GE | ESAC8B_GE | Closed | 45 | 3.4081 | ST | 58.82 |  | NO | 0 | 0.23 | 4.44 | 2.6116 | 0.15 | 0.4 | 2.6667 | 13.8 |  | COGNAT_1_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33819 | 4 | 4 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 9999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | MARIPOS_13.8_CTG9 | GT (Gas Turbine) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33820 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 14.081 | -7.59 | 7.59 | 9999 | -0.081 | 14 |  | GENTPJ |  | HYGOV | EXDC2A | Closed | 11.4 | 1.2642 | HY | 16 |  | NO | 0 | 0.28 | 3.173 | 0.50768 | 0.3187 | 0.9591 | 3.0094 | 11.5 |  | WESTPT_2_UNIT | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33821 | RN | RN |  | Missing BA | [17 empty] | 0 | 5 | -3.75 | 3.75 | 9999 | -5 | [6 empty] | Open | 0 | 0 | CC | 6.25 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | CC (Combined Cycle Generic) | RN
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33822 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 30.7125 | -13.8 | 13.8 | 9999 | -30.7125 |  |  | GENTPJ | PSS2B | H6E | ESST4B | Closed | 20.2 | 2.0197 | HY | 38.2 |  | NO | 0 | 1 | 3.5 | 1.337 | 0.13 | 0.348 | 2.6769 | 11 |  | TIGRCK_7_UNITS unit 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33822 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 30.7125 | -11.93 | 11.93 | 9999 | -1.7125 | 29 |  | GENTPJ |  | HYG3 | ESDC1A | Closed | 20.2 | 2.0197 | HY | 32.5 |  | NO | 0 | 1 | 4.1 | 1.3325 | 0.201 | 0.473 | 2.3532 | 11 |  | TIGRCK_7_UNITS unit 2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33830 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.4 | -1 | 1.5 | 9999 | -3.4 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 3 |  | NO | 0 | 1 | 5.1633 | 0.1549 | 0.124 | 0.55 | 4.4355 | 9.11 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33832 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 8.4 | -2.92 | 4.07 | 9999 | -8.4 |  |  | GENTPF |  |  | EXST1_GE | Closed | 8.4 | -0.39134 | GT | 9.35 |  | NO | 0 | 1 | 3 | 0.2805 | 0.126 | 0.357 | 2.8333 | 4.16 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33834 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 6.5 | -2.1 | 3.3 | 9999 | -6.5 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 7 |  | NO | 0 | 1 | 4.23 | 0.2961 | 0.14 | 0.574 | 4.1 | 9.11 |  | KALINA_2_UNIT 1 | GT (Gas Turbine) | 1
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 33846 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 9.4 | -1.9 | 3 | 9999 | -9.4 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 7.73 | 0.42686 | HY | 9 |  | NO | 0 | 1 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 7.2 |  | PARDEB_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 33846 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 10.4 | -1.9 | 2 | 9999 | -10.4 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 8 | 0.42686 | HY | 9 |  | NO | 0 | 1 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 7.2 |  | PARDEB_6_UNITS | HY (Hydro) | 2
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 33848 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 9.4 | -1.425 | 3 | 9999 | -9.4 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 7.73 | -1.425 | HY | 9 |  | NO | 0 | 1 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 7.2 |  | PARDEB_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 33850 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.7 | -1.9 | 2 | 9999 | -3.7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.77 | -1.1068 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 4.16 |  | CAMCHE_1_PL1X3 | HY (Hydro) | 1
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 33850 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 3.7 | 0 | 0 | 9999 | -3.7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.77 | 0 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 4.16 |  | CAMCHE_1_PL1X3 | HY (Hydro) | 2
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 33850 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 3.7 | 0 | 0 | 9999 | -3.7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.77 | 0 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 4.16 |  | CAMCHE_1_PL1X3 | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33868 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 46 | -22.28 | 22.28 | 9999 | -46 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 46 | 5.122 | W3 | 51.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWND2_1_WIND3 | W3 (Wind Turbine, Type 3) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33873 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 85.92 | -41.62 | 41.62 | 9999 | -85.92 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 85.92 | 9.5122 | W3 | 95.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWND2_1_WIND1 USWND2_1_WIND2 | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34050 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [9 empty] | Missing PS |  |  | 10 | 21.236 | -120 | 15 | 9999 | 6.764 | 28 |  | GENTPJ |  | GGOV1 | REXS | Open | 0 | 0 | ST | 30.19 | PF<-0.85 | NO | 0 | 0.122 | 3.2 | 0.96608 | 0.2 | 0.6 | 3 | 12.47 |  | ULTPCH_1_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34053 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20 | -1.3 | 2.4 | 9999 | -20 |  |  | REGC_A |  |  | REEC_D | Closed | 14 | -1.3 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.8 |  | CRWCKS_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 187 | Sierra Pacific Industries |  | 34055 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 1.05 | 10.9 | -4.05 | 6.75 | 9999 | 0.1 | 11 |  | GENTPJ | PSS2B | IEEEG1_GE | ESAC2A | Closed | 3.78 | 3.7973 | ST | 12.86 |  | NO | 0 | 0.173 | 2.42 | 0.31121 | 0.235 | 0.763 | 3.2468 | 13.8 |  | SPIFBD_1_PL1X2 | ST (Steam Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34056 | 1 | 1 |  | Missing BA | [17 empty] | 7.8 | 24.48 | -15 | 15 | 9999 | 1.52 | 26 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 19.79 | -8.3505 | ST | 26 |  | NO | 0 | 0.117 | 2.7692 | 0.71999 | 0.126 | 0.357 | 2.8333 | 13.8 |  | STNRES_1_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34058 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 72.5 | -15 | 17.8 | 9999 | 7.5 | 80 |  | GENTPJ | PSS2B | PIDGOV | ESST4B | Closed | 72 | -2.0458 | HY | 80 |  | NO | 0 | 0.2 | 2.7 | 2.16 | 0.148 | 0.988 | 6.6757 | 13.8 |  | DONNLS_7_UNIT | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34060 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 16 | -6 | 9 | 9999 | -16 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 12.69 | 4.2615 | HY | 17 |  | NO | 0 | 1 | 4.64 | 0.7888 | 0.152 | 0.59 | 3.8816 | 13.8 |  | SNDBAR_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34062 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 91.445 | -40.47 | 40.47 | 9999 | 1.555 | 93 |  | GENQEC | PSS2C | HYGOV | ST4C | Closed | 70.02 | 10.0488 | HY | 100 |  | NO | 0 | 0.287 | 3.6 | 3.6 |  |  | NAN | 13.8 |  | STANIS_7_UNIT1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34074 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 11 | -1 | 2 | 9999 | -11 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 9.1 | 1.494 | HY | 11 |  | NO | 0 | 1 | 4.64 | 0.5104 | 0.152 | 0.59 | 3.8816 | 6.9 |  | BEARDS_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34076 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 8.8 | -6 | 6 | 9999 | -8.8 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 8.11 | 3.9294 | HY | 13 | PF<-0.85 | NO | 0 | 1 | 4.64 | 0.6032 | 0.152 | 0.59 | 3.8816 | 6.9 |  | TULLCK_7_UNITS | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34076 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 9.9 | -6 | 6 | 9999 | -9.9 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 9.13 | 3.9294 | HY | 13 |  | NO | 0 | 1 | 4.64 | 0.6032 | 0.152 | 0.59 | 3.8816 | 6.9 |  | TULLCK_7_UNITS | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34076 | 3 | 3 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0.74 | 6.48 | -3 | 3 | 9999 | -6.48 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 5.99 | 3 | HY | 7.2 |  | NO | 0 | 1 | 4.64 | 0.33408 | 0.152 | 0.59 | 3.8816 | 6.9 |  | TULLCK_7_UNITS | HY (Hydro) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34078 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 7 | -2.8 | 3.515 | 9999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 4.9 | 3.515 | HY | 7 |  | NO | 0 | 1 | 4.64 | 0.3248 | 0.152 | 0.59 | 3.8816 | 6 |  | SPRGAP_1_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 139 | Wellhead Electric Co. |  | 34142 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 35.3 | 50.1 | -17.29 | 23.63 | 9999 | 1.3 | 51.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 63 |  | NO | 0 | 0.18 | 1.91 | 1.2033 | 0.103 | 0.445 | 4.3204 | 13.8 |  | PNOCHE_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34186 | 1 | 1 |  | Missing BA | [17 empty] | 18 | 60.5 | -25 | 37.5 | 9999 | 10.676 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 71.176 |  | NO | 0 | 0.181 | 2.1 | 1.4947 | 0.13 | 0.45 | 3.4615 | 13.8 |  | PNOCHE_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34201 | WP | WP |  | Missing BA | [17 empty] | 0 | 7 | -1 | 1 | 9999 | -7 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.22 | 0 | JE | 5 |  | NO | 0 | 1 | 4.1117 | 0.20558 | 0.126 | 0.357 | 2.8333 | 12.47 |  | TEMBLR_7_WELLPT | JE (Jet Engine) | WP
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34207 | QF | QF |  | Missing BA | [17 empty] | 0 | 2.5 | -0.6 | 1.25 | 9999 | -2.5 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.48 | 0.325 | ST | 2.5 |  | NO | 0 | 1 | 4.1117 | 0.10279 | 0.126 | 0.357 | 2.8333 | 12.47 |  | WRGHTP_7_AMENGY | ST (Steam Turbine) | QF
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34209 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.8 | -0.9 | 1.805 | 9999 | -3.8 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.82 | 1.2438 | HY | 3.8 |  | NO | 0 | 1 | 4.1117 | 0.15624 | 0.126 | 0.357 | 2.8333 | 12.47 |  | STOREY_7_MDRCHW | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34213 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 2.8 | -0.7 | 1.33 | 9999 | -2.8 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | JE | 2.8 |  | NO | 0 | 1 | 4.1117 | 0.11513 | 0.126 | 0.357 | 2.8333 | 12.47 |  | BULLRD_7_SAGNES | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34215 | QF | QF |  | Missing BA | [17 empty] | 0 | 1.2 | -0.3 | 0.6 | 9999 | -1.2 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | ST | 1.2 |  | NO | 0 | 1 | 4.1117 | 0.04934 | 0.126 | 0.357 | 2.8333 | 12.47 |  | MIDWAY_1_QF | ST (Steam Turbine) | QF
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34253 | QF | QF |  | Missing BA | [17 empty] | 0 | 2.8 | -0.7 | 1.33 | 9999 | -2.8 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | HY | 2.8 |  | NO | 0 | 1 | 4.1117 | 0.11513 | 0.126 | 0.357 | 2.8333 | 12.47 |  | BORDEN_2_QF | HY (Hydro) | QF
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34257 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20.3 | -0.2 | 0.2 | 9999 | -20.3 |  |  | REGC_A |  |  | REEC_A | Closed | 14.21 | 0 | P3 | 21.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.3 |  | AVENAL_6_SUNCTY 0035-WD SPV | P3 (Photovoltaic, Fixed) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34263 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 19.3 | -0.2 | 0.2 | 9999 | -19.3 |  |  | REGC_A |  |  | REEC_A | Closed | 13.51 | 0 | P3 | 20.52 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.3 |  | AVENAL_6_SANDDG 0036-WD SPV | P3 (Photovoltaic, Fixed) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34265 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 6 | -0.2 | 0.2 | 9999 | -6 |  |  | REGC_A |  |  | REEC_A | Closed | 0.61 | 0 | PV | 6.54 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.3 |  | AVENAL_6_AVPARK 0029-WD SPV | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34301 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [6 empty] | Missing PS |  |  | 15 | 49.6 | -5.6 | 6.24 | 9999 | 0.464 | 50.064 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | IC | 62.08 |  | NO | 0 | 0.22 | 1 | 0.6208 | 0.08 | 0.3 | 3.75 | 13.8 |  | CHWCHL_1_UNIT | IC (Internal Combustion) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34305 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 12.5 | -7.7 | 7.7 | 9999 | 2.206 | 14.706 |  | GENTPJ |  | GGOV1 | ESAC1A | Closed | 12.5 | 4.2183 | ST | 14.706 |  | NO | 0 | 0.19 | 3.5 | 0.51471 | 0.1 | 0.35 | 3.5 | 13.8 |  | CHWCHL_1_BIOMAS | ST (Steam Turbine) | 1
30 | PG AND E | 945 | Merced Irrigation District |  | 34306 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 95.97 | -18.3 | 42.6 | 9999 | 9.03 | 105 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 85 | 2.0332 | HY | 105 |  | NO | 0 | 0.3 | 3.9 | 4.095 | 0.11 | 0.34 | 3.0909 | 13.8 |  | EXCHEC_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34308 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 154.7 | -10.1 | 10.1 | 9999 | -154.7 |  |  | GENTPJ | PSS2A | H6E | ESST1A_GE | Closed | 96.87 | 6.9188 | HY | 155 |  | NO | 0 | 0.19 | 5.1 | 7.905 | 0.14 | 0.3 | 2.1429 | 13.8 |  | KERKH2_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34313 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 14.8 | 61.6 | -19.72 | 19.72 | 9999 | -61.6 |  |  | REGC_A |  |  | REEC_A | Closed | 43.12 | 7.6367 | PV | 64.68 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | MNDOTA_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34314 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -9.17 | 9.17 | 9999 | -20 |  |  | WT4G |  |  | WT4E | Closed | 14 | 1.7355 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34315 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 19.55 | -5.39 | 5.39 | 9999 | -19.55 |  |  | REGC_A |  |  | REEC_A | Closed | 1.955 | -2.2758 | PV | 20.28 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | ADMEST_6_SOLAR Q0632 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34316 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 0 | 11 | 0 | 0 | 9999 | -11 |  |  | GENTPJ | PFQRG |  | ESAC1A | Closed | 11 | 0 | HY | 25.2 |  | NO | 0 | 1 | 1.58 | 0.39816 | 0.2 | 0.6 | 3 | 9.11 |  | ONLLPP_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34319 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 19.998 | -9.112 | 9.112 | 9999 | -19.998 |  |  | REGC_A |  |  | REEC_D | Closed | 13.9986 | 9.112 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 945 | Merced Irrigation District |  | 34320 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 9 | -3 | 4.3 | 9999 | -9 |  |  | GENQEC |  |  | ESST4B | Closed | 9 | -0.62575 | HY | 10 |  | NO | 0 | 0.3 | 1.95 | 0.195 |  |  | NAN | 4.16 |  | MCSWAIN_8_UNITS | HY (Hydro) | 1
30 | PG AND E | 945 | Merced Irrigation District |  | 34322 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.44 | -2 | 2 | 9999 | -3.44 |  |  | GENQEC |  |  | ESST1A_GE | Closed | 3.44 | 0.51024 | HY | 4 |  | NO | 0 | 0.243 | 4.64 | 0.1856 |  |  | NAN | 12.5 |  | MERCFL_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34325 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 110.4 | -43.88 | 43.88 | 9999 | -110.4 |  |  | REGC_A |  |  | REEC_A | Closed | 77.28 | 43.88 | PV | 118.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.342 |  | SLST13_2_SOLAR1 Q0577 | PV (Photovoltaic) | 1
30 | PG AND E | 3008 | Panoche Energy Center, LLC |  | 34326 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 47 | 108.19 | -67.58 | 81.68 | 9999 | -6e-08 | 108.19 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 | 0.072 | 0.26 | 3.6111 | 13.8 |  | PNCHEG_2_PL1X4 | GT (Gas Turbine) | 1
30 | PG AND E | 3008 | Panoche Energy Center, LLC |  | 34327 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 47 | 108.19 | -67.58 | 81.68 | 9999 | -6e-08 | 108.19 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 | 0.072 | 0.26 | 3.6111 | 13.8 |  | PNCHEG_2_PL1X4 | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34328 | 1 | 1 |  | Missing BA | [17 empty] | 22 | 69.9 | -19.7 | 43.26 | 9999 | 12.335 | 82.235 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 82.235 |  | NO | 0 | 0.227 | 2.67 | 2.1957 | 0.07 | 0.49 | 7 | 13.8 |  | PNCHPP_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34329 | 2 | 2 |  | Missing BA | [17 empty] | 22 | 69.9 | -19.7 | 43.26 | 9999 | 12.335 | 82.235 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 82.235 |  | NO | 0 | 0.227 | 2.67 | 2.1957 | 0.07 | 0.49 | 7 | 13.8 |  | PNCHPP_1_PL1X2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34330 | 1 | 1 |  | Missing BA | [17 empty] | 11 | 12.5 | -4.96 | 7.35 | 9999 | 2.206 | 14.706 |  | GENTPJ |  | GGOV1 | ESAC1A | Closed | 11 | 1.2737 | ST | 14.706 |  | NO | 0 | 0.19 | 3.5 | 0.51471 | 0.1 | 0.35 | 3.5 | 13.8 |  | ELNIDP_6_BIOMAS | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34335 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 51.31 | -18.62 | 18.62 | 9999 | -51.31 |  |  | REGC_A |  |  | REEC_A | Closed | 35.917 | 1.6425 | PV | 54.585 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q0723 | PV (Photovoltaic) | 1
30 | PG AND E | 3008 | Panoche Energy Center, LLC |  | 34336 | 3 | 3 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 47 | 108.19 | -67.58 | 81.68 | 9999 | -6e-08 | 108.19 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 | 0.072 | 0.26 | 3.6111 | 13.8 |  | PNCHEG_2_PL1X4 | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34339 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 5 | -0.7 | -0.7 | 9999 | -5 |  |  | GEWTG |  |  | EXWTGE | Closed | 0.72 | -0.7 | PV | 5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.5 |  | MENBIO_6_RENEW1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34340 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 202.4 | -36.5 | 80 | 9999 | -202.4 |  |  | REGC_A |  |  | REEC_B | Closed | 110 | -10.1225 | PV | 111.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  | TRNQLT_2_SOLAR Q0643X | PV (Photovoltaic) | 1
30 | PG AND E | 3008 | Panoche Energy Center, LLC |  | 34341 | 4 | 4 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 47 | 108.19 | -67.58 | 81.68 | 9999 | -6e-08 | 108.19 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 | 0.072 | 0.26 | 3.6111 | 13.8 |  | PNCHEG_2_PL1X4 | GT (Gas Turbine) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34342 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 13 | 0 | 0 | 9999 | 4.8e-07 | 13 |  | WT1G | WT1P_B | WT1T |  | Closed | 3.9 | 0 | W3 | 13 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | INTTRB_6_UNIT | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34343 | MB | MB |  | Missing BA | [17 empty] | 0 | 8.6 | -3.8 | 5.3 | 9999 | -8.6 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 6.6 |  | KERKH1_7_UNIT 1 | HY (Hydro) | MB
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34345 | MB | MB |  | Missing BA | [17 empty] | 0 | 12.2 | -4.6 | 6.2 | 9999 | -12.2 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 6.6 |  | KERKH1_7_UNIT 3 | HY (Hydro) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34349 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | CANTUA_1_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34349 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | CANTUA_1_SOLAR | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 9 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | SCHNDR_1_WSTSDE | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 5 | 0 | 0 | 9999 | -5 |  |  | REGC_A |  |  | REEC_B | Closed | 3.5 | 0 | PV | 5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | SCHNDR_1_WSTSDE | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 3 | 3 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | SCHNDR_1_FIVPTS | PV (Photovoltaic) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 4 | 4 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 5 | 0 | 0 | 9999 | -5 |  |  | REGC_A |  |  | REEC_B | Closed | 3.5 | 0 | PV | 5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | SCHNDR_1_FIVPTS | PV (Photovoltaic) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34431 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 55.3 | -18.5 | 41 | 9999 | 5.2 | 60.5 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 71.18 |  | NO | 0 | 0.181 | 1.6 | 1.1389 | 0.125 | 0.499 | 3.992 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34433 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 55.3 | -18.5 | 41 | 9999 | 5.2 | 60.5 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 71.18 |  | NO | 0 | 0.181 | 1.6 | 1.1389 | 0.125 | 0.499 | 3.992 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34461 | 8 | 8 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 12 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 8
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34463 | 5 | 5 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 12 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | GUERNS_6_SOLAR | PV (Photovoltaic) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34467 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34485 | RE | RE |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | -2.5 | 16.725 | 0 | 0 | 9999 | -16.725 | [6 empty] | Closed | 11.7075 | 0 | PV | 16.725 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2585-RD | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34539 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 54.8 | -18 | 30.4 | 9999 | -5.8 | 49 |  | GENROU |  | GGOV1 | EXAC2 | Open | 0 | 0 | JE | 71.2 |  | NO | 0 | 1e-05 | 1.176 | 0.83731 | 0.05 | 0.4 | 8 | 13.8 |  | HENRTA_6_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34541 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 54.8 | -18 | 30.4 | 9999 | -5.8 | 49 |  | GENROU |  | GGOV1 | EXAC2 | Open | 0 | 0 | JE | 71.2 |  | NO | 0 | 1e-05 | 1.176 | 0.83731 | 0.05 | 0.4 | 8 | 13.8 |  | HENRTA_6_UNITA2 | JE (Jet Engine) | 1
30 | PG AND E | 139 | Wellhead Electric Co. |  | 34553 | RT | RT |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 49 | -25.3 | 25.3 | 9999 | -49 | [6 empty] | Open | 0 | 0 | OT | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 13.8 |  |  | OT (Other) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34557 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | HURON_6_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34557 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | HURON_6_SOLAR | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34563 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | STROUD_6_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34563 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | STROUD_6_SOLAR | PV (Photovoltaic) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34600 | 1 | 1 |  | Missing BA | [17 empty] | 83 | 413.2 | -174.4 | 174.4 | 9999 | 35.3 | 448.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 404 | 118.8674 | HY | 448.5 |  | NO | 0 | 0.19 | 4.331 | 19.4245 | 0.25 | 0.85 | 3.4 | 18 |  | HELMPG_7_UNIT1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34602 | 1 | 1 |  | Missing BA | [17 empty] | 83 | 413.2 | -174.4 | 174.4 | 9999 | 35.3 | 448.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 404 | 118.8674 | HY | 448.5 |  | NO | 0 | 0.19 | 4.331 | 19.4245 | 0.22 | 0.65 | 2.9545 | 18 |  | HELMPG_7_UNIT2 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34603 | ST | ST |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 2.9 | -2 | 2.2 | 9999 | 7.1 | 10 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 2.9 | 2.2 | GT | 10 | PF<0.8 | NO | 0 | 1e-05 | 2.7559 | 0.27559 | 0.124 | 0.55 | 4.4355 | 12.47 |  |  | GT (Gas Turbine) | ST
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34604 | 1 | 1 |  | Missing BA | [17 empty] | 83 | 410 | -181.8 | 181.8 | 9999 | 38.5 | 448.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 404 | 118.8674 | HY | 448.5 |  | NO | 0 | 0.19 | 4.331 | 19.4245 | 0.25 | 0.85 | 3.4 | 18 |  | HELMPG_7_UNIT3 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34608 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 14 | 18.59 | -8.4 | 11.523 | 9999 | 3.285 | 21.875 |  | GENTPJ |  | GGOV1 | ESST4B | Closed | 18.59 | -1.7624 | JE | 21.875 |  | NO | 0 | 0.176 | 2.28 | 0.49875 | 0.31 | 0.72 | 2.3226 | 13.8 |  | AGRICO_6_PL3N5 unit 3 | JE (Jet Engine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34608 | 4 | 4 |  | Missing BA | [17 empty] | 25.4 | 51.9 | -25 | 37.494 | 9999 | -5.34e-06 | 51.9 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 51.9 | -1.7624 | JE | 71.176 |  | NO | 0 | 0.189 | 1.4 | 0.99646 | 0.12 | 0.33 | 2.75 | 13.8 |  | AGRICO_7_UNIT unit 4 | JE (Jet Engine) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34608 | MB | MB |  | Missing BA |  |  |  |  | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 0 | 7.8 | -1 | 7 | 9999 | -7.8 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | UN | 12.5 | PF<0.8 | NO | 0 | 1e-05 | 5.06 | 0.6325 | 0.164 | 0.497 | 3.0305 | 13.8 |  | AGRICO_7_UNIT unit 2 | UN (Unknown) | MB
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34610 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 72.56 | -35.14 | 35.14 | 9999 | 8.04 | 80.6 |  | GENTPJ | PSS2B | HYGOV4 | ESST1A_GE | Closed | 72.15 | 14.8545 | HY | 80.6 |  | NO | 0 | 0.28 | 3.2 | 2.5792 | 0.2321 | 0.5476 | 2.3593 | 13.8 |  | HAASPH_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34610 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 72.56 | -33.69 | 33.69 | 9999 | 8.04 | 80.6 |  | GENTPJ | PSS2B | HYGOV4 | ESST1A_GE | Closed | 72.15 | 14.8545 | HY | 80.6 |  | NO | 0 | 0.28 | 3.2 | 2.5792 | 0.2321 | 0.5476 | 2.3593 | 13.8 |  | HAASPH_7_PL1X2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34612 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 53.39 | -26.85 | 26.85 | 9999 | 2.05 | 55.44 |  | GENTPJ | PSS2B | HYG3 | ESST1A_GE | Closed | 48 | 9.8648 | HY | 61.6 |  | NO | 0 | 0.117 | 4.331 | 2.6679 | 0.096 | 0.41 | 4.2708 | 13.8 |  | BALCHS_7_UNIT 2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34613 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | GATES_2_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34613 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | GATES_2_SOLAR | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34613 | 3 | 3 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 9999 | -10 |  |  | REGC_A |  |  | REEC_B | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | GATES_2_WSOLAR | PV (Photovoltaic) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34614 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 55.43 | -26.85 | 26.85 | 9999 | 0.009999 | 55.44 |  | GENTPJ | PSS2B | HYG3 | ESST1A_GE | Closed | 50 | 10.8726 | HY | 61.6 |  | NO | 0 | 0.117 | 4.331 | 2.6679 | 0.096 | 0.41 | 4.2708 | 13.8 |  | BALCHS_7_UNIT 3 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34616 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 51.5 | -12 | 9 | 9999 | -2.9 | 48.6 |  | GENTPJ |  | HYGOV | EXDC1 | Closed | 35 | 9 | HY | 54 |  | NO | 0 | 1 | 3.25 | 1.755 | 0.3372 | 0.9097 | 2.6978 | 13.8 |  | KINGRV_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34617 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 102 | -46.7 | 46.7 | 9999 | -102 |  |  | REGC_A |  |  | REEC_B | Closed | 71.4 | -10.7093 | PV | 112.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | HENRTS_1_SOLAR Q0581 | PV (Photovoltaic) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34618 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 0 | -15 | 48 | 9999 | 0 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0 | -15 | SC | 48 | PF<0.8 | NO | 0 | 1 | 1.5583 | 0.74798 | 0.167 | 0.33 | 1.976 | 13.2 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34621 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 0 | -15 | 48 | 9999 | 0 |  |  | GENTPF |  |  |  | Closed | 0 | -8.9237 | SC | 48 | PF<0.8 | NO | 0 | 1 | 1.5583 | 0.74798 | 0.167 | 0.33 | 1.976 | 13.2 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34623 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 60 | -27 | 27 | 9999 | -60 |  |  | REGC_A |  |  | REEC_A | Closed | 42 | -19.1487 | PV | 66 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | EXCLSG_1_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34624 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 31.62 | -9.43 | 9.43 | 9999 | -0.6 | 31.02 |  | GENTPJ | PSS2B | HYGOV | ESST4B | Closed | 31.2 | 5.0965 | HY | 33 |  | NO | 0 | 0.35 | 3.75 | 1.2375 | 0.0812 | 0.2696 | 3.3202 | 13.2 |  | BALCHS_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34629 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20 | -9.165 | 9.165 | 9999 | -20 |  |  | REGC_A |  |  | REEC_D | Closed | 14 | -0.4972 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.8 |  | KINGCO_1_KINGBR | PV (Photovoltaic) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34630 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 0 | 0 | -15 | 40 | 9999 | 0 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0 | 40 | SC | 65 | PF<0.8 | NO | 0 | 1 | 1.4 | 0.91 | 0.167 | 0.33 | 1.976 | 13.2 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34631 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3.2 | -1 | 1 | 9999 | -3.2 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 9.11 |  | CRNEVL_6_SJQN 2 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34632 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 0 | 0 | -15 | 40 | 9999 | 0 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0 | 40 | SC | 40 | PF<0.8 | NO | 0 | 1 | 1.4 | 0.56 | 0.167 | 0.33 | 1.976 | 13.2 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34633 | MB | MB |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 4.2 | -1 | 1 | 9999 | -4.2 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | CRNEVL_6_SJQN 3 | HY (Hydro) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34634 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 0.9 | -0.3 | 0.5 | 9999 | -0.9 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 1 |  | NO | 0 | 1 | 4.64 | 0.0464 | 0.152 | 0.59 | 3.8816 | 12 |  | CRNEVL_6_CRNVA | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34636 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 15.15 | -8.82 | 10.43 | 9999 | -15.15 |  |  | GENTPJ |  |  | ESST4B | Closed | 7.65 | 4.4858 | HY | 18.4 |  | NO | 0 | 0.274 | 2.514 | 0.46258 | 0.164 | 0.41 | 2.5 | 6.6 |  | FRIANT_6_UNITS | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34636 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 8.05 | -4.66 | 5.53 | 9999 | -8.05 |  |  | GENTPJ |  |  | ESST4B | Open | 0 | 0 | HY | 9.775 |  | NO | 0 | 0.254 | 2.375 | 0.23216 | 0.115 | 0.575 | 5 | 6.6 |  | FRIANT_6_UNITS | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34636 | 4 | 4 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 0 | 2 | -1.29 | 0 | 9999 | -2 |  |  | MOTOR1 |  |  |  | Open | 0 | 0 | HY | 2.381 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 6.6 |  | FRIANT_6_UNITS | HY (Hydro) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34639 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 18 | -5.01 | 9.69 | 9999 | -18 |  |  | WT4G |  |  | WT4E | Closed | 12.6 | 2.5744 | PV | 22.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | JAYNE_6_WLSLR | PV (Photovoltaic) | 1
30 | PG AND E | 960 | Rio Bravo Fresno |  | 34640 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 16 | 27.5 | -10 | 17.5 | 9999 | -6e-07 | 27.5 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 27.03 | 12.9749 | ST | 32.94 |  | NO | 0 | 0.18 | 3.3 | 1.087 | 0.17 | 0.59 | 3.4706 | 12.47 |  | ULTPFR_1_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34642 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 22.67 | -4.31 | 10.18 | 9999 | -7.9e-07 | 22.67 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 22.67 | 4.2325 | CT | 25.685 |  | NO | 0 | 0.197 | 2.5 | 0.64212 | 0.18 | 0.48 | 2.6667 | 13.8 |  | KINGCO_1_KINGBR | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34642 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 13.1 | -3.56 | 8.24 | 9999 | -13.1 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 12.63 | 4.2325 | CA | 14.556 |  | NO | 0 | 0.197 | 2.8 | 0.40757 | 0.12 | 0.4 | 3.3333 | 13.8 |  | KINGCO_1_KINGBR | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34644 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 22.5 | -9.426 | 9.426 | 9999 | -22.5 |  |  | REGC_A |  |  | REEC_D | Closed | 15.75 | -5.9368 | PV | 22.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | GIFENS_6_BUGSL1 Q0679 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34646 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 5 | 40 | -14.9 | 35 | 9999 | 10 | 50 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 15.9 | 8.1155 | CT | 71.176 | PF<0.8 | NO | 0.001 | 0.181 | 1.3 | 0.92529 | 0.11 | 0.37 | 3.3636 | 13.8 |  | SGREGY_6_SANGER | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34646 | 2 | 2 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 0 | 10.5 | -5.27 | 9.87 | 9999 | 2 | 12.5 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 3.9 | 8.1155 | CA | 15.625 | PF<0.8 | NO | 0.002 | 0.157 | 4.4 | 0.6875 | 0.105 | 0.409 | 3.8952 | 13.8 |  |  | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34648 | MB | MB |  | Missing BA | [17 empty] | 0 | 13.5 | -5 | 6.65 | 9999 | 1 | 14.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 12.7 |  | NO | 0 | 1 | 2.7559 | 0.35 | 0.124 | 0.55 | 4.4355 | 13.8 |  | DINUBA_6_UNIT | ST (Steam Turbine) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34649 | 1 | 1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 14 | -7.061 | 7.061 | 999 | -14 |  |  | REGC_A |  |  | REEC_B | Closed | 9.8 | 7.061 | PV | 17.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | Q0965 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34650 | RN | RN |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 5 | 0 | 0 | 9999 | -5 |  |  | DER_A |  |  |  | Closed | 3.5 | 0 | PV | 5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34651 | RE | RE |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 3.26 | 0 | 0 | 9999 | -3.26 | [6 empty] | Closed | 2.282 | 0 | PV | 3.26 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1523-RD spv and existing spv | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34652 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 16.5 | -5.4 | 7.885 | 9999 | 1 | 17.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 2.54 | 7.885 | JE | 17 |  | NO | 0 | 1 | 4.1071 | 0.69821 | 0.124 | 0.55 | 4.4355 | 9.11 |  | CHEVCO_6_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34652 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 8.5 | -2 | 3.8 | 9999 | 2 | 10.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 1.05 | 3.8 | JE | 9 |  | NO | 0 | 1 | 4.1072 | 0.36965 | 0.124 | 0.55 | 4.4355 | 9.11 |  | CHEVCO_6_UNIT 2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34653 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20.2 | -8.72 | 8.72 | 9999 | -20.2 |  |  | REGC_A |  |  | REEC_B | Closed | 14.14 | 8.72 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | Q0526 | PV (Photovoltaic) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34658 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5 | -1 | 1 | 9999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 2.3 |  | WISHON_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34658 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 5 | -1 | 1 | 9999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 2.3 |  | WISHON_6_UNITS | HY (Hydro) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34658 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 5 | -1 | 1 | 9999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 2.3 |  | WISHON_6_UNITS | HY (Hydro) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34658 | 4 | 4 |  | Missing BA | [17 empty] | 0 | 5 | -1 | 1 | 9999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 2.3 |  | WISHON_6_UNITS | HY (Hydro) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34658 | SJ | SJ |  | Missing BA | [17 empty] | 0 | 0.4 | 0 | 0 | 9999 | -0.4 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 2.3 |  | WISHON_6_UNITS | HY (Hydro) | SJ |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34663 | 12 | 12 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 15 | 134.14 | -44.86 | 44.86 | 9999 | -134.14 |  |  | REGC_A |  |  | REEC_A | Closed | 93.898 | 28.3178 | PV | 141.44 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.39 |  | CALFTN_2_SOLAR Q0877 | PV (Photovoltaic) | 12
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34666 | F | F |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -5.01 | 9.69 | 9999 | -20 |  |  | REGC_A |  |  | REEC_B | Closed | 14 | 4.0845 | PV | 23.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | F
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34667 | 3 | 3 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 153.91 | -70.12 | 70.12 | 9999 | -153.91 |  |  | REGC_A |  |  | REEC_A | Closed | 107.737 | -50.5678 | PV | 169.13 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  |  | PV (Photovoltaic) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34668 | 1 | 1 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 999 | -10 | [6 empty] | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2392-WD | PV (Photovoltaic) | 1
30 | PG AND E | 939 | Kings River Conservation Distric |  | 34671 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [9 empty] | 0 | 56 | -17 | 25 | 9999 | 4.5 | 60.5 |  | GENQEC | PSS2C | GGOV1 | AC7C | Open | 0 | 0 | JE | 71.18 |  | NO | 0 | 1e-05 | 0.97 | 0.69045 |  |  | NAN | 13.8 |  | MALAGA_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 939 | Kings River Conservation Distric |  | 34672 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [9 empty] | 0 | 56 | -17 | 25 | 9999 | 4.5 | 60.5 |  | GENQEC | PSS2C | GGOV1 | AC7C | Open | 0 | 0 | JE | 71.18 |  | NO | 0 | 1e-05 | 0.97 | 0.69045 |  |  | NAN | 13.8 |  | MALAGA_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34673 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20.2 | -8.72 | 8.72 | 9999 | -20.2 |  |  | REGC_A |  |  | REEC_B | Closed | 14.14 | 8.72 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | Q0532 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34677 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 19.8 | -6.1 | 6.1 | 9999 | -19.8 |  |  | REGC_A |  |  | REEC_B | Closed | 13.86 | 1.9477 | PV | 19.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.405 |  | WAUKNA_1_SOLAR2 Q0558 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34680 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -5.01 | 9.69 | 9999 | -20 |  |  | WT4G |  |  | WT4E | Closed | 14 | 4.7208 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | KANSAS_6_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34683 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 30.72 | -11 | 11 | 9999 | -30.72 |  |  | REGC_A |  |  | REEC_A | Closed | 21.504 | -2.6404 | PV | 32.64 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  | MSTANG_2_SOLAR Q0643W | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34685 | 2 | 2 |  | Missing BA | [17 empty] | -77.5 | 77.5 | -33 | 33 | 9999 | -77.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 87.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q0643W | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34688 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 126.82 | -48.17 | 48.17 | 9999 | -126.82 |  |  | REGC_A |  |  | REEC_B | Closed | 88.774 | -32.3269 | P4 | 132.51 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q0272 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34689 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 0 | 20 | 0 | 0 | 9999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | OROLOM_1_SOLAR2 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34690 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | 0 | 0 | 9999 | -20 |  |  | REGC_A |  |  | REEC_B | Closed | 14 | 0 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | CORCAN_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34692 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 12 | 0 | 0 | 9999 | -12 |  |  | REGC_A |  |  | REEC_B | Closed | 8.4 | 0 | PV | 12 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | CORCAN_1_SOLAR2 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34694 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20 | -8.76 | 8.76 | 9999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | 8.76 | PV | 21.84 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34696 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -5.01 | 9.69 | 9999 | -20 |  |  | GEWTG |  |  | EWTGFC | Closed | 14 | 1.4969 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | WAUKNA_1_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34699 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20 | -9.16 | 9.16 | 9999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | 5.1481 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | FRESHW_1_SOLAR1 Q0529 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34778 | QF | QF |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 17.5 | -6.5 | 9.215 | 9999 | -17.5 |  |  | GENTPF |  |  | EXST1_GE | Closed | 2.82 | 9.215 | ST | 17.5 |  | NO | 0 | 1 | 4.1117 | 0.71955 | 0.126 | 0.357 | 2.8333 | 21 |  | FELLOW_7_QFUNTS | ST (Steam Turbine) | QF
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34783 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 12 | -3.6 | 5.5 | 9999 | 2 | 14 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 2.13 | -3.6 | GT | 11 |  | NO | 0 | 1 | 4.2819 | 0.47101 | 0.14 | 0.574 | 4.1 | 9.11 |  | TXMCKT_6_UNIT | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34783 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 12 | -3 | 5 | 9999 | -12 |  |  | GENTPF |  |  | EXST1_GE | Closed | 2.13 | -3 | GT | 11 |  | NO | 0 | 1 | 4.2819 | 0.47101 | 0.14 | 0.574 | 4.1 | 9.11 |  | TXMCKT_6_UNIT | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34789 | 1 | 1 |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.6 | 0 | 0 | 9999 | -1.6 | [6 empty] | Closed | 1.6 | 0 | GT | 6.68 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34791 | 2 | 2 |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 5.6 | 0 | 0 | 9999 | -5.6 | [6 empty] | Closed | 5.6 | 0 | GT | 6.68 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34967 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 9.999 | 0 | 0 | 9999 | -9.999 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | TWISSL_6_SOLAR1 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34969 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 9.999 | 0 | 0 | 9999 | -9.999 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | TWISSL_6_SOLAR1 | PV (Photovoltaic) | 2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35000 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -2.85 | 2.85 | 9999 | -20 |  |  | GEWTG |  |  | EWTGFC | Closed | 14 | 2.6095 | PV | 50 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | ATWELL_1_SOLAR | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35001 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 50.7 | -24.05 | 19.98 | 9999 | -50.7 |  |  | REGC_A |  |  | REEC_A | Closed | 35.49 | -10.925 | PV | 56.115 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.4 |  |  | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35004 | 1 | 1 |  | Missing BA | [17 empty] | 50 | 84.22 | -7.87 | 44.58 | 9999 | 0.49001 | 84.71 |  | GENTPJ | IEEEST | GGOV1 | ESST1A_GE | Closed | 84.22 | 3.5186 | GT | 97 |  | NO | 0 | 0.297 | 5.5 | 5.335 | 0.0853 | 0.3113 | 3.6495 | 13.8 |  | SUNSET_2_UNITS GT1 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35012 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20.25 | -9.68 | 9.68 | 9999 | -20.25 |  |  | REGC_A |  |  | REEC_A | Closed | 14.175 | -7.5027 | PV | 22.446 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.4 |  | ALPSLR_1_NTHSLR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35013 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -6.57 | 9.69 | 9999 | -20 |  |  | GEWTG |  |  | EWTGFC | Closed | 14 | 1.2254 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | OLIVEP_1_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35018 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 11.2 | -1.52 | 8 | 9999 | -11.2 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 7.52 | 1.882 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 11 |  | KRNCNY_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35019 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model |  |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 15 | 61.4 | -44.86 | 44.86 | 9999 | -61.4 |  |  | WT4G |  |  | WT4E | Closed | 42.98 | 7.4214 | PV | 75 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  | LAMONT_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35020 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5.356 | -4.12 | 5.7 | 9999 | 2.464 | 7.82 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 4.22 | -1.5063 | HY | 7.82 | PF<0.8 | NO | 0 | 0.199 | 3.4286 | 0.26812 | 0.08 | 0.36 | 4.5 | 6.9 |  | RIOBRV_6_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35020 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 5.356 | -4.12 | 5.7 | 9999 | 2.464 | 7.82 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 3.12 | -1.5063 | HY | 7.82 | PF<0.8 | NO | 0 | 0.199 | 3.4286 | 0.26812 | 0.08 | 0.36 | 4.5 | 6.9 |  |  | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35022 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20.4 | -3.14 | 3.14 | 9999 | -20.4 |  |  | REGC_A |  |  | REEC_B | Closed | 14.28 | -1.1508 | PV | 20.64 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.386 |  | Q0620 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35023 | 1 | 1 |  | Missing BA | [17 empty] | 8 | 24.4 | -10 | 11.1 | 9999 | -24.4 |  |  | GENTPJ |  |  | REXS | Closed | 24.4 | 4.7905 | JE | 29.4444 |  | NO | 0.002 | 0.156 | 7.4 | 2.1789 | 0.0992 | 0.348 | 3.5081 | 13.8 |  | DOUBLEC_13_CTG_1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35023 | 2 | 2 |  | Missing BA | [17 empty] | 8 | 24.4 | -10 | 11.1 | 9999 | -24.4 |  |  | GENTPJ |  |  | REXS | Closed | 24.4 | 4.7905 | JE | 29.4444 |  | NO | 0.002 | 0.156 | 7.4 | 2.1789 | 0.0992 | 0.348 | 3.5081 | 13.8 |  | DOUBLEC_13_CTG_2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35024 | 1 | 1 |  | Missing BA | [17 empty] | 12 | 39 | -5 | 14.1 | 9999 | -19 | 20 |  | GENTPJ |  | GGOV1 |  | Closed | 20.3 | 2.5821 | JE | 22.22 |  | NO | 0 | 0.15 | 2.25 | 0.49995 | 0.17 | 0.7 | 4.1176 | 13.8 |  | DEXZEL_1_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35026 | 1 | 1 |  | Missing BA | [17 empty] | 8 | 24.4 | -6.3 | 6.3 | 9999 | 2.05 | 26.45 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 24.4 | 2.7403 | JE | 25.2 |  | NO | 0.002 | 0.142 | 2 | 0.504 | 0.11 | 0.38 | 3.4545 | 13.8 |  | KERNFT_1_UNITS unit 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35026 | 2 | 2 |  | Missing BA | [17 empty] | 8 | 24.4 | -9.5 | 9.5 | 9999 | 2.05 | 26.45 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 24.4 | 2.7403 | JE | 26.8 |  | NO | 0.002 | 0.156 | 2 | 0.536 | 0.11 | 0.38 | 3.4545 | 13.8 |  | KERNFT_1_UNITS unit 2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35027 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 8 | 24.4 | -9.5 | 9.5 | 9999 | 2 | 26.4 |  | GENTPJ | PFQRG | GGOV1 | ESAC8B_GE | Closed | 24.4 | 2.4973 | JE | 26.8 |  | NO | 0.001 | 0.156 | 2 | 0.536 | 0.11 | 0.38 | 3.4545 | 13.8 |  | HISIERA_13_CTG_1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35027 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 8 | 24.4 | -9.5 | 9.5 | 9999 | 2 | 26.4 |  | GENTPJ | PFQRG | GGOV1 | ESAC8B_GE | Closed | 24.4 | 2.4973 | JE | 26.8 |  | NO | 0.001 | 0.156 | 2 | 0.536 | 0.11 | 0.38 | 3.4545 | 13.8 |  | HISERIA_13_CTG_2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35029 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [6 empty] | Missing PS |  |  | 20.9 | 48 | -18 | 29 | 9999 | 1.07e-06 | 48 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 68.75 |  | NO | 0 | 0.22 | 1.3 | 0.89375 | 0.12 | 0.5 | 4.1667 | 13.8 |  | BDGRCK_1_UNITS | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35032 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 20.8 | -6.555 | 10.4 | 9999 | 2 | 22.8 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 7.24 | -3.95 | GT | 23 |  | NO | 0 | 1 | 4.174 | 0.96002 | 0.124 | 0.55 | 4.4355 | 9.11 |  | CHEVCY_1_UNIT | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35033 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20.46 | -8.084 | 8.084 | 9999 | -20.46 |  |  | REGC_A |  |  | REEC_B | Closed | 14.322 | -2.6249 | PV | 20.46 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | LHILLS_6_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35034 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20 | -8.18 | 8.18 | 999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | -1.2648 | PV | 21.78 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.405 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 951 | Mt. Poso Gogeneration Co. |  | 35036 | 1 | 1 |  | Missing BA | [17 empty] | 20 | 56.64 | -27.3 | 20.4 | 9999 | -56.64 |  |  | GENROU | PSS2A |  | ESAC8B_GE | Closed | 43.55 | 9.7949 | ST | 63.33 |  | NO | 0 | 0.159 | 4.23 | 2.6789 | 0.043 | 0.205 | 4.7674 | 13.8 |  | MTNPOS_1_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 35037 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 33 | 35.58 | -9.5 | 25.2 | 9999 | 12.22 | 47.8 |  | GENTPJ |  | GGOV1 | ESST4B | Closed | 35.58 | 2.3097 | JE | 47.8 |  | NO | 0 | 0.222 | 5.6 | 2.6768 | 0.07 | 0.14 | 2 | 12.47 |  | UNVRSY_1_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35038 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 48 | -15.8 | 24 | 9999 | 2 | 50 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 48 | 4.943 | JE | 49 |  | NO | 0 | 1 | 3.7029 | 1.8144 | 0.126 | 0.357 | 2.8333 | 9.11 |  | CHALK_1_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35040 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 22 | -11 | 14 | 9999 | 3 | 25 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Closed | 0.98 | 9.1164 | JE | 34.92 |  | NO | 0 | 0.116 | 2.3788 | 0.83068 | 0.1224 | 0.4172 | 3.4085 | 13.8 |  | KERNRG_115_U_1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35042 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20.357 | -6.87 | 6.87 | 9999 | -20.357 |  |  | REGC_A |  |  | REEC_A | Closed | 2.035 | -6.87 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  | PMPJCK_1_SOLAR2 Q0900 SPV | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35046 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 27 | -8 | 9.5 | 9999 | 2 | 29 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 5.21 | 9.5 | JE | 38 |  | NO | 0 | 1 | 3.7366 | 1.4199 | 0.126 | 0.357 | 2.8333 | 9.11 |  | VEDDER_1_SEKERN | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35047 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 15 | -9.206 | 9.206 | 9999 | -15 |  |  | REGC_A |  |  | REEC_D | Closed | 15 | 1.8374 | P4 | 17.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | WLDWD_1_SOLAR2 Q0901 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35048 | RT | RT |  | Missing BA | [12 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 7.5 | -2.375 | 3.8 | 9999 | -7.5 | [6 empty] | Open | 0 | 0 | UN | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.47 |  | FRITO_1_LAY | UN (Unknown) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35050 | 1 | 1 |  | Missing BA | [17 empty] | 5 | 9.5 | -3.6 | 6.25 | 9999 | 1.875 | 11.375 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 9.5 | -0.58507 | GT | 11.375 |  | NO | 0 | 0.142 | 2.1 | 0.23887 | 0.12 | 0.65 | 5.4167 | 6.9 |  | TANHIL_6_SOLART unit 1 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35050 | 2 | 2 |  | Missing BA | [17 empty] | 5 | 9.5 | -3.6 | 6.25 | 9999 | 1.875 | 11.375 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 9.5 | -0.58507 | GT | 11.375 |  | NO | 0 | 0.142 | 2.1 | 0.23887 | 0.12 | 0.65 | 5.4167 | 6.9 |  | TANHIL_6_SOLART unit 2 | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35052 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 11.6 | -3 | 4.75 | 9999 | 2.4 | 14 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 5.05 | 3.1094 | GT | 11 |  | NO | 0 | 1 | 3.7273 | 0.41 | 0.126 | 0.357 | 2.8333 | 9.11 |  | CHEVCD_6_UNIT | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35054 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 17.03 | -6.57 | 6.57 | 9999 | -17.03 |  |  | REGC_A |  |  | REEC_B | Closed | 11.921 | 3.0793 | PV | 17.05 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | Q0744 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35056 | 4 | 4 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 3.3 | -1.4 | 1.8 | 9999 | 0.572 | 3.872 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 3.973 |  | NO | 0 | 0.129 | 0.686 | 0.027255 | 1.161 | 1.566 | 1.3488 | 4.16 |  |  | JE (Jet Engine) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35056 | 5 | 5 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 3.2 | -1.4 | 1.8 | 9999 | 0.672 | 3.872 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 3.973 |  | NO | 0 | 0.129 | 0.686 | 0.027255 | 1.161 | 1.566 | 1.3488 | 4.16 |  |  | JE (Jet Engine) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35056 | 6 | 6 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 3 | -1.4 | 1.8 | 9999 | 0.872 | 3.872 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 3.973 |  | NO | 0 | 0.129 | 0.686 | 0.027255 | 1.161 | 1.566 | 1.3488 | 4.16 |  |  | JE (Jet Engine) | 6
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35058 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 48 | -15.9 | 24 | 9999 | 2 | 50 |  | GENROU |  | GGOV1 | EXST1_GE | Closed | 45 | 10.5283 | JE | 53 |  | NO | 0 | 1 | 2.9474 | 1.5621 | 0.152 | 0.59 | 3.8816 | 9.11 |  | LIVOAK_1_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35059 | 2 | 2 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 27.18 | -10.917 | 10.917 | 9999 | -27.18 |  |  | REGC_A |  |  | REEC_B | Closed | 19.026 | 4.9934 | PV | 27.29 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | Q0744 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35060 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 45.4 | -15 | 22.7 | 9999 | 2 | 47.4 |  | GENROU |  | GGOV1 | EXST1_GE | Closed | 45.4 | -3.633 | GT | 53 |  | NO | 0 | 1 | 2.9474 | 1.5621 | 0.152 | 0.59 | 3.8816 | 9.11 |  | MKTRCK_1_UNIT 1 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35062 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 44 | -14.5 | 22 | 9999 | 2 | 46 |  | GENROU |  | GGOV1 | EXST1_GE | Closed | 7.04 | 19.9648 | JE | 48 |  | NO | 0 | 1 | 2.9474 | 1.4148 | 0.152 | 0.59 | 3.8816 | 13.8 |  | DISCOV_1_CHEVRN | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35064 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 32.5 | -8 | 12 | 9999 | 2 | 34.5 |  | GENROU |  | GGOV1 | EXST1_GE | Open | 0 | 0 | JE | 24 |  | NO | 0 | 1 | 2.9474 | 0.70738 | 0.152 | 0.59 | 3.8816 | 9.11 |  | NAVY35_1_UNITS | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35064 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 32.5 | -8 | 12 | 9999 | 2 | 34.5 |  | GENROU |  | GGOV1 | EXST1_GE | Open | 0 | 0 | JE | 24 |  | NO | 0 | 1 | 2.9474 | 0.70738 | 0.152 | 0.59 | 3.8816 | 9.11 |  | NAVY35_1_UNITS | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35065 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20 | 0 | 0 | 9999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | 0 | PV | 23.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21.6 |  | 7STDRD_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35066 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [6 empty] | Missing PS |  |  | 32.6 | 48 | -18 | 29 | 9999 | 1.07e-06 | 48 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 48 | 17.7365 | JE | 68.75 |  | NO | 0 | 0.142 | 1.3 | 0.89375 | 0.15 | 0.35 | 2.3333 | 13.8 |  | BEARMT_1_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35067 | RE | RE |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 20.345 | 0 | 0 | 9999 | -20.345 | [6 empty] | Closed | 14.2415 | 0 | PV | 20.345 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | 2092-RD and others | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35068 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 18 | 0 | 0 | 999 | -18 | [6 empty] | Closed | 12.6 | 0 | PV | 19 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2110-RD | PV (Photovoltaic) | RE
30 | PG AND E | 3009 | PG&E National Energy Group |  | 35070 | 1 | 1 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 146 | 255 | -40 | 158 | 9999 | 15 | 270 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 146 | 30.1285 | GT | 340 |  | NO | 0 | 0.21 | 6.76 | 22.984 |  |  | NAN | 21 |  | LAPLMA_2_UNIT 1 | GT (Gas Turbine) | 1
30 | PG AND E | 3009 | PG&E National Energy Group |  | 35071 | 1 | 1 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 146 | 255 | -40 | 158 | 9999 | 15 | 270 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 146 | 30.0428 | GT | 340 |  | NO | 0 | 0.21 | 6.76 | 22.984 |  |  | NAN | 21 |  | LAPLMA_2_UNIT 2 | GT (Gas Turbine) | 1
30 | PG AND E | 3009 | PG&E National Energy Group |  | 35072 | 1 | 1 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 146 | 255 | -40 | 158 | 9999 | 15 | 270 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 146 | 29.8691 | GT | 340 |  | NO | 0 | 0.21 | 6.76 | 22.984 |  |  | NAN | 21 |  | LAPLMA_2_UNIT 3 | GT (Gas Turbine) | 1
30 | PG AND E | 3009 | PG&E National Energy Group |  | 35073 | 1 | 1 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 146 | 255 | -40 | 158 | 9999 | 15 | 270 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 146 | 30.0401 | GT | 340 |  | NO | 0 | 0.21 | 6.76 | 22.984 |  |  | NAN | 21 |  | LAPLMA_2_UNIT 4 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35074 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [14 empty] | 90.5 | 175 | -73.1 | 102 | 9999 | 4 | 179 |  | GENTPF | PSS2A | IEEEG1_GE | EXST4B | Closed | 90 | 15.7432 | CT | 234 |  | NO | 0 | 0.227 | 5.3 | 12.402 | 0.137 | 0.25 | 1.8248 | 18 |  | SUNRIS_2_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35075 | 1 | 1 |  | Missing BA | [17 empty] | 90.5 | 175 | -73.1 | 102 | 9999 | 4 | 179 |  | GENTPF | PSS2A | IEEEG1_GE | EXST4B | Open | 0 | 0 | CT | 234 |  | NO | 0 | 0.227 | 5.3 | 12.402 | 0.137 | 0.25 | 1.8248 | 18 |  | SUNRIS_2_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 921 | Elk Hills Power, LLC |  | 35076 | 1 | 1 |  | Missing BA | [17 empty] | 124.3 | 166.8 | -42.1 | 106 | 9999 | -15.1 | 151.7 |  | GENROU | PSS2B | GGOV3 | ESST4B | Closed | 124.3 | 31.7457 | CT | 234 |  | NO | 0 | 0.228 | 5.398 | 12.6313 | 0.051 | 0.234 | 4.5882 | 18 |  | ELKHIL_2_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 921 | Elk Hills Power, LLC |  | 35077 | 1 | 1 |  | Missing BA | [17 empty] | 122.9 | 166.8 | -41.7 | 103 | 9999 | -15.1 | 151.7 |  | GENROU | PSS2B | GGOV3 | ESST4B | Closed | 122.9 | 31.7145 | CT | 234 |  | NO | 0 | 0.228 | 5.398 | 12.6313 | 0.051 | 0.234 | 4.5882 | 18 |  | ELKHIL_2_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 921 | Elk Hills Power, LLC |  | 35078 | 1 | 1 |  | Missing BA | [17 empty] | 144 | 225 | -40.9 | 106 | 9999 | -225 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 144 | 33.5263 | CA | 250.6 |  | NO | 0 | 0.21 | 3.088 | 7.7385 | 0.055 | 0.436 | 7.9273 | 18 |  | ELKHIL_2_PL1X3 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35079 | 1 | 1 |  | Missing BA | [17 empty] | 90.5 | 175 | -91.6 | 127.9 | 9999 | -175 |  |  | GENTPJ | PSS2C |  | ESST4B | Open | 0 | 0 | CA | 293.3 |  | NO | 0 | 0.166 | 4.65 | 13.6384 | 0.0811 | 0.2045 | 2.5216 | 21 |  | SUNRIS_2_PL1X3 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35082 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -5.01 | 9.69 | 9999 | -20 |  |  | WT4G |  |  | WT4E | Closed | 14 | -0.40992 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.44 |  | ARVINN_6_ORION1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35084 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 12 | 0 | 0 | 9999 | -12 |  |  | WT4G |  |  | WT4E | Closed | 10 | 0 | PV | 15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | GOOSLK_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35087 | 3 | 3 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 15.25 | -6.3 | 6.3 | 9999 | -15.25 |  |  | REGC_A |  |  | REEC_B | Closed | 10.675 | 2.7464 | PV | 15.94 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | Q0744 | PV (Photovoltaic) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35089 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -9.59 | 9.59 | 9999 | -20 |  |  | REGC_A |  |  | REEC_B | Closed | 14 | -2.7321 | PV | 22.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | SKERN_6_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35091 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20.5 | -6.9 | 6.9 | 999 | -20.5 |  |  | REGC_A |  |  | REEC_A | Closed | 14.35 | 4.3061 | PV | 21.84 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | OLDRV1_6_SOLAR Q0517 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35092 | 4 | 4 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20.377 | -4.173 | 4.173 | 9999 | -20.377 |  |  | REGC_A |  |  | REEC_B | Closed | 14.2639 | 3.6618 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | Q0744 | PV (Photovoltaic) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35095 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 15.47 | -3.5593 | 3.5593 | 9999 | -15.47 |  |  | REGC_A |  |  | REEC_A | Closed | 10.829 | 0.45699 | PV | 17.22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.406 |  | MRLSDS_6_SOLAR Q0775 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35098 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 20.05 | -12.7 | 12.7 | 9999 | -20.05 |  |  | REGC_A |  |  | REEC_A | Closed | 14.035 | -6.114 | PV | 23.75 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | Q0557 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35099 | RN | RN |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 2 | 0 | 0 | 9999 | -2 |  |  | DER_A |  |  |  | Closed | 1.4 | 0 | PV | 2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35302 | RN | RN |  | Missing BA | [17 empty] | -2 | 2.45 | 0 | 0 | 9999 | -2.45 | [6 empty] | Open | 0 | 0 | OT | 2.45 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | OT (Other) | RN
30 | PG AND E | 462 | West Coast Energy |  | 35304 | 1 | 1 |  | Missing BA | [17 empty] | 113.4 | 180.5 | -59.5 | 80.8 | 9999 | 21.5 | 202 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Open | 0 | 0 | CT | 226 |  | NO | 0.003 | 0.201 | 5.46 | 12.3396 | 0.127 | 0.368 | 2.8976 | 15 |  | RUSCTY_2_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 462 | West Coast Energy |  | 35305 | 2 | 2 |  | Missing BA | [17 empty] | 110 | 179.2 | -56.1 | 90.4 | 9999 | 22.8 | 202 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Open | 0 | 0 | CT | 226 |  | NO | 0.003 | 0.201 | 5.46 | 12.3396 | 0.127 | 0.368 | 2.8976 | 15 |  | RUSCTY_2_UNITS | CT (Combined Cycle Combustion Turbine Part) | 2
30 | PG AND E | 462 | West Coast Energy |  | 35306 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 65 | 250.3 | -83.8 | 123.5 | 9999 | -250.3 |  |  | GENTPJ | PSS2B |  | ESST4B | Open | 0 | 0 | CA | 312.375 |  | NO | 0.003 | 0.21 | 3.49 | 10.9019 | 0.0572 | 0.4604 | 8.049 | 18 |  | RUSCTY_2_UNITS | CA (Combined Cycle Steam Part) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35307 | RN | RN |  | Missing BA | [17 empty] | -2.4 | 2.4 | 0 | 0 | 9999 | -2.4 | [6 empty] | Open | 0 | 0 | OT | 2.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | OT (Other) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35310 | RT | RT |  | Missing BA | [17 empty] | 0 | 21.8 | 0 | 0 | 9999 | -21.8 |  |  | REGC_A |  | WTGT_A | REEC_A | Open | 0 | 0 | W3 | 21.8 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 21.6 |  | LFC 51_2_UNIT 1 | W3 (Wind Turbine, Type 3) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35312 | RT | RT |  | Missing BA | [17 empty] | 0 | 13 | 0 | 0 | 9999 | -13 | [6 empty] | Open | 0 | 0 | W1 | 13 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 21.6 |  | SEAWST_6_LAPOS | W1 (Wind Turbine, Type 1) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35316 | RT | RT |  | Missing BA | [17 empty] | 0 | 24.1 | 0 | 0 | 9999 | -24.1 | [6 empty] | Open | 0 | 0 | W2 | 24.1 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.47 |  | ZOND_6_UNIT | W2 (Wind Turbine, Type 2) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35318 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 8.5 | 0 | 0 | 9999 | -8.5 |  |  | REGC_A |  | WTGT_A | REEC_A | Open | 0 | 0 | W3 | 8.5 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | FLOWD1_6_ALTPP1 | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35851 | 1 | 1 |  | Missing BA | [17 empty] | 19.9 | 48 | -16 | 25.4 | 9999 | 2 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Open | 0 | 0 | JE | 71.176 |  | NO | 0.002 | 0.181 | 1.176 | 0.83703 | 0.146 | 0.437 | 2.9932 | 13.8 |  | GILRPP_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35852 | 1 | 1 |  | Missing BA | [17 empty] | 20.1 | 47.7 | -16 | 28 | 9999 | 2.3 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Open | 0 | 0 | JE | 71.176 |  | NO | 0.002 | 0.181 | 1.176 | 0.83703 | 0.119 | 0.379 | 3.1849 | 13.8 |  | GILRPP_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35853 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 48.1 | -14 | 17.4 | 9999 | 1.9 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Open | 0 | 0 | JE | 71.176 |  | NO | 0.002 | 0.181 | 1.17 | 0.83276 | 0.069 | 0.526 | 7.6232 | 13.8 |  | GILRPP_1_PL3X4 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35854 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 30.08 | 47 | -11.82 | 40.29 | 9999 | 4.25 | 51.25 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 30.08 | 17.1443 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35855 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 30.05 | 43.3 | -12.07 | 44.81 | 9999 | 7.95 | 51.25 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 30.05 | 19.105 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35856 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 29.99 | 47.5 | -11.13 | 42.96 | 9999 | 3.75 | 51.25 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 29.99 | 19.1865 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35857 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | 30.15 | 46.1 | -11.8 | 44.2 | 9999 | 5.15 | 51.25 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 30.15 | 19.1871 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35858 | 1 | 1 |  | Missing BA | [17 empty] | 7.7 | 113 | -49.2 | 49.9 | 9999 | -113 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 44.9 | 25.14 | CA | 148.318 |  | NO | 0.003 | 0.14 | 5.41 | 8.024 | 0.112 | 0.231 | 2.0625 | 13.8 |  | LECEF_1_UNITS | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35859 | RN | RN |  | Missing BA |  |  |  |  | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 50 | -35.72 | 35.72 | 9999 | -50 | [6 empty] | Open | 0 | 0 | GT | 61.45 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | GT (Gas Turbine) | RN
30 | PG AND E | 470 | Calpine Corp. |  | 35860 | 1 | 1 |  | Missing BA | [17 empty] | 17.1 | 21.9 | -8.8 | 10 | 9999 | 0.769 | 22.669 |  | GENTPJ |  | GGOV1 | ESAC1A | Closed | 21.9 | 7.8064 | CT | 24.4 |  | NO | 0 | 1 | 2.11 | 0.51484 | 0.0556 | 0.144 | 2.5899 | 13.8 |  | CALPIN_1_AGNEW | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35860 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [6 empty] | Missing Sub R/X |  | 5.4 | 6.9 | -3.55 | 3.2 | 9999 | -6.9 |  |  | GENROU |  |  | ESAC1A | Closed | 6.9 | 3.2 | CA | 9.5 |  | NO | 0 | 1e-05 | 2.5 | 0.2375 | 0.24 | 0.675 | 2.8125 | 13.8 |  | CALPIN_1_AGNEW | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35861 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 0 | 8.4 | -6.3 | 6.3 | 9999 | 1.1e-07 | 8.4 |  | GENROU |  | GGOV1 | REXS | Open | 0 | 0 | GT | 10.5 | PF<0.8 | NO | 0 | 0.218 | 0.7097 | 0.074519 | 0.05 | 0.3 | 6 | 4.16 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35861 | RN | RN |  | Missing BA | [17 empty] | 0 | 12 | -4.875 | 9 | 9999 | -12 |  |  | DER_A |  |  |  | Open | 0 | 0 | PV | 2 | PF<0.8 | NO | 0.012 | 0.141 | 0 |  |  |  | NAN | 4.16 |  |  | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35863 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5.785 | 0 | 0 | 9999 | -5.785 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | JE | 6 |  | NO | 0 | 1 | 4.1117 | 0.2467 | 0.126 | 0.357 | 2.8333 | 12.47 |  | MARKHM_1_CATLST | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35871 | 2 | 2 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [5 empty] | Missing PS |  |  | 27.8 | 27.8 | -10.8 | 23.4 | 999 | -27.8 |  |  | GENROU |  |  | REXS | Closed | 27.8 | 0.17425 | CA | 42.4 | PF<0.8 | NO | 0 | 0.17 | 3.7 | 1.5688 | 0.059 | 0.169 | 2.8644 | 13.8 |  | GILROY_1_UNIT | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 35881 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 191.4 | -83 | 118.6 | 9999 | 8.49e-06 | 191.4 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 10 | 21.3193 | JE | 224 |  | NO | 0 | 1e-05 | 5 | 11.2 | 0.083 | 0.23 | 2.7711 | 18 |  | METEC_18_CTG1 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35882 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 191.4 | -83 | 118.6 | 9999 | 8.49e-06 | 191.4 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 10 | 21.3193 | JE | 224 |  | NO | 0 | 1e-05 | 5 | 11.2 | 0.083 | 0.23 | 2.7711 | 18 |  | METEC_18_CTG2 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35883 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 236.3 | -102 | 146.4 | 9999 | -236.3 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 10 | 25.208 | CC | 278 |  | NO | 0 | 1e-05 | 6.5 | 18.07 | 0.083 | 0.23 | 2.7711 | 18 |  | METEC_18_STG1 | CC (Combined Cycle Generic) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 36201 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 39.9 | -7 | 20 | 9999 | -1.9 | 38 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 24.57 | 9.4755 | GT | 45.176 |  | NO | 0 | 1 | 6.22 | 2.8099 | 0.07 | 0.3 | 4.2857 | 13.8 |  | SALIRV_2_UNIT | GT (Gas Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 36202 | 2 | 2 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 19.6 | 38.5 | -14.2 | 17.2 | 999 | -38.5 |  |  | GENTPJ |  |  | REXS | Closed | 19.6 | -1.2418 | CA | 42.4 |  | NO | 0 | 0.138 | 4 | 1.696 | 0.29 | 0.598 | 2.0621 | 13.8 |  | BASICE_2_UNITS | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36204 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 3.2 | -0.3 | 0.7 | 9999 | -3.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 3 | 0.2 | W3 | 3.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36204 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 3.2 | -0.3 | 0.7 | 9999 | -3.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 3 | 0.2 | W3 | 3.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12 |  |  | W3 (Wind Turbine, Type 3) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36207 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | [9 empty] | 0 | 60.5 | -22.2 | 37.5 | 9999 | -10.5 | 50 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 71.176 |  | NO | 0 | 1e-05 | 1.17 | 0.83276 | 0.163 | 0.403 | 2.4724 | 13.8 |  | KNGCTY_6_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36209 | 1 | 1 |  | Missing BA | [17 empty] | 2.5 | 16 | -5.6 | 10 | 9999 | 2 | 18 |  | GENROU |  | GGOV1 | EXST4B | Open | 0 | 0 | ST | 16 |  | NO | 0 | 1e-05 | 3 | 0.48 | 0.152 | 0.59 | 3.8816 | 12.47 |  |  | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36212 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 19.3 | -6.68 | 6.68 | 9999 | -19.3 |  |  | REGC_A |  |  | REEC_A | Closed | 13.51 | 6.68 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | FRNTBW_6_SOLAR1 Q0705 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36215 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 203.15 | -84.44 | 84.44 | 9999 | -203.15 |  |  | REGC_A |  |  | REEC_A | Closed | 142.205 | -17.6893 | P4 | 220 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | Q0779 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36220 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20.51 | -7.958 | 7.958 | 9999 | -20.51 |  |  | REGC_A |  |  | REEC_B | Closed | 14.357 | -1.6601 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  | Q0972 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36221 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [14 empty] | 0 | 166.28 | -45 | 90 | 9999 | 5.22 | 171.5 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 166.28 | 25.6351 | CT | 207.8 |  | NO | 0 | 0.18 | 5.36 | 11.1381 | 0.077 | 0.267 | 3.4675 | 18 |  | MOSSLD_2_PSP1 CTG1 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36222 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [14 empty] | 0 | 166.28 | -45 | 90 | 9999 | 5.22 | 171.5 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 166.28 | 25.6284 | CT | 207.8 |  | NO | 0 | 0.18 | 5.36 | 11.1381 | 0.077 | 0.267 | 3.4675 | 18 |  | MOSSLD_2_PSP1 CTG2 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36223 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 192.2 | -70 | 90 | 9999 | -192.2 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 150 | 33.8689 | CA | 233 |  | NO | 0 | 0.196 | 4.78 | 11.1374 | 0.061 | 0.572 | 9.377 | 18 |  | MOSSLD_2_PSP1 STG1 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36224 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [14 empty] | 0 | 166.28 | -45 | 90 | 9999 | 5.22 | 171.5 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 166.28 | 22.6594 | CT | 207.8 |  | NO | 0 | 0.18 | 5.36 | 11.1381 | 0.077 | 0.267 | 3.4675 | 18 |  | MOSSLD_2_PSP2 CTG3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36225 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [14 empty] | 0 | 166.28 | -45 | 90 | 9999 | 5.22 | 171.5 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 166.28 | 22.6594 | CT | 207.8 |  | NO | 0 | 0.18 | 5.36 | 11.1381 | 0.077 | 0.267 | 3.4675 | 18 |  | MOSSLD_2_PSP2 CTG4 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36226 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 192.14 | -70 | 90 | 9999 | -192.14 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 150 | 30.083 | CA | 233 |  | NO | 0 | 0.196 | 4.78 | 11.1374 | 0.061 | 0.572 | 9.377 | 18 |  | MOSSLD_2_PSP2 STG2 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36232 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 999 | -10 | [6 empty] | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21.6 |  | 1862-RD | PV (Photovoltaic) | RE
30 | PG AND E | 390 | Pacific Gas and Electric |  | 36411 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 1196 | -296 | 509 | 9999 | -3.81e-06 | 1196 |  | GENTPJ | IEEEST | IEEEG1_GE | ESAC2A | Closed | 1164.5 | 72.1748 | ST | 1300 |  | NO | 0 | 0.329 | 5.75 | 74.75 | 0.071 | 0.357 | 5.0282 | 25 |  | DIABLO_7_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 36412 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 1204 | -432.63 | 587.95 | 9999 | -1204 |  |  | GENTPJ | IEEEST |  | ESAC2A | Closed | 1167.9 | 82.8999 | ST | 1340 |  | NO | 0 | 0.3 | 5.62 | 75.308 | 0.061 | 0.376 | 6.1639 | 25 |  | DIABLO_7_UNIT 2 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36413 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5.6 | -1.9 | 2.66 | 9999 | 2 | 7.6 |  | GENROU |  | GGOV1 | EXST1_GE | Open | 0 | 0 | IC | 6 |  | NO | 0 | 1 | 2.9474 | 0.17684 | 0.152 | 0.59 | 3.8816 | 13.8 |  |  | IC (Internal Combustion) | 1
30 | PG AND E | 3004 | Vanderburg Air Force Base (US GO |  | 36414 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 3 | -1.7 | 1.7 | 9999 | -3 |  |  | GENROU |  |  | EXST1_GE | Open | 0 | 0 | GT | 3 |  | NO | 0 | 1 | 2.9474 | 0.088422 | 0.152 | 0.59 | 3.8816 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 3004 | Vanderburg Air Force Base (US GO |  | 36414 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 3 | -1.7 | 1.7 | 9999 | -3 |  |  | GENROU |  |  | EXST1_GE | Open | 0 | 0 | GT | 3 |  | NO | 0 | 1 | 2.9474 | 0.088422 | 0.152 | 0.59 | 3.8816 | 12.47 |  |  | GT (Gas Turbine) | 2
30 | PG AND E | 3004 | Vanderburg Air Force Base (US GO |  | 36414 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 3 | -1.7 | 1.7 | 9999 | -3 |  |  | GENROU |  |  | EXST1_GE | Open | 0 | 0 | GT | 3 |  | NO | 0 | 1 | 2.9474 | 0.088422 | 0.152 | 0.59 | 3.8816 | 12.47 |  |  | GT (Gas Turbine) | 3
30 | PG AND E | 3004 | Vanderburg Air Force Base (US GO |  | 36414 | 4 | 4 |  | Missing BA | [17 empty] | 0 | 3 | -1.7 | 1.7 | 9999 | -3 |  |  | GENROU |  |  | EXST1_GE | Open | 0 | 0 | GT | 3 |  | NO | 0 | 1 | 2.9474 | 0.088422 | 0.152 | 0.59 | 3.8816 | 12.47 |  |  | GT (Gas Turbine) | 4
30 | PG AND E | 3004 | Vanderburg Air Force Base (US GO |  | 36414 | 5 | 5 |  | Missing BA | [17 empty] | 0 | 3 | -1.7 | 1.7 | 9999 | -3 |  |  | GENROU |  |  | EXST1_GE | Open | 0 | 0 | GT | 3 |  | NO | 0 | 1 | 2.9474 | 0.088422 | 0.152 | 0.59 | 3.8816 | 12.47 |  |  | GT (Gas Turbine) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36430 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 229.5 | -95.12 | 95.12 | 9999 | -229.5 |  |  | REGC_A |  |  | REEC_A | Closed | 160.65 | 6.6293 | PV | 275.04 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.324 |  | TOPAZ_2_SOLAR unit A1 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36432 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 26.44 | -10.96 | 10.96 | 9999 | -26.44 |  |  | REGC_A |  |  | REEC_A | Closed | 18.508 | 6.6296 | PV | 34.32 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit A2 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36434 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 38.45 | -15.94 | 15.94 | 9999 | -38.45 |  |  | REGC_A |  |  | REEC_A | Closed | 26.915 | 5.4272 | PV | 46.08 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.324 |  | TOPAZ_2_SOLAR unit B1 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36436 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 73.3 | -30.4 | 30.4 | 9999 | -73.3 |  |  | REGC_A |  |  | REEC_A | Closed | 51.31 | 5.4272 | PV | 95.16 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit B2 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36439 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 195 | -76.6 | 76.6 | 9999 | -195 |  |  | REGC_A |  |  | REEC_A | Closed | 136.5 | -0.23559 | PV | 209.76 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.342 |  | CAVLSR_2_RSOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36440 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 6.5 | -2.55 | 2.55 | 9999 | -6.5 |  |  | REGC_A |  |  | REEC_A | Closed | 4.55 | -0.23591 | PV | 7 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.27 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36441 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 38.2 | -15 | 15 | 9999 | -38.2 |  |  | REGC_A |  |  | REEC_A | Closed | 26.74 | -0.2359 | PV | 41.04 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.342 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 36863 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 23 | 50 | -9.3 | 40 | 999 | 5 | 55 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 49.6 | 3.142 | CT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.38 | 0.98223 | 0.081 | 0.271 | 3.3457 | 13.8 |  | DUANE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 36864 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 23 | 50 | -9.3 | 40 | 999 | 5 | 55 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 47.6 | 2.9694 | CT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.38 | 0.98223 | 0.081 | 0.271 | 3.3457 | 13.8 |  | DUANE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 36865 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 47.79 | -15 | 36 | 999 | -47.79 |  |  | GENTPJ | PSS2A |  | ESAC7B | Closed | 45.8 | 2.8309 | CA | 63.059 | PF<0.8 | NO | 0 | 0.12 | 6.01 | 3.7898 | 0.079 | 0.265 | 3.3544 | 13.8 |  | DUANE_1_PL1X3 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 3003 | Lassen Municipality Utility Dist |  | 36912 | 2 | 2 |  | Missing BA | [12 empty] | Miss Turbine Type |  |  |  |  | 0 | 7.5 | -2.46 | 2.46 | 9999 | -7.5 |  |  | REGC_A |  |  | REEC_A | Closed | 7.497 | 0.40196 | UN | 7.9 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | 2
30 | PG AND E | 3003 | Lassen Municipality Utility Dist |  | 36938 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 30 | -6 | 6 | 9999 | 2 | 32 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 26.4 | 2.1986 | ST | 30 |  | NO | 0 | 1 | 2.7447 | 0.82341 | 0.126 | 0.357 | 2.8333 | 9.11 |  |  | ST (Steam Turbine) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37150 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 160 | -16 | 16 | 888 | -160 |  |  | REGC_A |  |  | REEC_A | Closed | 33 | 13.9443 | PV | 171.8261 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37302 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 77 | -13 | 12 | 888 | 1.91e-06 | 77 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Open | 0 | 0 | HY | 77 |  | NO | 0.002 | 0.284 | 2.7 | 2.079 | 0.13 | 0.23 | 1.7692 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37305 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 76.5 | -11 | 10 | 888 | 1.43e-06 | 76.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 73 | -11 | HY | 76.5 |  | NO | 0.004 | 0.216 | 2.304 | 1.7626 | 0.24 | 0.5 | 2.0833 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37306 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 76.5 | -10 | 20 | 888 | 1.43e-06 | 76.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 73 | -10 | HY | 76.5 |  | NO | 0.004 | 0.216 | 2.304 | 1.7626 | 0.24 | 0.5 | 2.0833 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37307 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 10.5 | -0.6 | 2.3 | 888 | -10.5 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 4 | -0.6 | HY | 10.5 |  | NO | 0.003 | 0.25 | 3.24 | 0.3402 | 0.17 | 0.25 | 1.4706 | 4.16 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37308 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 78 | -8.5 | 24.9 | 888 | 5.5 | 83.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 63 | -6.8184 | HY | 78 |  | NO | 0.003 | 0.284 | 3.4 | 2.652 | 0.22 | 0.42 | 1.9091 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37311 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 42.5 | -16.7 | 24.1 | 888 | 2.5 | 45 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 44.5 | 18.8857 | CT | 55.4 |  | NO | 0 | 0.13 | 2.64 | 1.4626 |  |  | NAN | 13.8 |  |  | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37313 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 50 | -14.2 | 37.5 | 888 | 10.5 | 60.5 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 47 | 19.0394 | JE | 56 |  | NO | 0 | 0.181 | 1.37 | 0.7672 | 0.112 | 0.461 | 4.1161 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37314 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 26.8 | -3.1 | 4.1 | 888 | 2.9 | 29.7 |  | GENTPJ |  | HYG3 | ESST1A_GE | Closed | 7 | 0.32316 | HY | 29.7 |  | NO | 0.003 | 0.25 | 1.692 | 0.50252 | 0.24 | 0.49 | 2.0417 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37315 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 48 | -4.8 | 31.6 | 888 | -8 | 40 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 40 | 8.3689 | CT | 60 |  | NO | 0 | 0.13 | 2.42 | 1.452 | 0.04 | 0.15 | 3.75 | 13.8 |  |  | CT (Combined Cycle Combustion Turbine Part) | 1 |  | PSS Exempt
30 | PG AND E | 363 | Sacramento Utility District |  | 37316 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 42.5 | -3.7 | 31.6 | 888 | -2.5 | 40 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 38 | 8.906 | JE | 52.5 |  | NO | 0 | 0.13 | 2.42 | 1.2705 | 0.04 | 0.15 | 3.75 | 13.8 |  |  | JE (Jet Engine) | 1 |  | PSS Exempt
30 | PG AND E | 363 | Sacramento Utility District |  | 37317 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 46.7 | -5.7 | 12.2 | 888 | -7.6e-07 | 46.7 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 44 | 5.5331 | HY | 46.7 |  | NO | 0.002 | 0.227 | 1.869 | 0.87282 | 0.25 | 0.55 | 2.2 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 363 | Sacramento Utility District |  | 37318 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 116 | -28 | 51 | 888 | 24 | 140 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 93 | 25.5268 | HY | 140 |  | NO | 0.002 | 0.22 | 2.151 | 3.0114 | 0.17 | 0.31 | 1.8235 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37319 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 134.3 | -20 | 48 | 888 | 5.7 | 140 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 94 | 25.7545 | HY | 140 |  | NO | 0.002 | 0.22 | 2.151 | 3.0114 | 0.17 | 0.31 | 1.8235 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 37521 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 175 | -20 | 108.5 | 9999 | 5 | 180 |  | GENQEC | PSS2B | GGOV3 | ESST6B | Closed | 39.7 | -17.1165 | CC | 250 |  | NO | 0 | 0.201 | 4.767 | 11.9175 |  |  | NAN | 18 |  | SUTTER_2_PL1X3 | CC (Combined Cycle Generic) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 37522 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 175 | -20 | 108.5 | 9999 | 5 | 180 |  | GENQEC | PSS2B | GGOV3 | ESST6B | Closed | 39.7 | -17.1165 | CC | 250 |  | NO | 0 | 0.201 | 4.767 | 11.9175 |  |  | NAN | 18 |  | SUTTER_2_PL1X3 | CC (Combined Cycle Generic) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 37523 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 175 | -20 | 108.5 | 9999 | -175 |  |  | GENTPJ | PSS2B |  | ESST6B | Closed | 39.7 | -17.1165 | CC | 250 |  | NO | 0 | 0.201 | 3.95 | 9.875 | 0.063 | 0.16 | 2.5397 | 18 |  | SUTTER_2_PL1X3 | CC (Combined Cycle Generic) | 3
30 | PG AND E | 313 | City of Redding |  | 37530 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 5 | -3 | 3 | 9999 | -5 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0.006 | 0.224 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37549 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  | PSS No Ex | [11 empty] | 0 | 69 | -30 | 22 | 9999 | 1 | 70 |  | GENTPJ | PSS2A | HYGOVR |  | Closed | 39.1 | 22 | HY | 71.9 |  | NO | 0.003 | 0.34 | 3.69 | 2.6531 | 0.1335 | 0.46 | 3.4457 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37550 | 2 | 2 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 0 | 69 | -30 | 22 | 9999 | 1 | 70 |  | GENTPJ | PSS2A | HYGOVR |  | Closed | 52.2 | 15.1422 | HY | 71.9 |  | NO | 0.003 | 0.34 | 3.69 | 2.6531 | 0.138 | 0.46 | 3.3333 | 13.8 |  |  | HY (Hydro) | 2
30 | PG AND E | 50 | US Bur Reclam |  | 37551 | 3 | 3 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 0 | 69 | -30 | 22 | 9999 | -3.1 | 65.9 |  | GENTPJ | PSS2A | HYGOVR |  | Closed | 52.2 | 15.1422 | HY | 71.9 |  | NO | 0.003 | 0.34 | 3.69 | 2.6531 | 0.127 | 0.46 | 3.622 | 13.8 |  |  | HY (Hydro) | 3
30 | PG AND E | 50 | US Bur Reclam |  | 37553 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 90 | -34 | 50 | 9999 | 2.38e-06 | 90 |  | GENQEC | PSS2C | HYGOV4 | ST4C | Closed | 85 | 5.4285 | HY | 80 |  | NO | 0.003 | 0.201 | 3.55 | 2.84 |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37553 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 90 | -34 | 50 | 9999 | 2.38e-06 | 90 |  | GENQEC | PSS2C | HYGOV4 | ST4C | Closed | 85 | 5.4285 | HY | 80 |  | NO | 0.003 | 0.201 | 3.55 | 2.84 |  |  | NAN | 13.8 |  |  | HY (Hydro) | 2
30 | PG AND E | 50 | US Bur Reclam |  | 37556 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 40 | -5 | 5 | 9999 | -4 | 36 |  | GENTPJ | PSS2B | HYGOV4 | ESST6B | Open | 0 | 0 | HY | 41.053 |  | NO | 0.008 | 0.289 | 2.02 | 0.82927 | 0.14 | 0.52 | 3.7143 | 6.9 |  |  | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 50 | US Bur Reclam |  | 37557 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 40 | -5 | 5 | 9999 | -4 | 36 |  | GENTPJ | PSS2B | HYGOV4 | ESST6B | Open | 0 | 0 | HY | 41.053 |  | NO | 0.008 | 0.289 | 2.02 | 0.82927 | 0.14 | 0.52 | 3.7143 | 6.9 |  |  | HY (Hydro) | 3 |  | PSS Exempt
30 | PG AND E | 50 | US Bur Reclam |  | 37559 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 40 | -5 | 5 | 9999 | -4 | 36 |  | GENTPJ | PSS2B | HYGOV4 | ESST6B | Closed | 30 | -2.4616 | HY | 41.053 |  | NO | 0.008 | 0.289 | 2.02 | 0.82927 | 0.14 | 0.52 | 3.7143 | 6.9 |  |  | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 50 | US Bur Reclam |  | 37561 | 1 | 1 |  | Missing BA | [6 empty] | RX Ratio | [10 empty] | 0 | 166.7 | -60 | 60 | 9999 | 23.3 | 190 |  | GENQEC | PSS2C | HYGOVR | ST4C | Closed | 65.7 | 5.4983 | HY | 166.67 |  | NO | 0.503 | 0.25 | 3.8 | 6.3335 |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37562 | 2 | 2 |  | Missing BA | [6 empty] | RX Ratio | [10 empty] | 0 | 166.7 | -60 | 60 | 9999 | 23.3 | 190 |  | GENQEC | PSS2C | HYGOVR | ST4C | Closed | 150 | 5.7098 | HY | 166.67 |  | NO | 0.503 | 0.25 | 3.8 | 6.3335 |  |  | NAN | 13.8 |  |  | HY (Hydro) | 2
30 | PG AND E | 50 | US Bur Reclam |  | 37575 | 1 | 1 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 0 | 142 | -50 | 50 | 9999 | 2 | 144 |  | GENTPJ | PSS2A | HYGOVR |  | Closed | 80 | -8.2615 | HY | 142 |  | NO | 0.003 | 0.284 | 2.77 | 3.9334 | 0.18 | 0.5 | 2.7778 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37576 | 2 | 2 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 0 | 142 | -50 | 50 | 9999 | 2 | 144 |  | GENTPJ | PSS2A | HYGOVR |  | Closed | 80 | -8.2615 | HY | 142 |  | NO | 0.003 | 0.284 | 2.77 | 3.9334 | 0.18 | 0.5 | 2.7778 | 13.8 |  |  | HY (Hydro) | 2
30 | PG AND E | 50 | US Bur Reclam |  | 37577 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 142 | -50 | 50 | 9999 | 2 | 144 |  | GENTPJ | PSS2B | HYGOVR | ESST6B | Closed | 100 | -6.942 | HY | 142 |  | NO | 0.003 | 0.27 | 2.77 | 3.9334 | 0.2 | 0.69 | 3.45 | 13.8 |  |  | HY (Hydro) | 3
30 | PG AND E | 50 | US Bur Reclam |  | 37578 | 4 | 4 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 0 | 142 | -50 | 50 | 9999 | 2 | 144 |  | GENTPJ | PSS2B | HYGOVR | ESST6B | Closed | 100 | -6.942 | HY | 142 |  | NO | 0.003 | 0.27 | 2.77 | 3.9334 | 0.2 | 0.69 | 3.45 | 13.8 |  |  | HY (Hydro) | 4
30 | PG AND E | 50 | US Bur Reclam |  | 37579 | 5 | 5 |  | Missing BA | [17 empty] | 0 | 142 | -50 | 50 | 9999 | 2 | 144 |  | GENTPJ | PSS2B | HYGOVR | ESST6B | Closed | 100 | -6.94 | HY | 142 |  | NO | 0.003 | 0.27 | 2.77 | 3.9334 | 0.2 | 0.69 | 3.45 | 13.8 |  |  | HY (Hydro) | 5
30 | PG AND E | 50 | US Bur Reclam |  | 37581 | 1 | 1 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 0 | 100 | -50 | 54 | 9999 | -8 | 92 |  | GENTPJ | PSS2A | HYGOV4 |  | Closed | 75 | 6.9226 | HY | 100 |  | NO | 0.007 | 0.299 | 3.7 | 3.7 | 0.1 | 0.53 | 5.3 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37581 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 100 | -50 | 54 | 9999 | -8 | 92 |  | GENTPJ | PSS2A | HYGOV4 | ST4C | Closed | 75 | 6.9226 | HY | 100 |  | NO | 0.007 | 0.299 | 3.8 | 3.8 | 0.11 | 0.41 | 3.7273 | 13.8 |  |  | HY (Hydro) | 2
30 | PG AND E | 50 | US Bur Reclam |  | 37590 | 1 | 1 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 0 | 66 | -35 | 35 | 9999 | 0.74 | 66.74 |  | GENTPJ | PSS2A | HYGOV4 |  | Closed | 35 | 13.3749 | HY | 73.684 |  | NO | 0.006 | 0.292 | 2.307 | 1.6999 | 0.08 | 0.53 | 6.625 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 50 | US Bur Reclam |  | 37590 | 2 | 2 |  | Missing BA | [5 empty] | PSS No Ex | [11 empty] | 0 | 66 | -35 | 35 | 9999 | 0.74 | 66.74 |  | GENTPJ | PSS2A | HYGOV4 |  | Closed | 35 | 13.3749 | HY | 73.684 |  | NO | 0.006 | 0.292 | 2.307 | 1.6999 | 0.07 | 0.55 | 7.8571 | 13.8 |  |  | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 50 | US Bur Reclam |  | 37645 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 6 | -3.5 | 4 | 9999 | 1.4 | 7.4 |  | GENTPJ | PSS2B | HYGOV4 | ESST4B | Closed | 5.2 | -2.3948 | HY | 8.625 |  | NO | 0.006 | 0.282 | 1.62 | 0.13972 | 0.11 | 0.53 | 4.8182 | 4.2 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37645 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 6 | -3.5 | 4 | 9999 | 1.4 | 7.4 |  | GENTPJ | PSS2B | HYGOV4 | ESST4B | Closed | 5.2 | -2.3948 | HY | 8.625 |  | NO | 0.006 | 0.282 | 1.62 | 0.13972 | 0.11 | 0.53 | 4.8182 | 4.2 |  |  | HY (Hydro) | 2
30 | PG AND E | 313 | City of Redding |  | 37940 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 16 | -5.7 | 8.2 | 9999 | 1.6 | 17.6 |  | GENROU | PSS2A | TGOV1 | ESST4B | Open | 0 | 0 | JE | 21.176 |  | NO | 0 | 0.18 | 6 | 1.2706 | 0.1306 | 0.6616 | 5.0658 | 13.8 |  | REDGPW_13.8_CT1 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37941 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit | [14 empty] | 0 | 23 | -11 | 12.1 | 9999 | 3.8 | 26.8 |  | GENROU | PSS2B | TGOV1 | ESAC8B_GE | Closed | 23.03 | 3.0557 | JE | 31.04 |  | NO | 0 | 0.141 | 6.2 | 1.9245 | 0.166 | 0.625 | 3.7651 | 13.8 |  | REDGPW_13.8_CT2 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37942 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 23 | -11.5 | 10.9 | 9999 | 2.4 | 25.4 |  | GENROU | PSS2B | TGOV1 | ESAC8B_GE | Closed | 20.44 | 2.9091 | JE | 31.04 |  | NO | 0 | 1e-05 | 6.2 | 1.9245 | 0.166 | 0.625 | 3.7651 | 13.8 |  | REDGPW_13.8_CT3 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37944 | 1 | 1 |  | Missing BA | [14 empty] | Missing PS | Missing Sub R/X |  | 0 | 27 | -0.9 | 14.9 | 9999 | 1.5 | 28.5 |  | GENROU |  | TGOV1 | ESAC5A | Closed | 24 | 3.3091 | JE | 31.5 |  | NO | 0 | 1e-05 | 5.7 | 1.7955 | 0.098 | 0.3124 | 3.1878 | 13.8 |  | REDGPW_13.8_ST1 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37958 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 39 | -3.8 | 18.2 | 9999 | 4.5 | 43.5 |  | GENROU | PSS2B | TGOV1 | ESAC1A | Closed | 37 | 5.6753 | JE | 50 |  | NO | 0 | 1e-05 | 8 | 4 | 0.0965 | 0.233 | 2.4145 | 13.8 |  | REDGPW_13.8_CT4 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37963 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 40 | -7.8 | 18 | 9999 | 4.8 | 44.8 |  | GENROU | PSS2B | TGOV1 | ESAC1A | Closed | 38 | 5.754 | JE | 50 |  | NO | 0 | 1e-05 | 6 | 3 | 0.0965 | 0.233 | 2.4145 | 13.8 |  | REDGPW_13.8_CT5 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38020 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 1 | -0.24 | 0.49 | 9999 | 0.11 | 1.11 |  | GENTPJ |  | HYG3 | ESST4B | Open | 0 | 0 | HY | 1.11 |  | NO | 0 | 1e-05 | 3 | 0.0333 | 0.15 | 0.45 | 3 | 115 |  |  | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38020 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 2.5 | -0.61 | 1.22 | 9999 | 0.28 | 2.78 |  | GENTPJ |  | HYG3 | ESST4B | Open | 0 | 0 | HY | 2.78 |  | NO | 0 | 1e-05 | 3 | 0.0834 | 0.15 | 0.45 | 3 | 115 |  |  | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38054 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 0 | 4.2 | 0 | 0 | 9999 | -4.2 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 4.42 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 60 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 361 | City of Roseville |  | 38071 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 50 | -10 | 20 | 9999 | 15 | 65 |  | GENROU | PSS2A | GGOV1 | EXST4B | Closed | 47.5 | 8.4688 | JE | 65 |  | NO | 0 | 1e-05 | 6.5 | 4.225 | 0.05 | 0.3 | 6 | 13.8 |  | FDYMNT_13.8_CT1 | JE (Jet Engine) | 1
30 | PG AND E | 361 | City of Roseville |  | 38079 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 50 | -10 | 20 | 9999 | 15 | 65 |  | GENROU | PSS2A | GGOV1 | EXST4B | Closed | 47.5 | 8.4688 | JE | 65 |  | NO | 0 | 1e-05 | 6.5 | 4.225 | 0.05 | 0.3 | 6 | 13.8 |  | FDYMNT_13.8_CT2 | JE (Jet Engine) | 2
30 | PG AND E | 361 | City of Roseville |  | 38080 | 3 | 3 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 70 | -29.4 | 35 | 9999 | -70 |  |  | GENROU | PSS2A |  | EXST4B | Closed | 70 | 13.7908 | JE | 65 |  | NO | 0 | 1e-05 | 4.5 | 2.925 | 0.05 | 0.3 | 6 | 13.8 |  | FDYMNT_13.8_STG | JE (Jet Engine) | 3
30 | PG AND E | 361 | City of Roseville |  | 38091 | 4 | 4 |  | Missing BA |  |  |  |  | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  | Missing Sub R/X |  | 0 | 37 | -18.5 | 33 | 9999 | -7 | 30 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 25 | 6.3283 | UN | 30 | PF<0.8 | NO | 0 | 1e-05 | 2.05 | 0.615 | 0.134 | 0.39 | 2.9104 | 13.8 |  |  | UN (Unknown) | 4
30 | PG AND E | 361 | City of Roseville |  | 38091 | 5 | 5 |  | Missing BA |  |  |  |  | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  | Missing Sub R/X |  | 0 | 37 | -18.5 | 33 | 9999 | -7 | 30 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 25 | 6.3283 | UN | 30 | PF<0.8 | NO | 0 | 1e-05 | 2.05 | 0.615 | 0.134 | 0.39 | 2.9104 | 13.8 |  |  | UN (Unknown) | 5
30 | PG AND E | 392 | Northern California Power Agency |  | 38106 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 33.5 | -14.7 | 38.5 | 999 | -33.5 |  |  | GENROU | PSS2B |  | ESAC7B | Closed | 23.8 | 3.3243 | ST | 64 | PF<0.8 | NO | 0 | 0.165 | 5.8 | 3.712 | 0.192 | 0.604 | 3.1458 | 13.8 |  | NCPA_7_GP1UN1 | ST (Steam Turbine) | 1
30 | PG AND E | 392 | Northern California Power Agency |  | 38108 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 30.5 | -14 | 39.5 | 999 | -30.5 |  |  | GENROU | PSS2B |  | ESAC7B | Closed | 21.8 | 3.1918 | ST | 64 | PF<0.8 | NO | 0 | 0.165 | 5.8 | 3.712 | 0.192 | 0.604 | 3.1458 | 13.8 |  | NCPA_7_GP1UN2 | ST (Steam Turbine) | 1
30 | PG AND E | 361 | City of Roseville |  | 38116 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 25.6 | -8.8 | 12.4 | 9999 | -0.9 | 24.7 |  | GENROU |  | GGOV1 | EXST4B | Closed | 24 | 2.039 | JE | 28.4 |  | NO | 0 | 1 | 8.77 | 2.4907 | 0.101 | 0.277 | 2.7426 | 13.8 |  | ROSVIL_13.8_GT1 | JE (Jet Engine) | 1
30 | PG AND E | 361 | City of Roseville |  | 38117 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 25.6 | -8.8 | 12.4 | 9999 | -0.9 | 24.7 |  | GENROU |  | GGOV1 | EXST4B | Open | 0 | 0 | JE | 28.4 |  | NO | 0 | 1 | 8.77 | 2.4907 | 0.101 | 0.277 | 2.7426 | 13.8 |  | ROSVIL_13.8_GT2 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38134 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 0.4 | 0 | 0 | 9999 | -2e-08 | 0.4 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 0.17 | 0 | HY | 0.4 |  | NO | 0 | 1e-05 | 3 | 0.012 | 0.15 | 0.45 | 3 | 69 |  |  | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38150 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 3.35 | -1.2 | 2.45 | 9999 | -3.35 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.4 | 0.24609 | IT | 4.06 |  | NO | 0 | 1e-05 | 1.47 | 0.059682 | 0.01 | 0.001 | 0.1 | 4.16 |  |  | IT (Internal Combustion Turbo Charged) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38150 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 3.35 | -1.2 | 2.45 | 9999 | -3.35 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.4 | 0.24609 | IT | 4.06 |  | NO | 0 | 1e-05 | 1.47 | 0.059682 | 0.01 | 0.001 | 0.1 | 4.16 |  |  | IT (Internal Combustion Turbo Charged) | 2
30 | PG AND E | 334 | Modesto Irrigation District |  | 38207 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 26.32 | -8.92 | 9.36 | 9999 | -26.32 |  |  | REGC_A |  |  | REEC_B | Closed | 19 | -5.4214 | PV | 28.69 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.34 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38330 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact |  |  | Unreas H | Unreas Sat |  |  |  | Miss Turbine Type |  | Missing PS |  |  | 0 | 49.2 | -24.6 | 36.9 | 9999 | -49.2 |  |  | GENTPJ |  |  | ESAC8B_GE | Open | 0 | 0 | UN | 61.5 | PF<0.8 | NO | 0 | 1e-05 | 1.267 | 0.7792 | 0.07 | 0.18 | 2.5714 | 0.48 |  |  | UN (Unknown) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38346 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 5.7 | -1.9 | 2.8 | 9999 | -5.7 | [6 empty] | Open | 0 | 0 | GT | 6.3 |  | NO | 0 | 0.264 | 0 |  |  |  | NAN | 9.11 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38350 | 1 | 1 |  | Missing BA | [17 empty] | 11 | 46 | -14 | 22.5 | 9999 | 11.9 | 57.9 |  | GENTPJ | PSS2A | HYGOV4 | ESST1A_GE | Closed | 45 | -6.0882 | HY | 47.9 |  | YES | 0 | 0.256 | 2.572 | 1.232 | 0.127 | 0.352 | 2.7717 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38351 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 20 | 48 | -20 | 53.1 | 9999 | 3 | 51 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 24 | -0.19542 | JE | 71.176 | PF<0.8 | YES | 0 | 1e-05 | 1.258 | 0.89539 | 0.295 | 0.792 | 2.6847 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38352 | 1 | 1 |  | Missing BA | [17 empty] | 28 | 53.5 | -10 | 54 | 9999 | 6.5 | 60 |  | GENROU | PSS2A | GGOV1 | ESST4B | Open | 0 | 0 | GT | 71.889 | PF<0.8 | YES | 0 | 0.472 | 7.82 | 5.6217 | 0.124 | 0.359 | 2.8952 | 13.8 |  |  | GT (Gas Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 334 | Modesto Irrigation District |  | 38353 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 20 | 46 | -20 | 53.1 | 9999 | 5 | 51 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 24 | -0.20311 | JE | 71.176 | PF<0.8 | YES | 0 | 1e-05 | 1.258 | 0.89539 | 0.295 | 0.792 | 2.6847 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38354 | 1 | 1 |  | Missing BA | [17 empty] | 28 | 53.5 | -10 | 54 | 9999 | 6.5 | 60 |  | GENROU | PSS2A | GGOV1 | ESST4B | Open | 0 | 0 | GT | 71.889 | PF<0.8 | YES | 0 | 0.472 | 7.82 | 5.6217 | 0.124 | 0.359 | 2.8952 | 13.8 |  |  | GT (Gas Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 334 | Modesto Irrigation District |  | 38356 | 1 | 1 |  | Missing BA | [7 empty] | Unreas H | Unreas Sat | [8 empty] | 30 | 45 | -20 | 22 | 9999 | 11.7 | 56.7 |  | GENROU |  | GGOV1 | ESAC1A | Closed | 43 | -5.647 | GT | 56.7 |  | YES | 0 | 0.472 | 1.285 | 0.72859 | 0.223 | 0.41 | 1.8386 | 13.8 |  |  | GT (Gas Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 334 | Modesto Irrigation District |  | 38357 | 1 | 1 |  | Missing BA |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | [7 empty] | Missing Sub R/X |  | 25 | 48 | -26.0556 | 26.3889 | 9999 | 2 | 50 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 49 | -4.3596 | GT | 71.176 |  | YES | 0 | 1e-05 | 1.17 | 0.83276 | 0.1207 | 0.4943 | 4.0953 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38357 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 27 | -38.2732 | 33.9718 | 9999 | -27 |  |  | GENTPJ | PSS2A |  | ESAC8B_GE | Closed | 7 | -4.3596 | GT | 44.388 | PF<0.8 | YES | 0 | 1e-05 | 3.9 | 1.7311 | 0.075 | 0.267 | 3.56 | 13.8 |  |  | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38365 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 2.2 | -0.6667 | 1.3333 | 9999 | -2.2 |  |  | GENTPJ |  |  |  | Closed | 0.8 | -0.096276 | HY | 2.2 |  | NO | 0 | 1 | 3 | 0.066 | 0.152 | 0.59 | 3.8816 | 12 |  | NHOGAN_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38365 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 2.2 | -0.3333 | 0.6667 | 9999 | -2.2 |  |  | GENTPJ |  |  |  | Closed | 0.8 | -0.096276 | HY | 1.1 |  | NO | 0 | 1 | 3 | 0.033 | 0.152 | 0.59 | 3.8816 | 12 |  | NHOGAN_6_UNITS | HY (Hydro) | 2
30 | PG AND E | 334 | Modesto Irrigation District |  | 38370 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 5 | 8.2 | -0.8125 | 1.1375 | 9999 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 8 | 0.1625 | GT | 10.549 |  | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38371 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 5 | 8.2 | -0.8125 | 1.1375 | 9999 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 8 | 0.1625 | GT | 10.549 |  | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38372 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.3833 | 6.3667 | 9999 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6 | -3.3833 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38373 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.3833 | 6.3667 | 9999 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6 | -3.3833 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38374 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.3 | 5.275 | 9999 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 7 | -3.3 | GT | 10.549 |  | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38375 | 1 | 1 |  | Missing BA | [17 empty] | 5 | 8.2 | -4 | 8.2 | 9999 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38380 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 20 | -9.7 | 9.7 | 9999 | -20 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 20.16 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.34 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38544 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 15 | 54 | 0 | 20 | 9999 | 0.2 | 54.2 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 50 | 9.8167 | JE | 76.94 |  | NO | 0 | 1e-05 | 1.341 | 1.0318 | 0.1092 | 0.479 | 4.3864 | 13.8 |  | ALMOND2 UNIT 2 | JE (Jet Engine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38545 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 15 | 54 | 0 | 20 | 9999 | 0.2 | 54.2 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 50 | 10.179 | JE | 76.94 |  | NO | 0 | 1e-05 | 1.341 | 1.0318 | 0.1092 | 0.479 | 4.3864 | 13.8 |  | ALMOND2 UNIT 3 | JE (Jet Engine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38546 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 15 | 54 | 0 | 20 | 9999 | 0.2 | 54.2 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 50 | 10.2332 | JE | 76.94 |  | NO | 0 | 1e-05 | 1.341 | 1.0318 | 0.1092 | 0.479 | 4.3864 | 13.8 |  | ALMOND2 UNIT 4 | JE (Jet Engine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38550 | 1 | 1 |  | Missing BA | [17 empty] | 10 | 55 | 0 | 10.4 | 9999 | 2.9 | 57.9 |  | GENTPJ | PSS2A | HYGOV4 | ESST1A_GE | Closed | 30 | 1.9187 | HY | 47.9 |  | YES | 0 | 1.072 | 2.572 | 1.232 | 0.127 | 0.352 | 2.7717 | 13.8 |  | DON PEDRO UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38552 | 1 | 1 |  | Missing BA | [17 empty] | 10 | 55 | 0 | 12.7 | 9999 | 2.9 | 57.9 |  | GENTPJ | PSS2A | HYGOV4 | ESST1A_GE | Closed | 30 | 1.3248 | HY | 47.9 |  | YES | 0 | 1.072 | 2.572 | 1.232 | 0.127 | 0.352 | 2.7717 | 13.8 |  | DON PEDRO UNIT 2 | HY (Hydro) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38554 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | 8 | 38.2 | 0 | 17.1 | 9999 | 7e-08 | 38.2 |  | GENTPJ |  | HYG3 | ESST1A_GE | Closed | 30 | 1.4018 | HY | 38.2 |  | YES | 0 | 1.072 | 3 | 1.146 | 0.205 | 0.369 | 1.8 | 13.8 |  | DON PEDRO UNIT 4 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 337 | Turlock Irrigation District |  | 38556 | 1 | 1 |  | Missing BA | [17 empty] | 11 | 24.8 | 0 | 16 | 9999 | -0.8 | 24 |  | GENROU |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | GT | 33.7 |  | YES | 0 | 1.072 | 8.4 | 2.8308 | 0.138 | 0.613 | 4.442 | 13.8 |  | WALNUT_GT UNIT 1 | GT (Gas Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 337 | Turlock Irrigation District |  | 38558 | 1 | 1 |  | Missing BA | [17 empty] | 11 | 24.8 | 0 | 16 | 9999 | -0.8 | 24 |  | GENROU |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | GT | 33.7 |  | YES | 0 | 1.072 | 8.4 | 2.8308 | 0.138 | 0.613 | 4.442 | 13.8 |  | WALNUT_GT UNIT 2 | GT (Gas Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 337 | Turlock Irrigation District |  | 38560 | 1 | 1 |  | Missing BA | [17 empty] | 0.5 | 5 | 0 | 5 | 9999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.9 | 0.32361 | HY | 4 | PF<0.8 | NO | 0 | 4.56 | 4.64 | 0.1856 | 0.152 | 0.59 | 3.8816 | 4.16 |  | LA_GRANGE UNIT 1 (C) | HY (Hydro) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38562 | 1 | 1 |  | Missing BA | [17 empty] | 0.5 | 5 | 0 | 5 | 9999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2 | 0.31582 | HY | 5 | PF<0.8 | NO | 0 | 4.56 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 4.16 |  | DAWSON UNIT | HY (Hydro) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38564 | 1 | 1 |  | Missing BA | [17 empty] | 16 | 49.9 | 0 | 20 | 9999 | 1.35 | 51.25 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 40 | 0.99722 | JE | 57.2 |  | YES | 0 | 1.072 | 1.6 | 0.9152 | 0.179 | 0.56 | 3.1285 | 13.8 |  | ALMOND UNIT | JE (Jet Engine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38570 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 40 | 82.3 | 0 | 40 | 9999 | 1.7 | 84 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 76.5 | 29.7794 | GT | 111.6 |  | YES | 0 | 1e-05 | 5.607 | 6.2574 | 0.08 | 0.3 | 3.75 | 13.8 |  | WEC PWR PLNT UNIT 1 | GT (Gas Turbine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38572 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 25 | 93.6 | 0 | 60 | 9999 | -93.6 |  |  | GENROU | PSS2A |  | ESST4B | Closed | 87 | 30.7096 | CC | 130.3 |  | YES | 0 | 1e-05 | 3.93 | 5.1208 | 0.0806 | 0.357 | 4.4293 | 13.8 |  | WEC PWR PLNT UNIT 3 | CC (Combined Cycle Generic) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38574 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 40 | 82.3 | 0 | 40 | 9999 | 1.7 | 84 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 76.5 | 29.0754 | GT | 111.6 |  | YES | 0 | 1e-05 | 5.607 | 6.2574 | 0.08 | 0.3 | 3.75 | 13.8 |  | WEC PWR PLNT UNIT 2 | GT (Gas Turbine) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 38700 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 32 | -10.71 | 10.71 | 9999 | 2.316 | 34.316 |  | GENTPJ | PSS2B | HYG3 | ESAC6A | Closed | 24.712 | 10.71 | HY | 34.316 |  | NO | 0.003 | 0.34 | 2.4 | 0.82358 | 0.208 | 0.458 | 2.2019 | 13.8 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38705 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 27 | -13.3 | 13.3 | 9999 | 3.555 | 30.555 |  | GENTPJ | PSS2B | HYG3 | ESAC6A | Closed | 24.712 | 11.4493 | HY | 30.555 |  | NO | 0.003 | 0.34 | 2.26 | 0.69054 | 0.25 | 0.634 | 2.536 | 13.8 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38710 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 27 | -13.3 | 13.3 | 9999 | 3.555 | 30.555 |  | GENTPJ | PSS2B | HYG3 | ESAC6A | Closed | 24.712 | 11.4443 | HY | 30.555 |  | NO | 0.003 | 0.34 | 2.26 | 0.69054 | 0.25 | 0.634 | 2.536 | 13.8 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38715 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 27 | -13.3 | 13.3 | 9999 | 3.555 | 30.555 |  | GENTPJ | PSS2B | HYG3 | ESAC6A | Closed | 24.712 | 11.4442 | HY | 30.555 |  | NO | 0.003 | 0.34 | 2.26 | 0.69054 | 0.25 | 0.634 | 2.536 | 13.8 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 939 | Kings River Conservation Distric |  | 38720 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 55 | -16.6 | 26.63 | 9999 | 6.1 | 61.1 |  | GENQEC | PSS2A | HYG3 | ESST4B | Closed | 44 | 13.4831 | HY | 61.1 |  | NO | 0 | 0.31 | 2.8 | 1.7108 |  |  | NAN | 13.8 |  | PINFLT_7_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 939 | Kings River Conservation Distric |  | 38720 | 2 | 2 |  | Missing BA | [17 empty] | 0 | 55 | -16.6 | 26.63 | 9999 | 6.1 | 61.1 |  | GENQEC | PSS2A | HYG3 | ESST4B | Closed | 44 | 13.4831 | HY | 61.1 |  | NO | 0 | 0.31 | 2.8 | 1.7108 |  |  | NAN | 13.8 |  | PINFLT_7_UNITS | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 939 | Kings River Conservation Distric |  | 38720 | 3 | 3 |  | Missing BA | [17 empty] | 0 | 55 | -16.6 | 26.63 | 9999 | 6.1 | 61.1 |  | GENQEC | PSS2A | HYG3 | ESST4B | Closed | 44 | 13.4831 | HY | 61.1 |  | NO | 0 | 0.31 | 2.8 | 1.7108 |  |  | NAN | 13.8 |  | PINFLT_7_UNITS | HY (Hydro) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38730 | 1 | 1 |  | Missing BA | [17 empty] | -48 | 53 | -10.6 | 8.908 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Closed | 45.442 | 3.4861 | HY | 53 |  | YES | 0 | 0.18 | 5.1 | 2.703 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38730 | 2 | 2 |  | Missing BA | [17 empty] | -48 | 53 | -10.6 | 8.908 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Closed | 45.442 | 3.4861 | HY | 53 |  | YES | 0 | 0.18 | 4.7 | 2.491 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38735 | 1 | 1 |  | Missing BA | [17 empty] | -48 | 53 | -10.6 | 8.908 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Closed | 45.442 | 3.4684 | HY | 53 |  | YES | 0 | 0.18 | 5.1 | 2.703 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 3 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38735 | 2 | 2 |  | Missing BA | [17 empty] | -48 | 53 | -10.6 | 8.908 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Closed | 45.442 | 3.4684 | HY | 53 |  | YES | 0 | 0.18 | 4.7 | 2.491 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 4 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38740 | 1 | 1 |  | Missing BA | [17 empty] | -48 | 53 | -26.5 | 18.55 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Open | 0 | 0 | HY | 53 |  | YES | 0 | 0.18 | 5.1 | 2.703 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 5 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38740 | 2 | 2 |  | Missing BA | [17 empty] | -48 | 53 | -26.5 | 18.55 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Open | 0 | 0 | HY | 53 |  | YES | 0 | 0.18 | 4.7 | 2.491 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 6 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38745 | 1 | 1 |  | Missing BA | [17 empty] | -48 | 53 | -26.5 | 18.55 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Open | 0 | 0 | HY | 53 |  | YES | 0 | 0.18 | 4.7 | 2.491 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 7 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38745 | 2 | 2 |  | Missing BA | [17 empty] | -48 | 53 | -26.5 | 18.55 | 9999 | -53 |  |  | GENTPJ |  |  | EXDC1 | Open | 0 | 0 | HY | 53 |  | YES | 0 | 0.18 | 4.7 | 2.491 | 0.19 | 0.63 | 3.3158 | 13.8 |  | SLUISP_2_UNITS unit 8 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38750 | 1 | 1 |  | Missing BA | [17 empty] | -30 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -24.204 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  | DOSMGO_2_NSPIN | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38750 | 2 | 2 |  | Missing BA | [17 empty] | -30 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -24.204 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  | DOSMGO_2_NSPIN | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38750 | 3 | 3 |  | Missing BA | [17 empty] | -30 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -24.204 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  | DOSMGO_2_NSPIN | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38755 | 1 | 1 |  | Missing BA | [17 empty] | -30 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -24.204 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  | DOSMGO_2_NSPIN | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38755 | 2 | 2 |  | Missing BA | [17 empty] | -30 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  | DOSMGO_2_NSPIN | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38755 | 3 | 3 |  | Missing BA | [17 empty] | -30 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  | DOSMGO_2_NSPIN | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38760 | 10 | 10 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 10 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38760 | 11 | 11 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 11 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38765 | 8 | 8 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 8 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38765 | 9 | 9 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 9 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38770 | 6 | 6 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 6 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38770 | 7 | 7 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 7 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -6.54 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 6 |  | NO | 0 | 1 | 1.7167 | 0.103 | 0.5 | 0.67 | 1.34 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -6.54 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 6 |  | NO | 0 | 1 | 1.7167 | 0.103 | 0.5 | 0.67 | 1.34 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -6.54 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 6 |  | NO | 0 | 1 | 1.7167 | 0.103 | 0.5 | 0.67 | 1.34 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 4 | 4 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 5 | 5 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 5 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 6 | 6 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 6 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 4 | 4 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -7.69 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 7 |  | NO | 0 | 1 | 1.8286 | 0.128 | 0.455 | 0.818 | 1.7978 | 13.2 |  |  | MP (Motor/Pump) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -7.69 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 7 |  | NO | 0 | 1 | 1.8286 | 0.128 | 0.455 | 0.818 | 1.7978 | 13.2 |  |  | MP (Motor/Pump) | 2
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -7.69 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 7 |  | NO | 0 | 1 | 1.8286 | 0.128 | 0.455 | 0.818 | 1.7978 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 4 | 4 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.666 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 5 | 5 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.666 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 5 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.666 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.666 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.666 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 4 | 4 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.666 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38795 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -16.92 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -16.4 | 0 | MP | 16 |  | NO | 0 | 1 | 1.9062 | 0.30499 | 0.321 | 0.64 | 1.9938 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38795 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -16.92 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 16 |  | NO | 0 | 1 | 1.9062 | 0.30499 | 0.321 | 0.64 | 1.9938 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38795 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -16.92 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 16 |  | NO | 0 | 1 | 1.9062 | 0.30499 | 0.321 | 0.64 | 1.9938 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38800 | 1 | 1 |  | Missing BA | [17 empty] | -33.84 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -30.933 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38800 | 2 | 2 |  | Missing BA | [17 empty] | -33.84 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -30.933 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38805 | 1 | 1 |  | Missing BA | [17 empty] | -33.84 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -30.933 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38805 | 2 | 2 |  | Missing BA | [17 empty] | -33.84 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -30.933 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38810 | 1 | 1 |  | Missing BA | [17 empty] | -33.84 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -30.933 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38810 | 2 | 2 |  | Missing BA | [17 empty] | -33.84 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -30.933 | 0 | MP | 33 |  | NO | 0 | 1 | 1.906 | 0.62898 | 0.159 | 0.42 | 2.6415 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38815 | 4 | 4 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38815 | 5 | 5 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 5 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38820 | 1 | 1 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -8.9 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 9 |  | NO | 0 | 1e-05 | 1.7689 | 0.1592 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 38820 | 2 | 2 |  | Missing BA | [8 empty] | Unreas Sat | [8 empty] | -8.9 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 9 |  | NO | 0 | 1e-05 | 1.7689 | 0.1592 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 2
30 | PG AND E | 362 | Department of Water Resources |  | 38820 | 3 | 3 |  | Missing BA | [8 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 9999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -26.666 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38825 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 123.157 | -34 | 38 | 9999 | -5.4e-07 | 123.157 |  | GENTPJ | PSS2A | HYG3 | EXDC1 | Closed | 114.05 | 33.8273 | HY | 123.157 |  | NO | 0.002 | 0.18 | 3.6 | 4.4337 | 0.164 | 0.379 | 2.311 | 12.5 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38830 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 115 | -56 | 60 | 9999 | 2.38e-06 | 115 |  | GENTPJ | PSS2A | HYG3 | EXDC1 | Closed | 109 | 33.923 | HY | 115 |  | NO | 0.002 | 0.18 | 3.8 | 4.37 | 0.163 | 0.378 | 2.319 | 12.5 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38835 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 123.157 | -34 | 38 | 9999 | -5.4e-07 | 123.157 |  | GENTPJ | PSS2A | HYG3 | EXDC1 | Closed | 114.05 | 33.5991 | HY | 123.157 |  | NO | 0.002 | 0.18 | 3.6 | 4.4337 | 0.164 | 0.379 | 2.311 | 12.5 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38840 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 115 | -56 | 60 | 9999 | 2.38e-06 | 115 |  | GENTPJ | PSS2A | HYG3 | EXDC1 | Closed | 109 | 38.9117 | HY | 115 |  | NO | 0.002 | 0.18 | 3.8 | 4.37 | 0.178 | 0.391 | 2.1966 | 12.5 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38845 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 123.157 | -34 | 38 | 9999 | -5.4e-07 | 123.157 |  | GENTPJ | PSS2A | HYG3 | EXDC1 | Closed | 114.05 | 37.4545 | HY | 123.157 |  | NO | 0.002 | 0.18 | 3.6 | 4.4337 | 0.145 | 0.335 | 2.3103 | 12.5 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38850 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 115 | -56 | 60 | 9999 | 2.38e-06 | 115 |  | GENTPJ | PSS2A | HYG3 | EXDC1 | Open | 0 | 0 | HY | 115 |  | NO | 0.002 | 0.18 | 3.8 | 4.37 | 0.142 | 0.33 | 2.3239 | 12.5 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38950 | 1 | 1 |  | Missing BA |  |  |  |  | Limit Power Fact | [12 empty] | -418 | 0 | 0.01765 | 0.01765 | 9999 | 0 | [6 empty] | Closed | -413.7203 | 0.01765 | DC | 400 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 180.5 | BES Exempt |  | DC (Represents DC ties) | 1 | Netting Exempt | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38951 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 400.001 | 1.3e-05 | 1.3e-05 | 9999 | -400.001 | [6 empty] | Closed | 400 | 1.3e-05 | DC | 400 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 180.5 | BES Exempt |  | DC (Represents DC ties) | 1 | Netting Exempt | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 39185 | 1 | 1 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -13.15 | 13.15 | -9.9 | 9.9 | 999 | -13.15 |  |  | REGC_A |  |  | REEC_C | Closed | 9.205 | -1.3465 | BA | 16.5 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 39233 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [15 empty] | 0 | 80.5 | 0 | 0 | 9999 | -80.5 |  |  | WT4G |  | WT4T | WT4E | Open | 0 | 0 | W4 | 89.444 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWND2_1_UNITS | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 39346 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -313.5 | 306.8 | -103 | 103 | 999 | -306.8 |  |  | REGC_A |  |  | REEC_C | Closed | 138.06 | 90.8123 | BA | 330 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
40 | NORTHWEST | 449 | Centralia City Light | Bonneville Power Admin | 40199 | 1 | 1 | [10 empty] | Unreas Sat |  | Gen on HV | [6 empty] | 0 | 12 | 0 | 0 | 14 | -12 |  |  | GENTPF |  |  |  | Closed | 3 | 0 | HY | 25 |  | NO | 0 | 0.2 | 3 | 0.75 | 0 | 0 | NAN | 69 |  | B_STREET_69_YELM_G1_3 | HY (Hydro) | 1
40 | NORTHWEST | 417 | Midstate Electric Co-op | Bonneville Power Admin | 40237 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 5 | -0.5 | -0.2 | 14 | -5 | [6 empty] | Closed | 4.5 | -0.35 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 115 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 427 | Cosmo Speciality Fiber | Bonneville Power Admin | 40277 | C1 | C1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 15.8 | 0 | 0 | 14 | -15.8 | [6 empty] | Closed | 15.8 | 0 | ST | 12 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | WEYERHSR | ST (Steam Turbine) | C1
40 | NORTHWEST | 187 | Sierra Pacific Industries | Bonneville Power Admin | 40277 | S1 | S1 | [12 empty] | Gen on HV | [6 empty] | 0 | 12 | 0 | 0 | 14 | -12 |  |  | (GENROU) |  |  |  | Closed | 8 | 0 | GT | 12 |  | NO | 0 | 0.2 | 0 |  | 0.05 | 0.3 | 6 | 115 |  | SIERRA_G | GT (Gas Turbine) | S1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40278 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -51.3 | 50 | -32 | 20.5 | 14 | 1.5 | 51.5 |  | GENTPJ | PSSSB | HYG3 | EXST1_GE | Open | 0 | 0 | HY | 50 | PF<-0.85 | YES | 0 | 0.2 | 3.129 | 1.5645 | 0.21 | 0.5 | 2.381 | 13.8 |  | G_COULEE_13.8_PG8 | HY (Hydro) | 8
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40282 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40282 | 2 | 2 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 51.5 | PF<0.8 | NO | 0 | 0.2 | 3.36 | 1.7304 | 0.091 | 0.318 | 3.4945 | 13.8 |  |  | HY (Hydro) | 2
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40284 | 3 | 3 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 3
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40284 | 4 | 4 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 51.5 | PF<0.8 | NO | 0 | 0.2 | 3.36 | 1.7304 | 0.091 | 0.318 | 3.4945 | 13.8 |  |  | HY (Hydro) | 4
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40286 | 5 | 5 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 5
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40286 | 6 | 6 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 6
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40291 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 690 | -240 | 185 | 14 | 36 | 726 |  | GENTPJ | PSS2B | HYGOVR |  | Open | 0 | 0 | HY | 707.8 |  | YES | 0 | 0.2 | 4.474 | 31.667 | 0.06 | 0.28 | 4.6667 | 15 |  | G_COULEE_15_G19 | HY (Hydro) | 1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40293 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 690 | -270 | 225 | 14 | 36 | 726 |  | GENTPJ | PSS2B | HYGOVR |  | Closed | 600 | 126.1995 | HY | 707.8 |  | YES | 0 | 0.2 | 4.474 | 31.667 | 0.06 | 0.28 | 4.6667 | 15 |  | G_COULEE_15_G20 | HY (Hydro) | 1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40296 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 805 | -346.464 | 279.04 | 14 | 21 | 826 |  | GENTPJ | PSS2B | HYGOVR |  | Closed | 633.536 | -25.2396 | HY | 825.6 |  | YES | 0 | 0.2 | 4.972 | 41.0488 | 0.13 | 0.28 | 2.1538 | 15 |  | G_COULEE_15_G22 | HY (Hydro) | 1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40298 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 805 | -300 | 250 | 14 | 21 | 826 |  | GENTPJ | PSS2B | HYGOVR |  | Closed | 700 | 126.1992 | HY | 825.6 |  | YES | 0 | 0.2 | 4.972 | 41.0488 | 0.08 | 0.26 | 3.25 | 15 |  | G_COULEE_15_G24 | HY (Hydro) | 1
40 | NORTHWEST | 54 | Lewis PUD | Bonneville Power Admin | 40307 | 1 | 1 | [12 empty] | Gen on HV |  |  |  | Missing PS |  |  | 0 | 35 | -34.04 | 22.02 | 14 | 0.1 | 35.1 |  | GENTPJ |  | HYG3 | EXST1_GE | Closed | 19.9 | 4.9933 | HY | 39 | PF<-0.85 | YES | 0 | 0.2 | 2.8 | 1.092 | 0.155 | 0.33 | 2.129 | 230 |  | COWFALLS_230_G01 | HY (Hydro) | 1
40 | NORTHWEST | 54 | Lewis PUD | Bonneville Power Admin | 40307 | 2 | 2 | [12 empty] | Gen on HV |  |  |  | Missing PS |  |  | 0 | 35 | -12.6 | 16.1 | 14 | 0.1 | 35.1 |  | GENTPJ |  | HYG3 | EXST1_GE | Closed | 19.9 | 4.9933 | HY | 39 |  | NO | 0 | 0.2 | 2.8 | 1.092 | 0.155 | 0.33 | 2.129 | 230 |  | COWFALLS_230_G02 | HY (Hydro) | 2
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 40346 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 15 | -10.05 | 2.16 | 14 | 2.25 | 17.25 |  | (GENTPJ) | (PSS2A) | (HYGOV4) | (EXST1_GE) | Closed | 13.9 | 2.16 | HY | 17.25 | PF<-0.85 | YES | 0 | 0.2 | 0 |  | 0.21 | 0.6 | 2.8571 | 13.8 |  | DEXTER_13.8_G01 | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 40365 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 266.3 | -143.4196 | 65.7791 | 14 | -266.3 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 224.3 | -16.5204 | HY | 266.32 |  | YES | 0.004 | 0.24 | 2.75 | 7.3238 | 0.21 | 0.42 | 2 | 13.8 |  |  | HY (Hydro) | 3
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40756 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 12.9 | -4.2 | 6.5 | 14 | -12.9 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 8 | -4.2 | HY | 13.6 |  | YES | 0 | 0.234 | 1.8 | 0.2448 | 0.1 | 0.27 | 2.7 | 6.6 |  | ROZA_12.5_PH1 | HY (Hydro) | 1
40 | NORTHWEST | 28 | Northern Wasco PUD | Bonneville Power Admin | 41011 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 6 | 0 | 0 | 14 | -6 | [6 empty] | Closed | 5 | 0 | HY | 5 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 496 | Bonners Ferry, City of | Bonneville Power Admin | 41240 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | 0 | 0 | 14 | -2 |  |  | GENTPF |  |  |  | Closed | 2 | 0 | HY | 4.4 |  | NO | 0 | 0.2 | 3 | 0.132 | 0 | 0 | NAN | 115 |  | MOYIE_115_G01 | HY (Hydro) | 1
40 | NORTHWEST | 1457 | Smith Creek Hydro LLC | Bonneville Power Admin | 41298 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 38 | -8 | 5.8 | 14 | -38 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 36 |  | NO | 0 | 0.2 | 3 | 1.08 | 0 | 0 | NAN | 13.8 |  | SMITHFLS_13.8_G01 | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 41303 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 20 | -12.8 | 11.8 | 14 | -20 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Open | 0 | 0 | HY | 23 | PF<-0.85 | YES | 0 | 0.2 | 2.632 | 0.60536 | 0.185 | 0.54 | 2.9189 | 13.8 |  | DETROIT_13.8_G03 | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 41306 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 12 | 29.9 | -25.275 | 15.23 | 14 | 2.1 | 32 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 14.9 | 5.5609 | HY | 29.9 | PF<-0.85 | YES | 0.007 | 0.299 | 3.28 | 0.98072 | 0.25 | 0.52 | 2.08 | 13.8 |  | LSTCR_PH_13.8_LSTC_G01 | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 41306 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 12 | 29.9 | -26 | 17.5 | 14 | 2.1 | 32 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Open | 0 | 0 | HY | 29.9 | PF<-0.85 | YES | 0.007 | 0.299 | 3.28 | 0.98072 | 0.25 | 0.52 | 2.08 | 13.8 |  | LSTCR_PH_13.8_LSTC_G02 | HY (Hydro) | 2
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 41729 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | 0 | 119.5 | -50 | 6 | 14 | 10.5 | 130 |  | GENTPJ | PSSSB | HYG3 | ESDC1A | Closed | 115 | -11.0796 | HY | 125 |  | YES | 0 | 0.2 | 4.457 | 5.5712 | 0.05 | 0.19 | 3.8 | 13.8 |  | G_COULEE_13.8_G09 | HY (Hydro) | 9
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 41734 | E | E | [10 empty] | Unreas Sat | [8 empty] | 0 | 119.5 | -50 | 6 | 14 | 13.5 | 133 |  | GENTPJ | PSS2A | HYG3 | ESDC1A | Closed | 115 | -11.0796 | HY | 125 |  | YES | 0 | 0.2 | 4.779 | 5.9737 | 0.05 | 0.49 | 9.8 | 13.8 |  | G_COULEE_13.8_G14 | HY (Hydro) | E
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 41735 | F | F | [10 empty] | Unreas Sat | [8 empty] | 0 | 119.5 | -50 | 6 | 14 | 13.5 | 133 |  | GENTPJ | PSS2A | HYG3 | ESDC1A | Closed | 115 | -11.0796 | HY | 125 |  | YES | 0 | 0.2 | 4.779 | 5.9737 | 0.05 | 0.55 | 11 | 13.8 |  | G_COULEE_13.8_G15 | HY (Hydro) | F
40 | NORTHWEST | 30 | Puget Sound Energy | Puget Sound Energy | 42332 | 5 | 5 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 6.6 | -2.4 | 3.4 | 30 | -0.1 | 6.5 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 6.5 | -2.4 | HY | 7.105 |  | NO | 0 | 1 | 2.2 | 0.15631 | 0.17 | 0.45 | 2.6471 | 6.9 |  | SNOQUALM_6.9_PH1-5 | HY (Hydro) | 5 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 42990 | Z4 | Z4 | [17 empty] | Missing Sub R/X |  | 0 | 151.8 | -73.5 | 73.5 | 14 | -151.8 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 151.7 | 61.756 | W4 | 168 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | PHALGLCH_0.69_Z1 | W4 (Wind Turbine, Type 4) | Z4 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin [Bus] | 42994 | Z4 | Z4 | [17 empty] | Missing Sub R/X |  | 0 | 190.9 | -92.5 | 92.5 | 14 | -190.9 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 57.27 | 90.5765 | W4 | 212 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | DODGEJCT_0.69_GN1 | W4 (Wind Turbine, Type 4) | Z4 |  | PSS Exempt
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43019 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 182.4 | -76.6251 | 104.8502 | 32 | -182.4 |  |  | GENROU | PSS2C |  |  | Closed | 148.9841 | 35.9267 | CC | 196 |  | YES | 0.001 | 1.862 | 3.08 | 6.0368 | 0.0703 | 0.215 | 3.0583 | 20 |  | BEAVERPG_20_G07 | CC (Combined Cycle Generic) | 1 |  | PSS Exempt
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43359 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 25.7 | -16.8 | 15.4 | 32 | 0.03 | 25.73 |  | GENTPJ | PSS2A | HYGOV4 | ESST1A_GE | Closed | 3.5808 | 3.8495 | HY | 34.5 | PF<-0.85 | NO | 0.004 | 1.52 | 1.71 | 0.58995 | 0.22 | 0.58 | 2.6364 | 13.8 |  | N_FORK_13.8_G02 | HY (Hydro) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43425 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 23 | -12.2634 | 11.7567 | 32 | -23 |  |  | GENTPF |  |  |  | Closed | 8.9597 | 1.8566 | HY | 25 |  | YES | 0 | 1.4 | 2.4 | 0.6 | 0 | 0 | NAN | 13.8 |  | PTLHYDRO_13.8_G1 | HY (Hydro) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43429 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11 | -7.5 | 6.2 | 32 | -11 |  |  | GENTPF |  |  |  | Open | 0 | 0 | HY | 12.5 | PF<-0.85 | YES | 0 | 1.4 | 3.616 | 0.452 | 0 | 0 | NAN | 13.8 |  | PTLHYDRO_13.8_G2 | HY (Hydro) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43465 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -2 | 2.4 | 32 | -5 |  |  | GENTPJ | PSS2B |  | ESST1A_GE | Closed | 1.7103 | 2.4 | HY | 5.5 |  | NO | 0.004 | 0.82 | 2.8 | 0.154 | 0.12 | 0.33 | 2.75 | 11 |  | RIVRMILL_11_G3 | HY (Hydro) | 3
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43466 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -2 | 0 | 32 | -5 |  |  | GENTPJ | PSS2B |  | ESST1A_GE | Closed | 1.7103 | 0 | HY | 5.5 |  | NO | 0.003 | 0.737 | 2.2 | 0.121 | 0.2 | 0.35 | 1.75 | 11 |  | RIVRMILL_11_G4 | HY (Hydro) | 4
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43466 | 5 | 5 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -2 | 2.4 | 32 | -5 |  |  | GENTPJ | PSS2B |  | ESST1A_GE | Closed | 1.7103 | 2.4 | HY | 5.5 |  | NO | 0.004 | 1 | 2 | 0.11 | 0.12 | 0.35 | 2.9167 | 11 |  | RIVRMILL_11_G5 | HY (Hydro) | 5
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43488 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 130 | -89.9035 | 58.4511 | 32 | -130 |  |  | GENTPJ | PSS2A | H6E | ESST1A_GE | Closed | 51.2837 | 36.2519 | HY | 144 | PF<-0.85 | YES | 0.003 | 1.902 | 3.85 | 5.544 | 0.185 | 0.6 | 3.2432 | 13.8 |  | ROUND_BU_13.8_G02 | HY (Hydro) | 2
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43556 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 18 | -10.1614 | -10.1614 | 32 | 15.11 | 33.11 |  | WT1G |  | WT1T |  | Closed | 8.4678 | -10.1614 | HY | 33.11 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | SULIVAN_57_G01 | HY (Hydro) | 1 |  | PSS Exempt
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 44007 | 13 | 13 | [7 empty] | PSS No Ex | [11 empty] | 0 | 80.5 | -41 | 37 | 14 | -80.5 |  |  | GENTPJ | PSS2A | H6E |  | Closed | 50 | 8.1797 | HY | 80.5 |  | YES | 0 | 0.2 | 2.84 | 2.2862 | 0.065 | 0.39 | 6 | 13.8 |  | BONNVILL_13.2_G13 | HY (Hydro) | 13
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 44007 | 14 | 14 | [7 empty] | PSS No Ex | [11 empty] | 0 | 80.5 | -35.2 | 29.2 | 14 | -80.5 |  |  | GENTPJ | PSS2A | H6E |  | Closed | 67 | 8.1797 | HY | 80.5 |  | YES | 0 | 0.2 | 2.84 | 2.2862 | 0.065 | 0.39 | 6 | 13.8 |  | BONNVILL_13.2_G14 | HY (Hydro) | 14
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 44008 | 15 | 15 | [7 empty] | PSS No Ex | [11 empty] | 0 | 80.5 | -35.2 | 29.2 | 14 | -80.5 |  |  | GENTPJ | PSS2A | H6E |  | Closed | 67 | 8.1797 | HY | 80.5 |  | YES | 0 | 0.2 | 2.84 | 2.2862 | 0.065 | 0.39 | 6 | 13.8 |  | BONNVILL_13.2_G15 | HY (Hydro) | 15
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 44008 | 16 | 16 | [7 empty] | PSS No Ex | [11 empty] | 0 | 80.5 | -38 | 33 | 14 | -80.5 |  |  | GENTPJ | PSS2A | H6E |  | Closed | 60 | 8.1797 | HY | 80.5 |  | YES | 0 | 0.2 | 2.84 | 2.2862 | 0.065 | 0.39 | 6 | 13.8 |  | BONNVILL_13.2_G16 | HY (Hydro) | 16
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 44009 | 17 | 17 | [7 empty] | PSS No Ex | [11 empty] | 0 | 80.5 | -36.3 | 30.45 | 14 | -80.5 |  |  | GENTPJ | PSS2A | H6E |  | Closed | 64.25 | 8.1796 | HY | 80.5 |  | YES | 0 | 0.2 | 2.84 | 2.2862 | 0.065 | 0.39 | 6 | 13.8 |  | BONNVILL_13.2_G17 | HY (Hydro) | 17
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 44009 | 18 | 18 | [7 empty] | PSS No Ex | [11 empty] | 0 | 80.5 | -36.3 | 30.45 | 14 | -80.5 |  |  | GENTPJ | PSS2A | H6E |  | Closed | 64.25 | 8.1796 | HY | 80.5 |  | YES | 0 | 0.2 | 2.84 | 2.2862 | 0.065 | 0.39 | 6 | 13.8 |  | BONNVILL_13.2_G18 | HY (Hydro) | 18
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44101 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G01 | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44102 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G02 | HY (Hydro) | 2
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44103 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G03 | HY (Hydro) | 3
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44104 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G04 | HY (Hydro) | 4
40 | NORTHWEST | 28 | Northern Wasco PUD | Bonneville Power Admin | 44128 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model | Missing PS |  |  | 0 | 10 | 0 | 0 | 14 | -10 | [6 empty] | Closed | 8 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 115 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44231 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 155 | -39.3298 | 57.9666 | 14 | 8.42 | 163.42 |  | GENTPJ | PSS2B | IEEEG3_GE | ESST1A_GE | Closed | 138.5 | -26.0827 | HY | 163.42 |  | YES | 0.006 | 0.39 | 3.25 | 5.3111 | 0.184 | 0.48 | 2.6087 | 13.8 |  | LOW_GRAN_13.8_G02 | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44231 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 132 | -48.7327 | 63.4281 | 14 | 31.42 | 163.42 |  | GENTPJ | PSS2B | IEEEG3_GE | ESST1A_GE | Closed | 125 | -26.0827 | HY | 163.42 |  | YES | 0.006 | 0.39 | 3.25 | 5.3111 | 0.184 | 0.48 | 2.6087 | 13.8 |  | LOW_GRAN_13.8_G01 | HY (Hydro) | 2
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44232 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 155 | -58.7522 | 63.1104 | 14 | -155 |  |  | GENTPJ | PSS2A | H6E | ESST4B | Closed | 138.5 | -26.0827 | HY | 163.42 |  | YES | 0.006 | 0.39 | 2.961 | 4.8389 | 0.028 | 0.2 | 7.1429 | 13.8 |  | LOW_GRAN_13.8_G04 | HY (Hydro) | 4
40 | NORTHWEST | 606 | EDP Renewables | Bonneville Power Admin | 44279 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 102 | -43.504 | -43.504 | 14 | -102 |  |  | WT2G |  | WT2T | WT2E | Closed | 102 | 9.0054 | W2 | 111.34 |  | YES | 0.017 | 0.34 | 0 |  |  |  | NAN | 0.6 |  | KITASVLY_0.6_G1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44508 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 5 | 0 | 0 | 13 | -5 | [6 empty] | Closed | 4 | 0 | HY | 5 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44574 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 47.25 | -22.88 | 22.88 | 13 | -47.25 | [6 empty] | Closed | 37.8 | 5.8031 | PV | 52.5 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44577 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44586 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 40 | -19.37 | 19.37 | 13 | -40 | [6 empty] | Closed | 8 | 11.1721 | W4 | 44.448 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44623 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model | Missing PS |  |  | 0 | 36.94 | -33.57 | 33.57 | 13 | -36.94 | [6 empty] | Closed | 7.388 | 14.9712 | ST | 43.42 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | ST (Steam Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44624 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44625 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 8 | 0 | 0 | 13 | -8 | [6 empty] | Closed | 6.4 | 0 | PV | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44625 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44626 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44627 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 20.8 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44628 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 2 | 0 | 0 | 13 | -2 | [6 empty] | Closed | 1.6 | 0 | PV | 2 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44628 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 8 | 0 | 0 | 13 | -8 | [6 empty] | Closed | 6.4 | 0 | PV | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44628 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 3
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44629 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44630 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44630 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44630 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 3
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44631 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44632 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44654 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 55.398 | -29.988 | 29.988 | 13 | -55.398 | [6 empty] | Closed | 11.0796 | -29.988 | WT | 63.168 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44834 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 6.25 | 4.69 | 4.69 | 13 | -6.25 | [6 empty] | Closed | 1.25 | 0.938 | ST | 7.81 | PF<0.8 | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.2 |  |  | ST (Steam Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44836 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4 | 9 | 13 | -15 |  |  | GENTPJ | PSS2B |  | EXST4B | Closed | 12 | 0.14356 | HY | 16.67 |  | NO | 0 | 0.25 | 2.61 | 0.43509 | 0.35 | 1.27 | 3.6286 | 6.9 |  | TOKETEE_6.9_G01 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44837 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4 | 7 | 13 | -15 |  |  | GENTPJ |  |  | ESDC3A | Closed | 12 | 0.1403 | HY | 16.67 |  | NO | 0 | 0.31 | 2.61 | 0.43509 | 0.36 | 1.4 | 3.8889 | 6.9 |  | TOKETEE_6.9_G02 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44838 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4 | 4 | 13 | -15 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 12 | 0.14787 | HY | 16.67 |  | NO | 0 | 0.31 | 2.53 | 0.42175 | 0.25 | 1.07 | 4.28 | 6.9 |  | TOKETEE_6.9_G03 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44839 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 13.41 | -5.59 | 6.49 | 13 | -13.41 | [6 empty] | Closed | 2.682 | -4.7921 | ST | 14.9 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  | RFP_13.8_RFP | ST (Steam Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44881 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 41 | -8.3 | -8.3 | 13 | 4.51 | 45.51 |  | WT1G | WT1P_B | WT1T |  | Closed | 8.2 | -1.66 | W1 | 45.14 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | COL_HILL_34.5_G01 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44971 | N | N | [10 empty] | Unreas Sat | [8 empty] | 0 | 5 | -2 | 2.4 | 13 | 0.55 | 5.55 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 4 | -0.22583 | HY | 5.55 |  | NO | 0 | 0.18 | 3 | 0.1665 | 0 | 0 | NAN | 69 |  | LKSISKIU_69_G01 | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45022 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1 | 0 | 0 | 13 | -1 |  |  | GENTPF |  |  |  | Closed | 0.8 | 0 | HY | 1 |  | NO | 0 | 0.18 | 3 | 0.03 | 0 | 0 | NAN | 4.2 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45026 | N | N | [10 empty] | Unreas Sat | [8 empty] | 0 | 24 | -4 | 8 | 13 | 1 | 25 |  | GENTPJ |  | GGOV1 | EXST4B | Closed | 19.2 | -0.27801 | HY | 25 |  | NO | 0 | 0.18 | 3 | 0.75 | 0.2 | 0.8 | 4 | 13.8 |  | BIOMASS_13.8_GN1 | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45045 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 9.9 | 0 | 0 | 13 | -9.9 | [6 empty] | Closed | 7.92 | 0 | PV | 9.9 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45056 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 5 | 0 | 0 | 13 | -5 | [6 empty] | Closed | 4 | 0 | PV | 5 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45086 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 4.8 | 0 | 0 | 13 | -4.8 | [6 empty] | Closed | 3.84 | 0 | PV | 4.8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45122 | N | N | [10 empty] | Unreas Sat | [8 empty] | 0 | 3 | 0 | 0 | 13 | -3 |  |  | GENTPF |  |  |  | Closed | 2.4 | 0 | HY | 3 |  | NO | 0 | 0.18 | 3 | 0.09 | 0 | 0 | NAN | 69 |  |  | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45138 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 3.3 | 0 | 0 | 13 | -3.3 | [6 empty] | Closed | 2.64 | 0 | PV | 3.3 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45168 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 3 | 0 | 0 | 13 | -3 |  |  | GENTPF |  |  |  | Closed | 2.4 | 0 | HY | 3.1 |  | NO | 0 | 0.18 | 3 | 0.093 | 0 | 0 | NAN | 2.4 |  | EAGLEPT_2.4_G1 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45172 | 1 | 1 | [10 empty] | Unreas Sat |  | Gen on HV | [6 empty] | 0 | 1 | 0 | 0 | 13 | -1 |  |  | GENTPF |  |  |  | Closed | 0.8 | 0 | HY | 13.7 |  | NO | 0 | 0.18 | 3 | 0.411 | 0 | 0 | NAN | 69 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45176 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2.2 | 0 | 0 | 13 | 1e-08 | 2.2 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 1.76 | 0 | HY | 2.2 |  | NO | 0 | 0.18 | 3 | 0.066 | 0 | 0 | NAN | 2.3 |  | FALLCRK_2.4_GEN | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45178 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.8 | 0 | 0 | 13 | -1.8 |  |  | GENTPF |  |  |  | Closed | 1.44 | 0 | HY | 5.1 |  | NO | 0 | 0.18 | 3 | 0.153 | 0 | 0 | NAN | 69 |  | FARMIRR_69_TOT_GEN | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45180 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 11 | -6.8 | 6.8 | 13 | -11 |  |  | GENTPJ |  |  | ESDC3A | Closed | 8.8 | 6.8 | HY | 12.94 |  | NO | 0 | 0.18 | 2.26 | 0.29244 | 0.12 | 0.34 | 2.8333 | 6.9 |  | FISH_CRK_6.9_G01 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45256 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 29 | -9.5 | 9.5 | 13 | -29 |  |  | GENTPJ | PSS2B |  | ESDC4B | Closed | 23.2 | -1.0535 | HY | 34.5 |  | NO | 0 | 0.31 | 3.08 | 1.0626 | 0.2 | 1.08 | 5.4 | 12 |  | LEMOLO_1_12_G01 | HY (Hydro) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45290 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 33 | -7.9 | 12.6 | 13 | 5.5 | 38.5 |  | GENTPJ | PSS2A | HYGOV | ESST4B | Closed | 26.4 | 0.03717 | HY | 45 |  | NO | 0 | 0.301 | 2.4 | 1.08 | 0.26 | 1 | 3.8462 | 11.5 |  | LEMOLO_2_11.5_G01 | HY (Hydro) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45338 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 8 | 0 | 0 | 13 | -8 | [6 empty] | Closed | 6.4 | 0 | PV | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45351 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 73.3 | -17 | 26 | 13 | -13.3 | 60 |  | GENTPJ | PSS2A | IEEEG3_GE | ESST1A_GE | Closed | 58.64 | 12.2803 | HY | 60 |  | NO | 0 | 0.18 | 3 | 1.8 | 0.219 | 0.941 | 4.2968 | 13.2 |  | YALE_13.8_GEN1 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45351 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 73.3 | -17 | 26 | 13 | -13.3 | 60 |  | GENTPJ | PSS2A | IEEEG3_GE | ESST1A_GE | Open | 0 | 0 | HY | 60 |  | NO | 0 | 0.18 | 3 | 1.8 | 0.219 | 0.941 | 4.2968 | 13.2 |  | YALE_13.8_GEN2 | HY (Hydro) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45368 | N | N | [10 empty] | Unreas Sat | [8 empty] | 0 | 5 | 0 | 0 | 13 | -5 |  |  | GENTPF |  |  |  | Closed | 4 | 0 | HY | 5 |  | NO | 0 | 0.18 | 3 | 0.15 | 0 | 0 | NAN | 69 |  |  | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45439 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 20.3 | -3.6 | 3.6 | 13 | -20.3 |  |  | GENTPJ |  |  | EXST4B | Closed | 16.24 | 1.1423 | HY | 20.3 |  | NO | 0 | 0.18 | 3 | 0.609 | 0.2 | 1 | 5 | 6.9 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45445 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 0.8 | -0.6 | 0.6 | 13 | 0.2 | 1 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 0.64 | 0.48 | HY | 1 | PF<-0.85 | NO | 0 | 0.18 | 3 | 0.03 | 0.2 | 1 | 5 | 2.3 |  | PROSPECT_2.3_G04 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45453 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -6 | 12 | 13 | 0.7 | 4.7 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 3.2 | -1.713 | HY | 4.7 | PF<0.8 | NO | 0 | 0.18 | 3 | 0.141 | 0.2 | 1 | 5 | 2.3 |  | PROSPECT_2.3_G01 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45485 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.2 | -1 | 2 | 13 | 0.47 | 4.67 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 3.36 | 0.089219 | HY | 4.67 |  | NO | 0 | 0.18 | 3 | 0.1401 | 0 | 0 | NAN | 4.2 |  | SLATECRK_4.16_GEN | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45502 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 0.83 | 0 | 0 | 13 | -0.83 | [6 empty] | Closed | 0.664 | 0 | PV | 0.83 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45502 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 2.9 | 0 | 0 | 13 | -2.9 | [6 empty] | Closed | 2.32 | 0 | PV | 2.9 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 2 |  | PSS Exempt
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 45542 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 15.1 | 41 | -30 | 28 | 14 | -0.05 | 40.95 |  | GENQEC | PSS2C | HYGOV |  | Open | 0 | 0 | HY | 45.5 | PF<-0.85 | YES | 0 | 0.18 | 3 | 1.365 |  |  | NAN | 13.8 |  | SWIFT_2_13.8_G02 | HY (Hydro) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45545 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 80 | 31.3 | 38 | 14 | -80 |  |  | GENTPJ | PSS2A |  | ESST1A_GE | Closed | 62 | 31.3 | HY | 86.9 |  | NO | 0 | 0.153 | 3.8 | 3.3022 | 0.16 | 0.54 | 3.375 | 13.8 |  | SWIFT_1_13.8_G02 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45546 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 80 | 33.4 | 38 | 14 | -80 |  |  | GENTPJ | PSS2A |  | ESST1A_GE | Closed | 62 | 33.4 | HY | 86.9 |  | NO | 0 | 0.093 | 3.8 | 3.3022 | 0.16 | 0.54 | 3.375 | 13.8 |  | SWIFT_1_13.8_G03 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45549 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -3 | 5 | 13 | 2 | 9 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 5.6 | 2.2602 | HY | 9 |  | NO | 0 | 0.18 | 3 | 0.27 | 0.2 | 1 | 5 | 6.6 |  | PROSPECT_6.6_G03 | HY (Hydro) | 1
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46055 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 6.7 | 0 | 0 | 35 | -6.7 | [6 empty] | Closed | 4 | 0 | HY | 6.7 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | PEC_115_G01 | HY (Hydro) | 1
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46071 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 9.4 | 0 | 0 | 35 | -9.4 | [6 empty] | Closed | 7 | 0 | HY | 9.4 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | QUIN_CH_115_G01 | HY (Hydro) | 1
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46268 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 31.4 | -6 | 25 | 14 | -31.4 |  |  | GENROU |  |  | ESST2A | Closed | 25.3 | 3.9531 | ST | 58.871 | PF<0.8 | NO | 0 | 0.2 | 1.71 | 1.0067 | 0.092 | 0.284 | 3.087 | 13.8 |  | WEYRHSR3_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46297 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 19.8 | 9 | 15 | 14 | -0.022 | 19.778 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 16 | 9 | ST | 19.778 | PF<0.8 | NO | 0 | 1e-05 | 3 | 0.59334 | 0.15 | 0.45 | 3 | 13.8 |  | ENID_RD_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46304 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.5 | 1.8 | 1.8 | 14 | -6.5 |  |  | GENTPF |  |  |  | Open | 0 | 0 | HY | 13.8 |  | NO | 0 | 1e-05 | 3 | 0.414 | 0 | 0 | NAN | 12 |  | LEABURGS_12_G02 | HY (Hydro) | 1
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46306 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 9.7 | -4 | 5.5 | 14 | -9.7 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 5 | -4 | HY | 9.412 |  | NO | 0 | 1e-05 | 1.97 | 0.18542 | 0.0059 | 0.1302 | 22.0678 | 11.5 |  | WALTVILE_66_G01 | HY (Hydro) | 1
40 | NORTHWEST | 647 | WestRock CP, LLC | Bonneville Power Admin | 46606 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 64 | -28 | 40 | 14 | -64 |  |  | GENROU | PSS2B |  | ESAC8B_GE | Open | 0 | 0 | ST | 75.5 |  | YES | 0 | 1.89 | 6.9 | 5.2095 | 0.0565 | 1.1551 | 20.4442 | 13.8 |  | TACOBMAS_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 38 | Tacoma Power | Tacoma Power [Bus] | 46617 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 2 | 0 | 0 | 38 | -2 |  |  | GENTPJ |  |  |  | Closed | 2 | 0 | HY | 2.5 |  | YES | 0 | 0.16 | 0.7583 | 0.018957 | 0.1261 | 0.4167 | 3.3045 | 13.8 |  | NFORK_13.8_G34 | HY (Hydro) | 1
40 | NORTHWEST | 38 | Tacoma Power | Tacoma Power [Bus] | 46617 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 2 | 0 | 0 | 38 | -2 |  |  | GENTPJ |  |  |  | Closed | 2 | 0 | HY | 2.5 |  | YES | 0 | 0.16 | 0.7583 | 0.018957 | 0.1261 | 0.4167 | 3.3045 | 13.8 |  | NFORK_13.8_G35 | HY (Hydro) | 2
40 | NORTHWEST | 929 | Columbia Basin Hydro | Avista | 46619 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 26.8 | -5.7502 | 8.5004 | 9999 | 0.6 | 27.4 |  | GENTPJ | PSS2A | HYG3 | ESST4B | Closed | 25.31 | 8.5004 | HY | 27.4 |  | YES | 0 | 0.2 | 1.7 | 0.4658 | 0.119 | 0.531 | 4.4622 | 6.9 |  | HEADWORK_13.8_G160 | HY (Hydro) | 1
40 | NORTHWEST | 929 | Columbia Basin Hydro | Avista | 46653 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 47 | -12 | 8 | 9999 | 1.67 | 48.67 |  | GENTPJ | PSS2A | HYG3 | ESST4B | Closed | 47 | 3.109 | HY | 48.7 |  | YES | 0 | 0.2 | 3.54 | 1.724 | 0.169 | 0.518 | 3.0651 | 13.8 |  | SUMMERFL_13.8_G161 | HY (Hydro) | 1
40 | NORTHWEST | 929 | Columbia Basin Hydro | Avista | 46655 | 1 | 1 |  | Missing BA | [17 empty] | 0 | 47 | -12 | 8 | 9999 | 1.67 | 48.67 |  | GENTPJ | PSS2A | HYG3 | ESST4B | Closed | 47 | 3.109 | HY | 48.7 |  | YES | 0 | 0.2 | 3.54 | 1.724 | 0.169 | 0.518 | 3.0651 | 13.8 |  | SUMMERFL_13.8_G162 | HY (Hydro) | 1
40 | NORTHWEST | 44 | Pend Oreille PUD | Bonneville Power Admin | 47010 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 22.5 | -12.5 | 14.945 | 29 | 2.5 | 25 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 12.9 | -6.7405 | HY | 25 |  | YES | 0 | 0.35 | 1.57 | 0.3925 | 0.22 | 0.52 | 2.3636 | 13.8 |  | BOX_CANY_13.8_G01 | HY (Hydro) | 1
40 | NORTHWEST | 44 | Pend Oreille PUD | Bonneville Power Admin | 47012 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 22.5 | -12.5 | 14.945 | 29 | 2.5 | 25 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 12.9 | -6.664 | HY | 25 |  | YES | 0 | 0.35 | 1.57 | 0.3925 | 0.22 | 0.52 | 2.3636 | 13.8 |  | BOX_CANY_13.8_G02 | HY (Hydro) | 2
40 | NORTHWEST | 51 | Emerald PUD | Bonneville Power Admin | 47023 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 3 | -0.5 | -0.5 | 14 | -3 |  |  | GENTPF |  |  |  | Closed | 2.5 | 0 | IC | 5 |  | NO | 0 | 0.2 | 3 | 0.15 | 0 | 0 | NAN | 115 |  |  | IC (Internal Combustion) | 1
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47104 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8183 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G01 | HY (Hydro) | 1
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47104 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -60 | 51.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Open | 0 | 0 | HY | 81.5 | PF<-0.85 | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G02 | HY (Hydro) | 2
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47105 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8184 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G03 | HY (Hydro) | 3
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47105 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8184 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G04 | HY (Hydro) | 4
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47106 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Open | 0 | 0 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G05 | HY (Hydro) | 5
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47106 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8183 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G06 | HY (Hydro) | 6
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47107 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8184 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G07 | HY (Hydro) | 7
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47107 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8184 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G08 | HY (Hydro) | 8
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47108 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8184 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G10 | HY (Hydro) | 9
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47108 | A | A | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 4.8184 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G09 | HY (Hydro) | A
40 | NORTHWEST | 39 | Energy Northwest | Bonneville Power Admin | 47271 | 2 | 2 | [8 empty] | RX Ratio | [6 empty] | Missing Model |  |  |  | 0 | 3.2 | -0.3 | 0.3 | 14 | -3.2 | [6 empty] | Closed | 3 | 0 | PV | 3.2 |  | NO | 0.8 | 1e-05 | 0 |  |  |  | NAN | 115 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 428 | Georgia Pacific | Bonneville Power Admin | 47290 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 42 | -26.5 | 33 | 14 | -42 |  |  | GENROU | PSS2B |  | ESAC8B_GE | Open | 0 | 0 | ST | 42 | PF<0.8 | NO | 0 | 0.2 | 3 | 1.26 | 0.072 | 0.337 | 4.6806 | 13.8 |  | WAUNA_13.8_G02 | ST (Steam Turbine) | 1
40 | NORTHWEST | 412 | Klickitat County PUD | Bonneville Power Admin | 47294 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 10.5 | -3.5 | 3.5 | 14 | -10.5 | [6 empty] | Open | 0 | 0 | CC | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | CC (Combined Cycle Generic) | 1
40 | NORTHWEST | 412 | Klickitat County PUD | Bonneville Power Admin | 47296 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 20 | -6.6 | 6.6 | 14 | -20 | [6 empty] | Open | 0 | 0 | JE | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | JE (Jet Engine) | 2
40 | NORTHWEST | 412 | Klickitat County PUD | Bonneville Power Admin | 47296 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 6 | -2 | 2 | 14 | -6 | [6 empty] | Open | 0 | 0 | CC | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | CC (Combined Cycle Generic) | 3
40 | NORTHWEST | 13 | PacifiCorp - West | Bonneville Power Admin | 47359 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1 | 0 | 0 | 14 | -1 |  |  | GENTPF |  |  |  | Closed | 1 | 0 | HY | 1 |  | NO | 0 | 0.18 | 3 | 0.03 | 0 | 0 | NAN | 230 |  | LION_MTN_230_G01 | HY (Hydro) | 1
40 | NORTHWEST | 652 | Southern California Power Auth | Bonneville Power Admin | 47384 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 50 | 0 | 0 | 14 | -50 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 30 | 0 | W3 | 51.25 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.58 |  | LINDN_0.6_G1 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47397 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 200.8 | -66 | 66 | 14 | -200.8 |  |  | REGC_A |  |  | REEC_A | Closed | 100 | -7.4647 | W3 | 124.332 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 47446 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | 0 | 32 | -1.5 | 18.2 | 14 | -32 |  |  | GENTPF |  |  | EXST4B | Closed | 18 | 3.1334 | ST | 14 |  | NO | 0 | 1 | 3 | 0.42 | 0 | 0 | NAN | 13.8 |  |  | ST (Steam Turbine) | 7
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 47448 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 25.6 | 0 | 11.4 | 14 | -25.6 |  |  | GENTPF |  |  | EXST4B | Closed | 12 | 6.4216 | ST | 14 |  | NO | 0 | 1 | 3 | 0.42 | 0 | 0 | NAN | 13.8 |  |  | ST (Steam Turbine) | 6
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47452 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 132.5 | -51.5 | 62 | 14 | -132.5 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 132.5 | 16.9696 | W4 | 298.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSNC_0.7_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47455 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 132.5 | -51.5 | 62 | 14 | -132.5 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 39.75 | 1.28 | W4 | 298.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSNC_0.7_Z2 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47458 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -38.5 | 42 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | 8.4031 | W4 | 324.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSCC_0.7_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47461 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -38.5 | 42 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | 8.4031 | W4 | 298.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSCC_0.7_Z2 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47464 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -66 | 76 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | 41.4415 | W4 | 324.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSSC_0.7_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47469 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -66 | 79 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | 0.87466 | W4 | 324.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSSC_0.7_Z2 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47489 | Z1 | Z1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5.9 | 98.9 | -30.2 | 42.8 | 14 | -98.9 |  |  | REGC_A |  |  |  | Closed | 30.15 | -30.2 | W3 | 117.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.72 |  |  | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 487 | Cannon Power | Bonneville Power Admin | 47495 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 115 | -50 | 25 | 14 | -115 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 105 | 12.747 | W4 | 127.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | DOOLEY_0.69_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 487 | Cannon Power | Bonneville Power Admin | 47498 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 117.3 | -51 | 25.5 | 14 | -117.3 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 25 | 12.7468 | W4 | 130.36 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 448 | Rathdrum Power, LLC | Bonneville Power Admin | 47568 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 122 | 211 | -111.2 | 111.2 | 29 | -39 | 172 |  | GENROU | PSS2A | GGOV1 | ESST4B | Closed | 165 | 2.8606 | CT | 211 |  | NO | 0.003 | 0.18 | 6.1 | 12.871 | 0.052 | 0.092 | 1.7692 | 18 |  | RATH_PWR_18_GT | CT (Combined Cycle Combustion Turbine Part) | 1
40 | NORTHWEST | 448 | Rathdrum Power, LLC | Bonneville Power Admin | 47569 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 70 | 143 | -75.6 | 75.6 | 29 | -143 |  |  | GENROU | PSS2A |  | REXS | Closed | 65 | 2.8606 | CA | 143.6 |  | NO | 0.003 | 0.18 | 4.35 | 6.2466 | 0.09 | 0.45 | 5 | 13.8 |  | RATH_PWR_13.8_ST | CA (Combined Cycle Steam Part) | 1
40 | NORTHWEST | 458 | Frederickson Power, LLP | Bonneville Power Admin | 47577 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 192 | -50 | 110 | 14 | -25.7 | 166.3 |  | GENROU | PSS2A | GGOV1 | EXST4B | Closed | 150 | -2.1098 | GT | 192 |  | YES | 0.002 | 0.202 | 5.92 | 11.3664 | 0.053 | 0.445 | 8.3962 | 18 |  | FREDCOGN_18_GT | GT (Gas Turbine) | 1
40 | NORTHWEST | 451 | NextEra Energy | Bonneville Power Admin | 47608 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 50 | -25 | 25 | 14 | -50 | [6 empty] | Closed | 45 | 7.547 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 452 | Calpine Corporation | Bonneville Power Admin | 47641 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 255 | -77.75 | 172.75 | 14 | -255 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 189 | 172.75 | CC | 311 |  | YES | 0.001 | 0.2 | 5.395 | 16.7784 | 0.158 | 0.838 | 5.3038 | 18 |  | CALPINE_16_ST3 | CC (Combined Cycle Generic) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47675 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 207 | -58.1 | 124.1 | 30 | 6.68e-06 | 207 |  | GENQEC | PSS2B | GGOV3 | ESST4B | Closed | 138 | -15.5036 | GT | 219 |  | NO | 0 | 1e-05 | 5.08 | 11.1252 |  |  | NAN | 18 |  | MINTFARM_18_CTG | GT (Gas Turbine) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47676 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 134 | -39.7333 | 98.6667 | 30 | -134 |  |  | GENQEC | PSS2C |  | ESST4B | Closed | 107 | -9.5267 | CC | 157.6 |  | YES | 0 | 1e-05 | 6.75 | 10.638 |  |  | NAN | 13.8 |  | MINTFARM_13.2_STG | CC (Combined Cycle Generic) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47687 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 207 | -42.1 | 125.8 | 30 | -22 | 185 |  | GENQEC | PSS2B | GGOV1 | ESST4B | Closed | 167.6 | -42.1 | GT | 200 |  | NO | 0.002 | 0.202 | 5.57 | 11.14 |  |  | NAN | 18 |  | GLDNDPSE_18_CT | GT (Gas Turbine) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47688 | L | L | [6 empty] | Limit Power Fact | [12 empty] | 0 | 110.6 | -55.9 | 90.3 | 30 | -110.6 |  |  | GENQEC | PSS2A |  | ST4C | Closed | 78.9 | -53.6739 | CC | 134.5 | PF<0.8 | NO | 0.002 | 0.2 | 5.5 | 7.3975 |  |  | NAN | 13.8 |  | GLDNDPSE_18_ST | CC (Combined Cycle Generic) | L
40 | NORTHWEST | 460 | TransAlta-Centralia Gen, LLC | Bonneville Power Admin | 47744 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 817.8 | -150 | 150 | 14 | -817.8 |  |  | GENROU | PSS2B |  | ESAC7B | Closed | 710 | 150 | CA | 870 |  | YES | 0.002 | 0.325 | 3.25 | 28.275 | 0.134 | 0.54 | 4.0299 | 20 |  | CENT_STM_20_G02 | CA (Combined Cycle Steam Part) | 2
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47799 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 50 | -16.4 | 16.4 | 14 | -50 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 30 | 2.8162 | W3 | 50 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BIG_HORN_0.6_G03 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 646 | Eurus Energy America Corp | Bonneville Power Admin | 47805 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 63 | -17.6175 | -17.6175 | 14 | 4.8e-07 | 63 |  | WT1G |  | WT1T |  | Closed | 18.9 | -30.5 | W1 | 69.3 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | COMB_H_2_0.6_Z1 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47806 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 90.3 | 0 | 0 | 14 | -90.3 |  |  | WT2G |  | WT2T | WT2E | Closed | 84 | 0 | W2 | 97.86 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | LEANJUN2_0.6_PG1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47810 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 111 | -39.4 | 39.4 | 14 | -111 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 32.7 | -18.3153 | W3 | 123.58 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | LEANJUN2_0.6_PG2 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47872 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 102 | -33.5 | 33.5 | 14 | -102 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 100 | 0.607 | W3 | 113.56 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BIG_HORN_0.6_G01 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47873 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 97.5 | -32 | 32 | 14 | -97.5 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 97.5 | 2.8161 | W3 | 108.55 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BIG_HORN_0.6_G02 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47879 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 82.8 | -4.3111 | -4.3111 | 14 | -82.8 |  |  | WT2G | WT1P_B | WT2T | WT2E | Closed | 40 | 0 | W2 | 91 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | HOPKRIDG_0.6_G02 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 992 | White Creek Wind I, LLC | Bonneville Power Admin | 47907 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 92 | -53.8 | 53.8 | 14 | -92 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 92 | 6.7379 | W4 | 140.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | WHITECRK_0.6_Z2 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1425 | Harvest Wind LLC | Bonneville Power Admin | 47907 | Z2 | Z2 | [17 empty] | Missing Sub R/X |  | 0 | 34.5 | -20.2 | 20.2 | 14 | -34.5 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 10.5 | 6.7379 | W4 | 140.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | Z2
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47924 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 132 | -39.4 | 39.4 | 14 | -132 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 120 | -29.2908 | W3 | 146.7 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  | KLNDSCHL_0.6_Z3 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47925 | 1 | 1 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 9 | -0.2633 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47925 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | -10 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 9 | -0.2633 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 487 | Cannon Power | Bonneville Power Admin | 47937 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 29.9 | -13 | 6.5 | 14 | -29.9 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 27.9 | -12.2711 | W4 | 33.23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | ENERGIZE_0.7_G1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 337 | Turlock Irrigation District | Bonneville Power Admin | 47939 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 96.6 | -42 | 21 | 14 | -96.6 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 22 | -0.10372 | W4 | 107.35 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TUOLUMNE_0.69_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 337 | Turlock Irrigation District | Bonneville Power Admin | 47940 | Z2 | Z2 | [17 empty] | Missing Sub R/X |  | 0 | 40 | 0 | 0 | 14 | -40 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 6.6 | 0 | W3 | 40 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | TUOLUMNE | W3 (Wind Turbine, Type 3) | Z2
40 | NORTHWEST | 1458 | Energy Northwest Packwood | Bonneville Power Admin | 47948 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 32.5 | 0 | 0 | 14 | -0.5 | 32 |  | WT1G |  | WT1T |  | Closed | 9.57 | 0 | W1 | 35.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | NINECNYN_0.69_Z1 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1458 | Energy Northwest Packwood | Bonneville Power Admin | 47952 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 31.2 | 0 | 0 | 14 | -0.2 | 31 |  | WT1G |  | WT1T |  | Closed | 9.3 | 0 | W1 | 34.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | NINECNYN_0.69_Z2 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47974 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 100.8 | -26.6 | -26.6 | 14 | -100.8 |  |  | WT2G |  | WT2T | WT2E | Closed | 45 | 0 | W2 | 109.25 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | HAYCANYN_0.6_Z1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47975 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 98.7 | -41.275 | -41.275 | 14 | -98.7 |  |  | WT2G |  | WT2T | WT2E | Closed | 95 | -22.5394 | W2 | 106.972 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | STAR_PT_0.6_Z1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1425 | Harvest Wind LLC | Bonneville Power Admin | 47981 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 64.4 | -35.8 | 35.8 | 14 | -64.4 |  |  | REGC_A |  |  | REEC_A | Closed | 19.32 | -13.0483 | W4 | 72 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | HARVESTW_0.6_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 472 | Condon Wind Power, LLC | Bonneville Power Admin | 47989 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 25 | 0 | 0 | 14 | 25 | 50 |  | WT1G |  | WT1T |  | Closed | 15 | 0 | W1 | 55 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | CONDWIND_0.6_G01 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 491 | Invenergy LLC | Bonneville Power Admin | 47995 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 72 | -25.6 | 25.6 | 14 | -72 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 72 | 21.4941 | W3 | 82.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.58 |  | HORN_BTE_0.6_G1 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48166 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | -24.7 | -24.6 | 6.5 | 6.5 | 29 | 24.6 |  |  | GENROU |  |  | SEXS_GE | Closed | -24.6 | 6.5 | MP | 24.608 | PF<0.8 | NO | 0 | 0.3 | 5.01 | 1.2329 | 0.05 | 0.3 | 6 | 13.8 |  | Inland Empire Paper UN1 | MP (Motor/Pump) | 1
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48168 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | -24.7 | -24.6 | 6.5 | 6.5 | 29 | 24.6 |  |  | GENROU |  |  | SEXS_GE | Closed | -24.6 | 6.5 | MP | 24.608 | PF<0.8 | NO | 0 | 0.3 | 5.01 | 1.2329 | 0.05 | 0.3 | 6 | 13.8 |  | Inland Empire Paper UN2 | MP (Motor/Pump) | 1
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48189 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 8.8 | -5.5 | 6 | 29 | 2 | 10.8 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 7 | -0.26628 | HY | 12 | PF<-0.85 | NO | 0 | 0.168 | 1.88 | 0.2256 | 0.15 | 0.32 | 2.1333 | 4 |  | LITTFALL_4_GEN2 | HY (Hydro) | 2
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48191 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 8.2 | -0.5 | 2.3 | 29 | -8.2 |  |  | GENTPJ |  |  | ESST4B | Closed | 8 | -0.5 | HY | 8.888 |  | NO | 0 | 0.166 | 2.1 | 0.18665 | 0.2 | 0.454 | 2.27 | 4 |  | LITTFALL_4_GEN3 | HY (Hydro) | 3
40 | NORTHWEST | 295 | Hydro Technology Systems | Avista | 48227 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 1.3 | 0 | 0 | 29 | -1.3 | [6 empty] | Closed | 1.2 | 0 | HY | 1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 11 |  | Meyers Falls UN1 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 295 | Hydro Technology Systems | Avista | 48227 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 0.3 | 0 | 0 | 29 | -0.3 | [6 empty] | Closed | 0.2 | 0 | HY | 0.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 11 |  | Meyers Falls UN2 | HY (Hydro) | 2 | Netting Exempt
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48241 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 1 | 15.6 | 0 | 4.8 | 29 | -15.6 | [6 empty] | Closed | 5 | 0 | HY | 15.6 |  | NO | 0 | 0.268 | 0 |  |  |  | NAN | 13.8 |  | POST STR 13.8 G01 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 294 | Plummer Forest Products | Avista | 48321 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 5 | 0 | 3.7 | 29 | -5 | [6 empty] | Closed | 4.5 | 0.031314 | ST | 6.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | PLUMMER_4.16_G01 | ST (Steam Turbine) | 1 | Netting Exempt
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48331 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 1.8 | 2.8 | 0 | 0 | 29 | -2.8 | [6 empty] | Closed | 2.25 | 0 | HY | 2.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.4 |  | POST_FLS_2.4_G01 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48335 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 1 | 10.2 | 0 | 6 | 29 | -10.2 | [6 empty] | Closed | 3 | 0 | HY | 11.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | POST STR 4.16 G02 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 291 | City of Spokane | Avista | 48433 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 2 | 0 | 1.5 | 29 | -2 | [6 empty] | Closed | 1.5 | 0 | HY | 2.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.4 |  | Upriver UN1 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 291 | City of Spokane | Avista | 48435 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 5.8 | -4.5 | 3.6 | 29 | -5.8 | [6 empty] | Closed | 5 | 0.090609 | HY | 6.5 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | Upriver UN4 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 293 | Potlatch Paper | Avista | 48482 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 33.3 | -10 | 25 | 29 | -4.3e-07 | 33.3 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 22 | 25 | ST | 41.6 | PF<0.8 | YES | 0 | 0.275 | 1.76 | 0.73216 | 0.1765 | 0.3333 | 1.8884 | 12 |  | CLEARWTR_12_G03 | ST (Steam Turbine) | 1
40 | NORTHWEST | 293 | Potlatch Paper | Avista | 48483 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 50 | -10 | 55 | 29 | 0 | 50 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 28 | 39.5469 | ST | 66.92 | PF<0.8 | YES | 0 | 0.197 | 1.362 | 0.91145 | 0.146 | 0.368 | 2.5205 | 12 |  | CLEARWTR_12_G04 | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50170 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 25 | -3 | 5 | 10 | 5 | 30 |  | GENTPJ |  | HYGOV | ESAC8B_GE | Closed | 22.205 | 3.2384 | HY | 30 |  | NO | 0.004 | 0.25 | 2.79 | 0.837 | 0.2636 | 0.7692 | 2.9181 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50293 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 6.67 | -3.23 | 3.23 | 10 | -6.67 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 6.191 | -1.2681 | HY | 12 |  | NO | 0 | 0.14 | 0.81 | 0.0972 | 0.11 | 0.6 | 5.4545 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50293 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 6.67 | -3.23 | 3.23 | 10 | -6.67 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 6.191 | -1.2681 | HY | 7.41 |  | NO | 0 | 0.14 | 0.81 | 0.060021 | 0.11 | 0.6 | 5.4545 | 4.16 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 50401 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 26 | -12.6 | 12.6 | 10 | -26 |  |  | GENROU |  |  | ESAC6A | Open | 0 | 0 | GT | 28.89 |  | NO | 0 | 0.15 | 2.5 | 0.72225 | 0.2 | 0.5 | 2.5 | 12.6 |  |  | GT (Gas Turbine) | 1
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50437 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 60 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.912 | 19.3625 | HY | 132 |  | NO | 0 | 0.27 | 3.2 | 4.224 | 0.21 | 0.45 | 2.1429 | 13.2 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50438 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 64 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.912 | 19.3624 | HY | 132 |  | NO | 0 | 0.27 | 4.74 | 6.2568 | 0.2 | 0.39 | 1.95 | 13.2 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50442 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 64 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.912 | 19.3625 | HY | 132 |  | NO | 0 | 0.28 | 5.25 | 6.93 | 0.14 | 0.24 | 1.7143 | 13.2 |  |  | HY (Hydro) | 6
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50443 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 60 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.912 | 19.3624 | HY | 132 |  | NO | 0 | 0.27 | 3.2 | 4.224 | 0.19 | 0.42 | 2.2105 | 13.2 |  |  | HY (Hydro) | 7
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 50845 | B | B | [10 empty] | Unreas Sat | [8 empty] | 0 | 30.544 | -10 | 14 | 10 | 1.456 | 32 |  | GENTPJ | PSS2A | GGOV1 | ESST1A_GE | Open | 0 | 0 | CC | 32 |  | NO | 0 | 0.22 | 2.24 | 0.7168 | 0.08 | 0.18 | 2.25 | 13.8 |  |  | CC (Combined Cycle Generic) | B
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50922 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 29 | -18.75 | 18.75 | 10 | 2.2 | 31.2 |  | GENTPJ | IEEEST | HYGOV | EXST1_GE | Closed | 25.925 | -0.28435 | HY | 31.2 | PF<-0.85 | NO | 0 | 0.215 | 3.221 | 1.005 | 0.175 | 0.542 | 3.0971 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50925 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 29 | -18.75 | 18.75 | 10 | 2.2 | 31.2 |  | GENTPJ | IEEEST | HYGOV | EXST1_GE | Closed | 25.925 | -0.28435 | HY | 31.2 | PF<-0.85 | NO | 0 | 0.215 | 3.221 | 1.005 | 0.175 | 0.542 | 3.0971 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50975 | 1 | 1 |  |  |  | Unapproved Gen Model | [7 empty] | Gen at 0.0 |  |  |  |  | Missing PS |  |  | 0 | 0 | -80 | 131 | 10 | 0 |  |  | GENTPJ |  |  | ESURRY | Closed | 0 | 5.916 | ST | 180 | PF<0.8 | NO | 0.003 | 0.2 | 1.55 | 2.79 | 0.126 | 0.54 | 4.2857 | 16.5 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50977 | 3 | 3 |  |  |  | Unapproved Gen Model | [7 empty] | Gen at 0.0 |  |  |  |  | Missing PS |  |  | 0 | 0 | -80 | 131 | 10 | 0 |  |  | GENTPJ |  |  | ESURRY | Closed | 0 | 5.8671 | ST | 180 | PF<0.8 | NO | 0.003 | 0.2 | 1.55 | 2.79 | 0.126 | 0.54 | 4.2857 | 16.5 |  |  | ST (Steam Turbine) | 3
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50978 | 4 | 4 |  |  |  | Unapproved Gen Model | [7 empty] | Gen at 0.0 |  |  |  |  | Missing PS |  |  | 0 | 0 | -80 | 131 | 10 | 0 |  |  | GENTPJ |  |  | ESURRY | Closed | 0 | 5.7707 | ST | 180 | PF<0.8 | NO | 0.003 | 0.2 | 1.55 | 2.79 | 0.126 | 0.54 | 4.2857 | 16.5 |  |  | ST (Steam Turbine) | 4
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51037 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15 | -11.25 | 11.25 | 10 | -15 |  |  | GENROU |  |  | EXST1_GE | Open | 0 | 0 | ST | 18.8 | PF<-0.85 | NO | 0 | 0.2 | 2.04 | 0.38352 | 0.065 | 0.305 | 4.6923 | 13.2 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51039 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 276.5 | -116 | 151 | 10 | -1.049e-05 | 276.5 |  | GENROU | PSS2A | GGOV1 | EXST1_GE | Closed | 224.979 | -20.7682 | CC | 290 |  | NO | 0 | 0.17 | 7.48 | 21.692 | 0.038 | 0.104 | 2.7368 | 21 |  |  | CC (Combined Cycle Generic) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51043 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 5.5 | -2.6 | 2.6 | 10 | -5.5 |  |  | GENTPJ |  |  | EXAC8B | Closed | 4.676 | -2.3024 | HY | 5 |  | NO | 0 | 0.24 | 2.2 | 0.11 | 0.2 | 0.4 | 2 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51054 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 3.501 | -1.695 | 1.695 | 10 | -3.501 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 3.441 | 0.42844 | HY | 4.3 |  | NO | 0 | 0.14 | 0.81 | 0.03483 | 0.11 | 0.6 | 5.4545 | 4.16 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51055 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 29.52 | -14.286 | 14.286 | 10 | -29.52 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 29.017 | 0.38291 | HY | 34.81 |  | NO | 0 | 0.23 | 1.72 | 0.59873 | 0.064 | 1.18 | 18.4375 | 25.2 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51104 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 21 | -12.6 | 12.6 | 10 | 3 | 24 |  | GENROU | PSS2A | IEEEG1_GE | EXST4B | Closed | 20.348 | 2.1935 | ST | 24 |  | NO | 0 | 0.234 | 2.87 | 0.6888 | 0.065 | 0.16 | 2.4615 | 12 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51135 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 25 | -12.1 | 12.1 | 10 | -25 |  |  | GENTPJ | PSS2A |  | EXST4B | Closed | 20.947 | 1.8278 | HY | 27.8 |  | NO | 0 | 0.25 | 1.44 | 0.40032 | 0.051 | 0.11 | 2.1569 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51135 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 25 | -12.1 | 12.1 | 10 | -25 |  |  | GENTPJ | PSS2A |  | EXST4B | Closed | 20.947 | 1.8278 | HY | 27.8 |  | NO | 0 | 0.25 | 1.44 | 0.40032 | 0.06 | 0.139 | 2.3167 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51140 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 24.75 | -14 | 14 | 10 | -24.75 |  |  | GENTPJ | PSS2A |  | EXAC1 | Closed | 23.66 | -0.076316 | ST | 26.5 |  | NO | 0 | 0.35 | 5 | 1.325 | 0.075 | 0.173 | 2.3067 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51212 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.32 | -7.2 | 7.2 | 10 | -10.32 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 8.854 | 0.37377 | HY | 12 | PF<-0.85 | NO | 0 | 0.274 | 1 | 0.12 | 0.1 | 0.4 | 4 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51212 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.32 | -7.2 | 7.2 | 10 | -10.32 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 8.854 | 0.37377 | HY | 12 | PF<-0.85 | NO | 0 | 0.274 | 1 | 0.12 | 0.1 | 0.4 | 4 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51212 | 3 | 3 | [9 empty] | Unreas H | [9 empty] | 0 | 3.399 | -1.98 | 1.98 | 10 | -3.399 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.916 | 0.37377 | HY | 3.3 |  | NO | 0 | 0.257 | 0.84 | 0.02772 | 0.1 | 0.4 | 4 | 13.8 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 1 | 1 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -6.73 | 8.41 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 10.242 | 1.7806 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 2 | 2 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -6.6 | 7.14 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 10.242 | 1.7806 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 3 | 3 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -4.36 | 6.2 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 10.242 | 1.7806 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 4 | 4 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -3.79 | 6.76 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 10.242 | 1.7806 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 4
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51246 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 5.4 | -0.26 | 0.26 | 10 | -5.4 | [6 empty] | Closed | 4.47 | 0 | HY | 5.95 |  | NO | 0 | 0.13 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 51273 | FD | FD | [11 empty] | Gen at 0.0 |  |  | Miss Turbine Type |  |  | Missing Sub R/X |  | 0 | 0 | -8 | 8 | 10 | 0 |  |  | GENROU |  |  |  | Closed | 0 | -1.9254 | UN | 8 | PF<0.8 | NO | 0 | 1e-05 | 2.4 | 0.192 | 0.05 | 0.3 | 6 | 25.2 |  |  | UN (Unknown) | FD
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51368 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 12.9 | -4.67 | 4.63 | 10 | 1.472 | 14.372 |  | GENTPJ | PSS2A | PIDGOV | EXAC8B | Closed | 10.789 | -2.2142 | HY | 14.372 |  | NO | 0 | 0.176 | 1.48 | 0.21271 | 0.266 | 0.499 | 1.8759 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 51392 | FD | FD | [11 empty] | Gen at 0.0 |  |  | Miss Turbine Type | Missing Model |  | Missing Sub R/X |  | 0 | 0 | -10 | 10 | 10 | 0 | [6 empty] | Closed | 0 | 1.4198 | UN | 10 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.65 |  |  | UN (Unknown) | FD
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 51393 | FD | FD | [11 empty] | Gen at 0.0 |  |  | Miss Turbine Type | Missing Model |  | Missing Sub R/X |  | 0 | 0 | -10 | 10 | 10 | 0 | [6 empty] | Closed | 0 | 1.4198 | UN | 10 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.65 |  |  | UN (Unknown) | FD
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51395 | 5 | 5 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 59.904 | -24 | 29 | 10 | 7.426 | 67.33 |  | GENROU | WSCCST | IEEEG1_GE | EXAC1A | Open | 0 | 0 | UN | 67.33 |  | NO | 0 | 0.197 | 4.21 | 2.8346 | 0.114 | 0.264 | 2.3158 | 13.8 |  |  | UN (Unknown) | 5
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51414 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.4 | -3.7 | 3.7 | 10 | -10.4 |  |  | GENTPJ | PSS2A |  | IEEET1 | Closed | 9.157 | -1.2236 | HY | 11.4 |  | NO | 0 | 0.15 | 1.622 | 0.18491 | 0.25 | 0.45 | 1.8 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51499 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 3 | -2.25 | 2.25 | 10 | -3 |  |  | GENTPJ |  |  |  | Closed | 2.491 | 0.47908 | HY | 3.75 | PF<0.8 | NO | 0 | 0.18 | 0.79 | 0.029625 | 0.154 | 0.447 | 2.9026 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51541 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16.26 | -5.99 | 8.37 | 10 | 0.49 | 16.75 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 13.618 | 0.27512 | HY | 16.75 |  | NO | 0.004 | 0.255 | 1.33 | 0.22278 | 0.185 | 0.322 | 1.7405 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51541 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16.26 | -5.99 | 8.37 | 10 | 0.49 | 16.75 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 13.618 | 0.27512 | HY | 16.75 |  | NO | 0.004 | 0.255 | 1.33 | 0.22278 | 0.203 | 0.353 | 1.7389 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 4.773 | -1.69 | 2.35 | 10 | 0.0050001 | 4.778 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 3.997 | 0.15702 | HY | 4.778 |  | NO | 0.063 | 0.151 | 0.9 | 0.043002 | 0.252 | 0.411 | 1.631 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11.042 | -4.06 | 5.67 | 10 | 0.343 | 11.385 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 9.247 | 0.15702 | HY | 11.385 |  | NO | 0.005 | 0.23 | 1.15 | 0.13093 | 0.201 | 0.328 | 1.6318 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11.042 | -4.06 | 5.67 | 10 | 0.343 | 11.385 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 9.247 | 0.15702 | HY | 11.385 |  | NO | 0.005 | 0.23 | 1.15 | 0.13093 | 0.211 | 0.345 | 1.6351 | 6.9 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11.042 | -4.06 | 5.67 | 10 | 0.343 | 11.385 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 9.247 | 0.15702 | HY | 11.385 |  | NO | 0.005 | 0.23 | 1.15 | 0.13093 | 0.215 | 0.352 | 1.6372 | 6.9 |  |  | HY (Hydro) | 4
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51556 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 3.5 | -1.7 | 1.7 | 10 | -3.5 |  |  | GENTPJ |  |  | EXAC8B | Closed | 2.964 | 0.42462 | HY | 3.89 |  | NO | 0 | 0.228 | 0.788 | 0.030653 | 0.091 | 0.335 | 3.6813 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51592 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 8.5 | -2.5 | 2.5 | 10 | -8.5 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 7.199 | -0.7278 | HY | 9 |  | NO | 0 | 0.23 | 1.72 | 0.1548 | 0.064 | 1.18 | 18.4375 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51592 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 8.5 | -2.5 | 2.5 | 10 | -8.5 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 7.199 | -0.7278 | HY | 9 |  | NO | 0 | 0.23 | 1.72 | 0.1548 | 0.064 | 1.18 | 18.4375 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51598 | A | A | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 28 | -18 | 18 | 10 | -28 |  |  | GENROU | PSS2A |  | EXST1_GE | Open | 0 | 0 | CC | 30 | PF<-0.85 | NO | 0 | 0.09 | 2.49 | 0.747 | 0.077 | 0.196 | 2.5455 | 13.8 |  |  | CC (Combined Cycle Generic) | A
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51599 | B | B | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 18 | -18 | 18 | 10 | -18 |  |  | GENROU | PSS2A |  | EXST1_GE | Open | 0 | 0 | CC | 30 | PF<0.8 | NO | 0 | 0.09 | 2.49 | 0.747 | 0.077 | 0.196 | 2.5455 | 13.8 |  |  | CC (Combined Cycle Generic) | B
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51719 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 3
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51719 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 4
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51719 | D2 | D2 | [9 empty] | Unreas H | [9 empty] | 0 | 3 | -1.19 | 2.286 | 10 | -3 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 3.81 | PF<0.8 | NO | 0 | 0.16 | 0.936 | 0.035662 | 0.1364 | 0.44 | 3.2258 | 12.5 |  |  | IC (Internal Combustion) | D2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51720 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51720 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51720 | D1 | D1 | [9 empty] | Unreas H | [9 empty] | 0 | 3 | -1.19 | 2.286 | 10 | -3 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 3.81 | PF<0.8 | NO | 0 | 0.16 | 0.936 | 0.035662 | 0.1364 | 0.44 | 3.2258 | 12.5 |  |  | IC (Internal Combustion) | D1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51739 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 34.002 | -4.19 | 12.15 | 10 | 2.248 | 36.25 |  | GENROU | PSS2B | GGOV1 | EXST2A | Open | 0 | 0 | ST | 36.25 |  | NO | 0 | 0.157 | 2.6 | 0.9425 | 0.04 | 0.13 | 3.25 | 13.8 |  |  | ST (Steam Turbine) | 1
52 | FORTISBC | 75 | Fortis BC |  | 52163 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 120 | -40 | 60 | 10 | -4.77e-06 | 120 |  | GENTPJ | PSS2A | HYGOV | ESST1A_GE | Closed | 109.3717 | 60 | HY | 141.5 |  | NO | 0 | 0.25 | 2.77 | 3.9195 | 0.08 | 0.3 | 3.75 | 14.4 |  |  | HY (Hydro) | 3
52 | FORTISBC | 75 | Fortis BC |  | 53000 | 5 | 5 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 6.5 | -2.8 | 2.8 | 10 | -6.5 | [6 empty] | Open | 0 | 0 | UN | 6.5 |  | NO | 0 | 0.13 | 0 |  |  |  | NAN | 12.5 |  |  | UN (Unknown) | 5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54006 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 5.6 | 0.22802 | 0.22802 | 76 | 0.6 | 6.2 |  | GENTPJ |  | IEEEG3_GE | EXDC1 | Closed | 3.6 | 0.228 | HY | 6 |  | NO | 0 | 0.18 | 3 | 0.18 | 0.17 | 0.55 | 3.2353 | 4.16 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54006 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 5.6 | 0.22169 | 0.22169 | 76 | 0.6 | 6.2 |  | GENTPJ |  | IEEEG3_GE | EXDC1 | Closed | 3.5 | 0.222 | HY | 6 |  | NO | 0 | 0.18 | 3 | 0.18 | 0.17 | 0.55 | 3.2353 | 4.16 |  |  | HY (Hydro) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54006 | 3 | 3 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 5.6 | 0.22169 | 0.22169 | 76 | 0.6 | 6.2 |  | GENTPJ |  | IEEEG3_GE | EXDC1 | Closed | 3.5 | 0.222 | HY | 6 |  | NO | 0 | 0.18 | 3 | 0.18 | 0.17 | 0.55 | 3.2353 | 4.16 |  |  | HY (Hydro) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54014 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 6 | 18 | -10.5 | 13.6 | 76 | 3.111 | 21.111 |  | GENTPJ |  | IEEEG1_GE | ESAC7B | Closed | 13.1 | 5.5638 | ST | 21.111 | PF<0.8 | NO | 0 | 0.13 | 3 | 0.63333 | 0.1395 | 0.3571 | 2.5599 | 13.8 |  |  | ST (Steam Turbine) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54033 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -0.5 | 8.4 | -2.8 | 4.1 | 76 | 0.9 | 9.3 |  | GENTPJ |  | IEEEG3_GE | EXDC1 | Open | 0 | 0 | HY | 9.3 |  | NO | 0.002 | 0.21 | 4.2 | 0.3906 | 0.328 | 0.684 | 2.0854 | 13.2 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54054 | G1 | G1 | [16 empty] | Missing PS |  |  | 0 | 99.5 | -32.7 | 48.2 | 76 | 0.5 | 100 |  | GENQEC |  | GGOV1 | EXST2A | Closed | 50 | 47.1822 | GT | 110.556 |  | NO | 0 | 0.3 | 4.97 | 5.4946 |  |  | NAN | 14.4 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54075 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | -20 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 23.1 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54086 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 22.5 | 0 | 0 | 76 | -22.5 |  |  | REGC_A |  |  | REEC_A | Closed | 18.5 | 0 | WT | 25.2 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54098 | G1 | G1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 4 | -1.452 | -1.452 | 76 | -4 |  |  | GENROU |  |  |  | Closed | 3.6 | -1.452 | UN | 5 |  | NO | 0 | 0.156 | 1.176 | 0.0588 | 0.1284 | 0.6203 | 4.831 | 138 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54098 | G2 | G2 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.4 | -0.871 | -0.871 | 76 | -2.4 |  |  | GENROU |  |  |  | Closed | 2.1 | -0.871 | UN | 3 |  | NO | 0 | 0.119 | 1.176 | 0.03528 | 0.1284 | 0.6203 | 4.831 | 138 |  |  | UN (Unknown) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54098 | G3 | G3 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.4 | -0.871 | -0.871 | 76 | -2.4 |  |  | GENROU |  |  |  | Open | 0 | 0 | UN | 3 |  | NO | 0 | 0.084 | 2.634 | 0.07902 | 0.1284 | 0.6203 | 4.831 | 138 |  |  | UN (Unknown) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54098 | G4 | G4 | [5 empty] | At Mvar Limit | [8 empty] | Miss Turbine Type |  |  |  |  | 0 | 3.1 | -1.5 | 1.5 | 76 | -3.1 |  |  | GENTPJ |  |  |  | Closed | 2.4 | -1.5 | UN | 3.48 |  | NO | 0 | 0.253 | 1.19 | 0.041412 | 0.077 | 0.298 | 3.8701 | 138 |  |  | UN (Unknown) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54098 | G5 | G5 | [5 empty] | At Mvar Limit | [8 empty] | Miss Turbine Type |  |  |  |  | 0 | 3.1 | -1.5 | 1.5 | 76 | -3.1 |  |  | GENTPJ |  |  |  | Closed | 2.4 | -1.5 | UN | 3.48 |  | NO | 0 | 0.253 | 1.19 | 0.041412 | 0.077 | 0.298 | 3.8701 | 138 |  |  | UN (Unknown) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54098 | G6 | G6 | [5 empty] | At Mvar Limit | [8 empty] | Miss Turbine Type |  |  |  |  | 0 | 3.2 | -1.55 | 1.55 | 76 | -3.2 |  |  | GENTPJ |  |  |  | Closed | 2.7 | -1.55 | UN | 3.55 |  | NO | 0 | 0.29 | 1.19 | 0.042245 | 0.077 | 0.298 | 3.8701 | 138 |  |  | UN (Unknown) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54098 | G7 | G7 | [5 empty] | At Mvar Limit | [6 empty] | Gen on HV |  | Miss Turbine Type |  |  |  |  | 0 | 9.5 | -4.6 | 4.6 | 76 | -9.5 |  |  | GENTPJ |  |  |  | Closed | 7.5 | -4.6 | UN | 10.55 |  | NO | 0 | 0.22 | 1.19 | 0.12555 | 0.077 | 0.298 | 3.8701 | 138 |  |  | UN (Unknown) | G7
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54102 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 60 | -19.7 | 29.1 | 76 | 6.7 | 66.7 |  | GENTPJ | PSS2B | HYGOV | ESDC4B | Closed | 29.8 | -2.264 | HY | 66.7 |  | NO | 0.003 | 0.28 | 3.52 | 2.3478 | 0.21 | 0.625 | 2.9762 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54107 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [7 empty] | Gen on HV | [6 empty] | 0 | 14.7 | -4.0757 | -4.0757 | 76 | -14.7 |  |  | REGC_A |  |  | REEC_A | Closed | 12.4 | -4.076 | WT | 16.2 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54108 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 60 | -19.4 | 28.6 | 76 | -2.38e-06 | 60 |  | GENTPJ | PSS2B | HYGOV | ESAC8B_GE | Closed | 29.8 | -2.7842 | HY | 65.5 |  | NO | 0.002 | 0.34 | 3.7 | 2.4235 | 0.186 | 0.599 | 3.2204 | 13.8 |  |  | HY (Hydro) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54121 | 1 | 1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.521 | -2.11 | 2.11 | 76 | -2.521 | [6 empty] | Open | 0 | 0 | UN | 3.53 | PF<0.8 | NO | 0.034 | 0.157 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54121 | 2 | 2 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.521 | -2.11 | 2.11 | 76 | -2.521 | [6 empty] | Open | 0 | 0 | UN | 3.53 | PF<0.8 | NO | 0.034 | 0.157 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54151 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 160 | -54.4 | 80.2 | 76 | 5 | 165 |  | GENTPJ | PSS2A | G2WSCC | EXAC8B | Closed | 12.0039 | -3.017 | HY | 184 |  | NO | 0.002 | 0.242 | 3.65 | 6.716 | 0.328 | 0.684 | 2.0854 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54172 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5.6 | -1.8 | 2.7 | 76 | 0.025 | 5.625 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 3 | 2.7 | HY | 6 |  | NO | 0.002 | 0.2 | 3.22 | 0.1932 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54172 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 3.4 | -1.1 | 1.6 | 76 | 0.2 | 3.6 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.5 | 1.6 | HY | 4 |  | NO | 0.002 | 0.2 | 3.22 | 0.1288 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54172 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 3.4 | -1.1 | 1.6 | 76 | 0.2 | 3.6 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.5 | 1.6 | HY | 4 |  | NO | 0.002 | 0.2 | 3.22 | 0.1288 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54172 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5.6 | -1.8 | 2.7 | 76 | 0.025 | 5.625 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 3 | 2.7 | HY | 6 |  | NO | 0.002 | 0.2 | 3.22 | 0.1932 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54189 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -15 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -7.9 | 0 | MP | 100 |  | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54189 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -15 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -7.9 | 0 | MP | 100 |  | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54196 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 4.08 | -1.3 | 1.9 | 76 | 0.42 | 4.5 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.5 | -1.3 | HY | 4.5 |  | NO | 0.002 | 0.2 | 3.22 | 0.1449 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54196 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 4.08 | -1.3 | 1.9 | 76 | 0.42 | 4.5 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.5 | -1.3 | HY | 4.5 |  | NO | 0.002 | 0.2 | 3.22 | 0.1449 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54214 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 14.1 | -4.4 | 6.5 | 76 | 0.9 | 15 |  | GENTPJ |  | IEEEG3_GE | EXDC1 | Closed | 6 | 6.5 | HY | 15 |  | NO | 0.002 | 0.16 | 4 | 0.6 | 0.129 | 0.605 | 4.6899 | 13.8 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54219 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 22.5 | 0 | 0 | 76 | -22.5 |  |  | REGC_A |  |  |  | Closed | 18.5 | 0 | WT | 22.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54222 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11 | -3.3 | 4.9 | 76 | 0.25 | 11.25 |  | GENTPJ |  | GPWSCC | EXDC1 | Closed | 4.5 | 0.19129 | HY | 11.25 |  | NO | 0.002 | 0.25 | 3.44 | 0.387 | 0.25 | 0.536 | 2.144 | 13.2 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54242 | G6 | G6 | [5 empty] | At Mvar Limit | [8 empty] | Miss Turbine Type | Missing Model |  |  |  | 0 | 5.7 | -1.873 | 2.76 | 76 | -5.7 | [6 empty] | Closed | 5 | -1.873 | UN | 6.33 |  | NO | 0.025 | 0.285 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54242 | G7 | G7 | [5 empty] | At Mvar Limit | [8 empty] | Miss Turbine Type | Missing Model |  |  |  | 0 | 4.275 | -1.405 | 2.07 | 76 | -4.275 | [6 empty] | Closed | 3.8 | -1.405 | UN | 4.75 |  | NO | 0.018 | 0.213 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | G7
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54242 | X4 | X4 | [8 empty] | RX Ratio | [6 empty] | Missing Model |  |  |  | 2.28 | 5.7 | 0 | 0 | 76 | -5.7 | [6 empty] | Closed | 5 | 0 | WT | 6.34 |  | NO | 0.4 | 0.312 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | X4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54242 | X5 | X5 | [5 empty] | At Mvar Limit |  |  | RX Ratio | [5 empty] | Miss Turbine Type | Missing Model |  |  |  | 2.07 | 4.425 | -1.454 | 2.143 | 76 | -4.425 | [6 empty] | Closed | 3.8 | -1.454 | UN | 5 |  | NO | 0.192 | 0.119 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | X5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54250 | D1 | D1 |  |  |  |  | Exceed Gen Limit | [7 empty] | Gen on HV | [6 empty] | -4.2 | 19.8 | -2.2371 | -2.2371 | 76 | -19.8 |  |  | REGC_A |  |  | REEC_A | Closed | 15.7 | -2.237 | WT | 22 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | D1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54266 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 16 | 0 | 0 | 76 | -16 |  |  | REGC_A |  |  | REEC_A | Closed | 13 | 0 | WT | 17.6 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 22 | 0 | 0 | 76 | -22 |  |  | (REGC_A) |  |  | (REEC_A) | Closed | 0.4 | 0 | PV | 27.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | PV (Photovoltaic) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G3 | G3 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G4 | G4 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G5 | G5 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G6 | G6 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G7 | G7 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G7
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G8 | G8 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G8
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | G9 | G9 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | G9
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54270 | GX | GX |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 2.5 | 0.67188 | 0.67188 | 76 | -2.5 | [6 empty] | Closed | 1.7 | 0.672 | IC | 2.5 |  | NO | 0 | 0.3 | 0 |  |  |  | NAN | 138 | BES Exempt |  | IC (Internal Combustion) | GX
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54275 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 22 | -7.231 | 10.655 | 76 | -22 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 27.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54320 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [7 empty] | Gen on HV | [6 empty] | 0 | 13.9 | -0.11857 | -0.11857 | 76 | -13.9 |  |  | REGC_A |  |  | REEC_A | Closed | 0.3 | -0.119 | WT | 16.8 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54345 | G5 | G5 | [14 empty] | Miss Turbine Type |  |  |  |  | 134 | 435 | -143 | 210 | 76 | 48.762 | 483.762 |  | GENROU | PSS2A | IEEEG1_GE | EXST1_GE | Open | 0 | 0 | UN | 483.762 |  | NO | 0.002 | 0.25 | 3.21 | 15.5288 | 0.044 | 0.2 | 4.5455 | 20 |  |  | UN (Unknown) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54350 | G6 | G6 | [14 empty] | Miss Turbine Type |  |  |  |  | 132.3 | 435 | -136.4 | 210 | 76 | 48.76 | 483.76 |  | GENROU | PSS2A | IEEEG1_GE | ESST1A_GE | Open | 0 | 0 | UN | 483.76 |  | NO | 0.002 | 0.205 | 2.3 | 11.1265 | 0.044 | 0.2 | 4.5455 | 20 |  |  | UN (Unknown) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54367 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 8.75 | 0 | 0 | 76 | -8.75 | [6 empty] | Closed | 7.2 | 0 | WT | 8.75 |  | NO | 0 | 0.769 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54377 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 5 | 0.15057 | 0.15057 | 76 | 0.4 | 5.4 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.5 | 0.151 | HY | 6 |  | NO | 0.002 | 0.2 | 3.22 | 0.1932 | 0.17 | 0.55 | 3.2353 | 4.16 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54381 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 3.6 | -1.2 | 1.7 | 76 | 1.5e-07 | 3.6 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.5 | -1.2 | HY | 4 |  | NO | 0.002 | 0.2 | 3.22 | 0.1288 | 0.17 | 0.55 | 3.2353 | 6.9 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54383 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 25 | 0 | 0 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | WT | 26.4 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54383 | G2 | G2 | [12 empty] | Gen on HV | [6 empty] | 0 | 22 | 0 | 0 | 76 | -22 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | WT | 24 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54403 | G3 | G3 | [14 empty] | Miss Turbine Type |  |  |  |  | 142 | 512 | -164 | 280 | 76 | 74 | 586 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST5B | Open | 0 | 0 | UN | 586 |  | NO | 0.004 | 0.277 | 2.9 | 16.994 | 0.07 | 0.25 | 3.5714 | 22 |  |  | UN (Unknown) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54408 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 31.8 | -10.5 | 15.4 | 76 | 3.494 | 35.294 |  | GENROU | PSS2A | GGOV1 | ESST4B | Closed | 25 | 15.4 | ST | 35.29 |  | NO | 0 | 0.145 | 3.1 | 1.094 | 0.055 | 0.299 | 5.4364 | 12.5 |  |  | ST (Steam Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54424 | G2 | G2 | [14 empty] | Miss Turbine Type |  |  |  |  | 199 | 418 | -137.37 | 202.45 | 76 | 59 | 477 |  | GENROU | PSS2A | IEEEG1_GE | ESST1A_GE | Open | 0 | 0 | UN | 477 |  | NO | 0.005 | 0.3 | 2.348 | 11.2 | 0.099 | 0.401 | 4.0505 | 19 |  |  | UN (Unknown) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54436 | G1 | G1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | -1.096 | IC | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 138 |  |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54436 | G2 | G2 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | -1.096 | IC | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 138 |  |  | IC (Internal Combustion) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54436 | G3 | G3 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | -1.096 | IC | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 138 |  |  | IC (Internal Combustion) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54436 | G4 | G4 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | -1.096 | IC | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 138 |  |  | IC (Internal Combustion) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54436 | G5 | G5 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | -1.096 | IC | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 138 |  |  | IC (Internal Combustion) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54436 | G6 | G6 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | -1.096 | IC | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 138 |  |  | IC (Internal Combustion) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54450 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 6.4 | 0.5981 | 0.5981 | 76 | -6.4 |  |  | GENTPJ |  |  |  | Closed | 4.7 | 0.598 | HY | 7 |  | NO | 0 | 0.2 | 3 | 0.21 | 0.17 | 0.55 | 3.2353 | 4.16 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54490 | G3 | G3 | [14 empty] | Miss Turbine Type |  |  |  |  | 176 | 525 | -169.6 | 255.4 | 76 | 61 | 586 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST5B | Closed | 430 | 38.7188 | UN | 586 |  | NO | 0.002 | 0.277 | 2.9 | 16.994 | 0.073 | 0.333 | 4.5616 | 22 |  |  | UN (Unknown) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54491 | G1 | G1 | [14 empty] | Miss Turbine Type |  |  |  |  | 123.6 | 450 | -104 | 200 | 76 | 32.353 | 482.353 |  | GENTPJ | PSS2A | IEEEG1_GE | EXST1_GE | Closed | 268.106 | 36.5308 | UN | 482.353 |  | NO | 0.002 | 0.25 | 3.742 | 18.0496 | 0.142 | 0.31 | 2.1831 | 20.5 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54492 | G2 | G2 | [14 empty] | Miss Turbine Type |  |  |  |  | 200 | 450 | -88 | 212 | 76 | 55.88 | 505.88 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST1A_GE | Closed | 268.237 | 35.4689 | UN | 505.882 |  | NO | 0.002 | 0.25 | 3.57 | 18.06 | 0.069 | 0.288 | 4.1739 | 20.5 |  |  | UN (Unknown) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54521 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 6.8 | 1.4286 | 1.4286 | 76 | -6.8 | [6 empty] | Closed | 5.7 | 1.429 | WT | 7.01 |  | NO | 999 | 999 | 0 |  |  |  | NAN | 240 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54521 | X2 | X2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 6.8 | 1.4286 | 1.4286 | 76 | -6.8 | [6 empty] | Closed | 5.7 | 1.429 | WT | 7.01 |  | NO | 999 | 999 | 0 |  |  |  | NAN | 240 |  |  | WT (Wind Turbine) | X2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54535 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [7 empty] | Gen on HV | [6 empty] | 0 | 16 | 1.3353 | 1.3353 | 76 | -16 |  |  | GENROU |  |  |  | Closed | 8.2 | 1.335 | ST | 17.8 |  | NO | 0 | 0.137 | 1.987 | 0.35369 | 0.1 | 0.2 | 2 | 69 |  |  | ST (Steam Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54535 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [7 empty] | Gen on HV | [6 empty] | 0 | 26 | 2.0029 | 2.0029 | 76 | -26 |  |  | GENROU |  |  |  | Closed | 12.3 | 2.003 | ST | 28.9 |  | NO | 0 | 0.132 | 3.7 | 1.0693 | 0.1 | 0.28 | 2.8 | 69 |  |  | ST (Steam Turbine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54556 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 15 | 0 | 0 | 76 | -15 | [6 empty] | Closed | 9.7 | 0 | WT | 16.7 |  | NO | 0 | 0.151 | 0 |  |  |  | NAN | 69 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54585 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 4.6 | 0 | 0 | 76 | -4.6 | [6 empty] | Closed | 3.2 | 0 | WT | 5.75 |  | NO | 0.006 | 0.301 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54585 | G3 | G3 | [5 empty] | At Mvar Limit | [6 empty] | Gen on HV |  | Miss Turbine Type | Missing Model | Missing PS |  |  | 0 | 4.8 | -1.2 | 1.2 | 76 | -4.8 | [6 empty] | Closed | 3.2 | -1.2 | UN | 100 |  | NO | 0 | 0.15 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54590 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 15 | 0 | 0 | 76 | -15 |  |  | REGC_A |  |  | REEC_A | Closed | 12.3 | 0 | WT | 16.667 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54590 | G2 | G2 | [12 empty] | Gen on HV | [6 empty] | 0 | 12 | 0 | 0 | 76 | -12 |  |  | REGC_A |  |  | REEC_A | Closed | 10.1 | 0 | WT | 13.333 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54590 | G3 | G3 | [12 empty] | Gen on HV | [6 empty] | 0 | 17 | 0 | 0 | 76 | -17 |  |  | REGC_A |  |  | REEC_A | Closed | 14.1 | 0 | WT | 19 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54590 | X1 | X1 | [12 empty] | Gen on HV | [6 empty] | 0 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 16.6 | 0 | WT | 22.3 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | X1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54625 | G2 | G2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -9 | 0 | -4.1 | -4.1 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -4.5 | -4.1 | MP | 100 | PF<0.8 | NO | 0 | 0.167 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54626 | M6 | M6 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -25.6 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -13.5 | 0 | MP | 100 |  | NO | 0 | 0.233 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | M6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54627 | G1 | G1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 96 | -28.4 | 41.9 | 76 | -12 | 84 |  | GENROU | PSS2C | GGOV3 | AC7C | Closed | 23 | 27.1459 | GT | 96.1 |  | NO | 0.002 | 0.21 | 6.37 | 6.1216 | 0.017 | 0.224 | 13.1765 | 13.8 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54683 | 10 | 10 | [5 empty] | At Mvar Limit |  | PSS No Ex | [11 empty] | 12 | 31.9 | -10.5 | 15.4 | 76 | 3.512 | 35.412 |  | GENROU | PSS2C | GGOV1 |  | Closed | 28.3 | 15.4 | JE | 35.41 |  | NO | 0 | 0.16 | 1.5 | 0.53115 | 0.078 | 0.34 | 4.359 | 13.8 |  |  | JE (Jet Engine) | 10 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54686 | 12 | 12 | [7 empty] | PSS No Ex | [11 empty] | 4 | 36 | -12.6 | 18.6 | 76 | 2.3 | 38.3 |  | GENROU | PSS2B | GGOV1 |  | Closed | 34.6 | 4.1995 | HY | 42.59 |  | NO | 0 | 0.16 | 4.5 | 1.9166 | 0.098 | 0.201 | 2.051 | 13.8 |  |  | HY (Hydro) | 12 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54687 | 11 | 11 | [7 empty] | PSS No Ex | [11 empty] | 12 | 31.9 | -10.5 | 15.4 | 76 | 3.512 | 35.412 |  | GENROU | PSS2C | GGOV1 |  | Closed | 22 | 4.8734 | JE | 35.41 |  | NO | 0 | 0.16 | 1.5 | 0.53115 | 0.078 | 0.34 | 4.359 | 13.8 |  |  | JE (Jet Engine) | 11 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54712 | 3 | 3 | [7 empty] | PSS No Ex | [11 empty] | 4 | 33 | -11 | 16 | 76 | -1.31e-06 | 33 |  | GENROU | PSS2B | GGOV1 |  | Closed | 31.5 | 9.2649 | JE | 42.59 |  | NO | 0 | 0.16 | 4.5 | 1.9166 | 0.287 | 0.694 | 2.4181 | 13.8 |  |  | JE (Jet Engine) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54713 | 14 | 14 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 20 | 45 | -12.6 | 44.48 | 76 | 22.5 | 67.5 |  | GENROU | PSS2C | GGOV1 |  | Closed | 40.9 | 18.4001 | JE | 67.5 | PF<0.8 | NO | 0.001 | 0.19 | 1.209 | 0.81607 | 0.099 | 0.38 | 3.8384 | 13.8 |  |  | JE (Jet Engine) | 14
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54780 | 1 | 1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.521 | -2.11 | 2.11 | 76 | -2.521 | [6 empty] | Open | 0 | 0 | UN | 3.53 | PF<0.8 | NO | 0.034 | 0.157 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54780 | 2 | 2 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.521 | -2.11 | 2.11 | 76 | -2.521 | [6 empty] | Open | 0 | 0 | UN | 3.53 | PF<0.8 | NO | 0.034 | 0.157 | 0 |  |  |  | NAN | 138 |  |  | UN (Unknown) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54789 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 4 | -1.7144 | W3 | 97.7 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54846 | G4 | G4 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.6 | -0.64518 | W3 | 16 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54848 | G5 | G5 |  |  |  | Unapproved Gen Model | [15 empty] | 0.675 | 14.4 | -6.8 | 7 | 76 | -14.4 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.5 | -0.73209 | W3 | 14.4 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54852 | G6 | G6 |  |  |  | Unapproved Gen Model | [15 empty] | 0.675 | 14.4 | -7 | 7 | 76 | -14.4 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.5 | -0.71957 | W3 | 14.4 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55087 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 5 | 23.3 | -7.657 | 11.28 | 76 | 6.2 | 29.5 |  | (GENTPJ) | (PSS2A) | (GGOV1) | (EXAC8B) | Closed | 19.8 | 1.3521 | CC | 29.5 |  | NO | 0.002 | 0.14 | 0 |  | 0.282 | 0.906 | 3.2128 | 13.8 |  |  | CC (Combined Cycle Generic) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55089 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 2.27 | 43 | -14.132 | 20.825 | 76 | 4.06 | 47.06 |  | GENTPJ | PSS2A | GGOV1 | EXAC8B | Closed | 32.2 | -14.132 | ST | 47.06 |  | NO | 0.001 | 0.183 | 3 | 1.4118 | 0.126 | 0.324 | 2.5714 | 13.8 |  |  | ST (Steam Turbine) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55109 | G4 | G4 | [12 empty] | Gen on HV | [6 empty] | -2 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 22.22 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55118 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 18.8 | 0 | 0 | 76 | -18.8 |  |  | GENTPJ |  |  |  | Closed | 6 | 0 | WT | 18.8 |  | NO | 0 | 0.147 | 1.275 | 0.2397 | 0.0748 | 0.3274 | 4.377 | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55119 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 26.4 |  | NO | 0 | 0.833 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55135 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 26.4 |  | NO | 0 | 0.833 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55135 | G2 | G2 | [12 empty] | Gen on HV | [6 empty] | 0 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 26.4 |  | NO | 0 | 0.833 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55146 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 10 | 46 | -16.2 | 30 | 76 | -8.3e-07 | 46 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 32.1 | -16.2 | JE | 57.882 |  | NO | 0 | 0.2 | 1.839 | 1.0644 | 0.14 | 0.4 | 2.8571 | 13.8 |  |  | JE (Jet Engine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55272 | JC | JC | [15 empty] | Missing Model |  |  |  | 0 | 12 | 0 | 0 | 76 | -12 | [6 empty] | Closed | 10 | 0 | GT | 15 |  | NO | 0.002 | 0.17 | 0 |  |  |  | NAN | 138 | BES Exempt |  | GT (Gas Turbine) | JC
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55328 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 40.8 | -11.4 | 7.9 | 76 | -40.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -4.4051 | W3 | 39.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55444 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 1.75 | 8 | 1.5497 | 1.5497 | 76 | 8 | 16 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 6.8 | 1.55 | GT | 9.8 |  | NO | 0.003 | 0.196 | 2.82 | 0.27636 | 0.05 | 0.18 | 3.6 | 138 | BES Exempt |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55444 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 1.75 | 8 | 1.5497 | 1.5497 | 76 | 8 | 16 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 6.8 | 1.55 | GT | 9.8 |  | NO | 0.003 | 0.196 | 2.82 | 0.27636 | 0.05 | 0.18 | 3.6 | 138 | BES Exempt |  | GT (Gas Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55476 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3 | 0.35623 | 0.35623 | 76 | -3 | [6 empty] | Closed | 2.5 | 0.356 | WT | 3.15 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55476 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3 | 0.35623 | 0.35623 | 76 | -3 | [6 empty] | Closed | 2.5 | 0.356 | WT | 3.15 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55482 | G1 | G1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 418.5 | -137 | 203 | 76 | 46.5 | 465 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST1A_GE | Open | 0 | 0 | UN | 465 |  | NO | 0.005 | 0.298 | 2.43 | 11.2995 | 0.07 | 0.3 | 4.2857 | 19 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55485 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 3.6 | -0.9346 | 0.9346 | 76 | -3.6 |  |  | (REGC_A) |  |  | (REEC_A) | Closed | 2.575 | -0.9346 | WT | 4 |  | NO | 0.12 | 0.74 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55485 | G2 | G2 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.6 | -0.9346 | 0.9346 | 76 | -3.6 | [6 empty] | Closed | 2.575 | -0.9346 | WT | 4 |  | NO | 0.12 | 0.74 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55485 | G3 | G3 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.6 | -0.9346 | 0.9346 | 76 | -3.6 | [6 empty] | Closed | 2.575 | -0.9346 | WT | 4 |  | NO | 0.12 | 0.74 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55485 | G4 | G4 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 3.6 | -0.9346 | 0.9346 | 76 | -3.6 | [6 empty] | Closed | 2.575 | -0.9346 | WT | 4 |  | NO | 0.12 | 0.74 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55487 | G2 | G2 | [14 empty] | Miss Turbine Type |  |  |  |  | 143.885 | 408 | -131 | 170 | 76 | 57 | 465 |  | GENTPJ | PSS2A | IEEEG1_GE | EXST1_GE | Open | 0 | 0 | UN | 465 |  | NO | 0.003 | 0.323 | 2.43 | 11.2995 | 0.093 | 0.325 | 3.4946 | 19 |  |  | UN (Unknown) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55496 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 60 | 166.3 | -42 | 78 | 76 | 17 | 183.3 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST1A_GE | Open | 0 | 0 | CA | 183.3 |  | NO | 0.001 | 0.18 | 3 | 5.499 | 0.056 | 0.16 | 2.8571 | 16 |  |  | CA (Combined Cycle Steam Part) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55497 | G5 | G5 | [14 empty] | Miss Turbine Type |  |  |  |  | 127.1 | 407 | -98.2 | 157.5 | 76 | -2 | 405 |  | GENROU | PSS2A | IEEEG1_GE | EXST4B | Open | 0 | 0 | UN | 438.589 |  | NO | 0.005 | 0.3 | 3.25 | 14.2541 | 0.08 | 0.217 | 2.7125 | 21 |  |  | UN (Unknown) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55516 | G1 | G1 | [6 empty] | Limit Power Fact |  |  | Unreas H | [9 empty] | 0 | 45 | -15.77 | 38.5 | 76 | 22.5 | 67.5 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 38.3 | 24.4797 | JE | 67.5 | PF<0.8 | NO | 0 | 0.17 | 1.25 | 0.84375 | 0.11 | 0.32 | 2.9091 | 13.8 |  |  | JE (Jet Engine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55628 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 9.2 | -2.498 | -2.498 | 76 | -9.2 | [6 empty] | Closed | 7.6 | -2.498 | WT | 9.2 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55628 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 9.2 | -2.2167 | -2.2167 | 76 | -9.2 | [6 empty] | Closed | 7.6 | -2.217 | WT | 9.2 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55630 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 15 | -5.7634 | -5.7634 | 76 | -15 |  |  | (REGC_A) |  |  | (REEC_A) | Closed | 11.9 | -5.763 | WT | 16.67 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55715 | 15 | 15 | [7 empty] | PSS No Ex | [11 empty] | 17 | 43 | -14.1 | 22 | 76 | 28.176 | 71.176 |  | GENROU | PSS2C | GGOV1 |  | Closed | 40.9 | 5.7252 | JE | 71.18 |  | NO | 0.005 | 0.144 | 1.193 | 0.84918 | 0.121 | 0.485 | 4.0083 | 13.8 |  |  | JE (Jet Engine) | 15
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55734 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [9 empty] | -13.05 | 0 | -4.7 | 6.5 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.6 | -4.7 | MP | 14.9 | PF<0.8 | NO | 0.009 | 0.28 | 0.904 | 0.1347 | 0.1 | 0.3 | 3 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55793 | G1 | G1 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | [9 empty] | 20 | 45.8 | -15.4 | 22.69 | 76 | -4.3e-07 | 45.8 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 18.5 | -0.36026 | GT | 76.941 |  | NO | 0.006 | 0.156 | 1.341 | 1.0318 | 0.11 | 0.49 | 4.4545 | 13.8 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56085 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.8 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56134 | 5 | 5 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | [9 empty] | 0 | 3.4 | 0.639 | 0.639 | 76 | -1.8e-07 | 3.4 |  | GENTPJ |  | GGOV1 | EXDC2_GE | Closed | 1.5 | 0.639 | IT | 3.4 |  | NO | 0 | 0.287 | 0.785 | 0.02669 | 0.17 | 0.55 | 3.2353 | 6.9 |  |  | IT (Internal Combustion Turbo Charged) | 5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56185 | M1 | M1 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.8 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56209 | 16 | 16 | [9 empty] | Unreas H | [9 empty] | -10 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.4 | 0 | MP | 100 |  | NO | 0 | 0.275 | 0.882 | 0.882 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 16 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56210 | 15 | 15 | [9 empty] | Unreas H | [9 empty] | -8 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.4 | 0 | MP | 100 |  | NO | 0 | 0.275 | 0.882 | 0.882 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 15 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56241 | G3 | G3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 11.5 | -4 | 7 | 76 | 1.5 | 13 |  | GENROU |  | GPWSCC | EXAC1 | Closed | 9.6 | 5.3048 | ST | 13 |  | NO | 0 | 0.19 | 11.3 | 1.469 | 0.2 | 0.6 | 3 | 13.8 |  |  | ST (Steam Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56241 | G4 | G4 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 11.5 | -4 | 7 | 76 | 1.5 | 13 |  | GENROU |  | GPWSCC | EXAC1 | Closed | 9.6 | 5.3048 | ST | 13 |  | NO | 0 | 0.19 | 11.3 | 1.469 | 0.2 | 0.6 | 3 | 13.8 |  |  | ST (Steam Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56266 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -26.35 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -19.9 | 0 | MP | 28 |  | NO | 0.004 | 0.21 | 1.2 | 0.336 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56272 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 8.5 | 0.93969 | 0.93969 | 76 | -8.5 | [6 empty] | Closed | 7.9 | 0.94 | W4 | 9.4 |  | NO | 0 | 0.232 | 0 |  |  |  | NAN | 25 |  |  | W4 (Wind Turbine, Type 4) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56308 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 45 | -28 | 28 | 76 | -45 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | WS | 53 | PF<-0.85 | NO | 0.3 | 1.2 | 0 |  |  |  | NAN | 0.72 |  |  | WS (Wind Turbine, Offshore) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56320 | G1 | G1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 11.5 | -4 | 7 | 76 | -11.5 | [6 empty] | Closed | 5.1 | 7 | GT | 13.5 |  | NO | 0 | 0.19 | 0 |  |  |  | NAN | 13.8 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56328 | G1 | G1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [13 empty] | 0 | 28.2 | -7.9 | 5.5 | 76 | -28.2 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -7.9 | W3 | 27.5 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56335 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 7.334 | 13.5 | -4.4 | 6.5 | 76 | -0.013001 | 13.487 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 13.1 | -4.4 | IC | 15 |  | NO | 0 | 0.144 | 4.4 | 0.66 | 0.1015 | 0.3261 | 3.2128 | 13.8 |  |  | IC (Internal Combustion) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56338 | 1 | 1 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0 | 41.4 | -0.12183 | 0.12183 | 76 | -41.4 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 20 | 0.122 | W3 | 44 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56351 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 16 | 90 | -38 | 92 | 76 | 22 | 112 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 77.501 | 23.2079 | GT | 112 | PF<0.8 | NO | 0.004 | 0.19 | 5.714 | 6.3997 | 0.08 | 0.28 | 3.5 | 13.8 |  |  | GT (Gas Turbine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56357 | 3 | 3 | [7 empty] | PSS No Ex | [11 empty] | 50 | 133 | -46.44 | 82.4 | 76 | -133 |  |  | GENROU | PSS2B |  |  | Closed | 101.401 | -19.2704 | CC | 157 |  | NO | 0.004 | 0.131 | 4.84 | 7.5988 | 0.23 | 0.45 | 1.9565 | 18 |  |  | CC (Combined Cycle Generic) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56389 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 30 | -14.5 | 14.5 | 76 | -30 |  |  | WT3G, (REGC_A) | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 30 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 25 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56401 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 24.75 | 0.071246 | 0.071246 | 76 | -24.75 |  |  | REGC_A |  |  |  | Closed | 0.5 | 0.071 | PV | 24.75 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 25 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56402 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 16.2 | -0.040612 | -0.040612 | 76 | -16.2 |  |  | GENROU |  |  |  | Closed | 0.2 | -0.041 | W1 | 18 |  | NO | 0 | 0.302 | 3 | 0.54 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56402 | 3 | 3 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 14.4 | -0.040612 | -0.040612 | 76 | -14.4 |  |  | GENROU |  |  |  | Closed | 0.2 | -0.041 | W1 | 16 |  | NO | 0 | 0.302 | 3 | 0.48 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56516 | G2 | G2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 101 | -24.88 | 36.39 | 76 | 26.28 | 127.28 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 39.8 | 22.5787 | CC | 127.28 |  | NO | 0 | 0.121 | 2.503 | 3.1858 | 0.047 | 0.123 | 2.617 | 13.8 |  |  | CC (Combined Cycle Generic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M2 | M2 | [14 empty] | Miss Turbine Type |  |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Open | 0 | 0 | UN | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | UN (Unknown) | M2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M3 | M3 | [14 empty] | Miss Turbine Type |  |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Open | 0 | 0 | UN | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | UN (Unknown) | M3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M4 | M4 | [14 empty] | Miss Turbine Type |  |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Open | 0 | 0 | UN | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | UN (Unknown) | M4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M5 | M5 | [14 empty] | Miss Turbine Type |  |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Open | 0 | 0 | UN | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | UN (Unknown) | M5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56620 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -0.55033 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56621 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -0.97683 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56623 | G3 | G3 |  |  |  | Unapproved Gen Model | [15 empty] | 0.6 | 12.8 | -6.2 | 6.2 | 76 | -12.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -0.80024 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56624 | G4 | G4 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -0.7236 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56625 | G5 | G5 |  |  |  | Unapproved Gen Model | [15 empty] | 0.975 | 20.8 | -10.1 | 10.1 | 76 | -20.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | 1.1081 | W3 | 19.58 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56634 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.018 | 39.6 | -17.1 | 20.5 | 76 | -39.6 |  |  | WT4G |  | WT4T | WT4E | Closed | 0.6 | -2.6312 | W4 | 44 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.4 |  |  | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56690 | 4 | 4 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 6.4 | 1.102 | 1.102 | 76 | -6.4 | [6 empty] | Closed | 5.9 | 1.102 | WT | 7.1 |  | NO | 0 | 0.232 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56773 | 1 | 1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | 0 | 46.2 | -33 | 33 | 76 | -46.2 |  |  | WT4G |  | WT4T | WT4E | Open | 0 | 0 | WT | 57.2 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.4 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56785 | M2 | M2 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.8 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56791 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0.675 | 14.4 | -7 | 7 | 76 | -14.4 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.4 | -0.51791 | W3 | 14.4 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56793 | G3 | G3 |  |  |  | Unapproved Gen Model | [15 empty] | 0.6 | 12.8 | -6.2 | 6.2 | 76 | -12.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.2 | -0.526 | W3 | 12.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56822 | G1 | G1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | 0 | 75.9 | -52.5 | 52.5 | 76 | -75.9 |  |  | WT4G |  | WT4T | WT4E | Closed | 2.4 | -10.2241 | W4 | 92.4 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.4 |  |  | W4 (Wind Turbine, Type 4) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56885 | ST | ST |  |  |  |  | Exceed Gen Limit | [14 empty] | 10 | 95.7 | -31.4 | 46.3 | 76 | 10.3 | 106 |  | GENQEC | PSS6C | IEEEG1_GE | AC7C | Closed | 95.701 | 11.1632 | CC | 106 |  | NO | 0.004 | 0.18 | 3.26 | 3.4556 |  |  | NAN | 13.8 |  |  | CC (Combined Cycle Generic) | ST
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56941 | M1 | M1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -32.49 | 0 | -15.7 | -15.7 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -4.6 | -15.7 | MP | 28 | PF<0.8 | NO | 0 | 0.2 | 1.2 | 0.336 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | M1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57210 | 21 | 21 | [9 empty] | Unreas H | [9 empty] | -6.5 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.4 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 21 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57210 | 22 | 22 | [9 empty] | Unreas H | [9 empty] | -5.4 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 22 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57233 | 11 | 11 | [6 empty] | Limit Power Fact | [12 empty] | 2 | 22 | -13 | 27 | 76 | 11.8 | 33.8 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 10.6 | 13.4577 | ST | 33.8 | PF<0.8 | NO | 0.004 | 0.147 | 1.86 | 0.62868 | 0.119 | 0.374 | 3.1429 | 13.8 |  |  | ST (Steam Turbine) | 11
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57264 | G1 | G1 |  |  |  |  | Exceed Gen Limit | At Mvar Limit | [13 empty] | 4.49 | 84.9 | -26.1 | 57.9 | 76 | 18.1 | 103 |  | GENROU | PSS2C | GGOV1 | ESAC7B | Closed | 84.901 | -26.1 | JE | 103 |  | NO | 0.004 | 0.175 | 6 | 6.18 | 0.077 | 0.275 | 3.5714 | 13.8 |  |  | JE (Jet Engine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57265 | 51 | 51 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [9 empty] | -15.932 | 0 | -7.2 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -13.4 | 0 | MP | 14 | PF<-0.85 | NO | 0.008 | 0.25 | 0.95 | 0.133 | 0.06 | 0.27 | 4.5 | 13.8 |  |  | MP (Motor/Pump) | 51
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57351 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 16 | 90 | -38 | 92 | 76 | 22 | 112 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 77.501 | 15.4458 | GT | 112 | PF<0.8 | NO | 0.004 | 0.19 | 5.714 | 6.3997 | 0.08 | 0.28 | 3.5 | 13.8 |  |  | GT (Gas Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57516 | G3 | G3 | [10 empty] | Unreas Sat | [8 empty] | 25 | 101 | -26.25 | 39.47 | 76 | 26.28 | 127.28 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 35 | 38.0346 | CC | 127.28 |  | NO | 0 | 0.121 | 2.503 | 3.1858 | 0.047 | 0.123 | 2.617 | 13.8 |  |  | CC (Combined Cycle Generic) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57534 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.019 | 41.8 | -18.1 | 21.7 | 76 | -41.8 |  |  | WT4G |  | WT4T | WT4E | Closed | 0.6 | -3.0905 | W4 | 46.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.4 |  |  | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57574 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | -20 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 22.23 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57574 | 2 | 2 | [12 empty] | Gen on HV | [6 empty] | -20 | 20 | 0 | 0 | 76 | -20 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 22.23 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 138 |  |  | WT (Wind Turbine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57735 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 37.7 | -22.3 | 22.3 | 76 | -37.7 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -2.2878 | W3 | 36.7 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57834 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [9 empty] | -13.05 | 0 | -4.7 | 6.5 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.6 | -4.7 | MP | 14.9 | PF<0.8 | NO | 0.009 | 0.28 | 0.904 | 0.1347 | 0.1 | 0.3 | 3 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57885 | M5 | M5 | [14 empty] | Miss Turbine Type | Missing Model |  |  |  | -11.19 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -6.8 | 0 | UN | 12.8 |  | NO | 0 | 0.32 | 0 |  |  |  | NAN | 6.9 |  |  | UN (Unknown) | M5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57901 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 25.74 | 0 | 0 | 76 | -25.74 |  |  | WT2G | WT2P | WT2T | WT2E | Open | 0 | 0 | W1 | 28.6 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W1 (Wind Turbine, Type 1) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58017 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 30 | -9.9 | 14.5 | 76 | 7.5 | 37.5 |  | GENROU |  | TGOV1 | ESST1A_GE | Closed | 20 | 7.9253 | OT | 37.5 |  | NO | 0 | 0.13 | 3.5 | 1.3125 | 0.065 | 0.3 | 4.6154 | 25 |  |  | OT (Other) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58030 | ST | ST | [5 empty] | At Mvar Limit | [13 empty] | 12 | 45.5 | -15 | 23.8 | 76 | -45.5 |  |  | GENROU | PSS2A |  | ESAC7B | Closed | 26.223 | -15 | CC | 50.6 |  | NO | 0.005 | 0.2 | 4.7 | 2.3782 | 0.12 | 0.67 | 5.5833 | 14.7 |  |  | CC (Combined Cycle Generic) | ST
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58052 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -3.4 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.6 | 0 | MP | 100 |  | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58070 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 10.35 | 1.5 | 1.5 | 76 | 2.59 | 12.94 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 10 | 1.5 | WT | 12.938 |  | NO | 0.005 | 0.173 | 0.899 | 0.11631 | 0.25 | 0.9 | 3.6 | 25 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58085 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58085 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58085 | 3 | 3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58088 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 1.134 | 5.4 | 2.2489 | 2.2489 | 76 | -1.4e-07 | 5.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 5 | 2.249 | IC | 7.63 |  | NO | 0 | 0.159 | 1.778 | 0.13566 | 0.153 | 0.493 | 3.2222 | 4.2 |  |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58111 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -40.89 | 0 | 0 | 0.9 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.16 | 3.425 | 3.425 | 0.25 | 0.38 | 1.52 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58124 | G1 | G1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4.2 | 7.3 | 76 | 1 | 16 |  | GENROU |  | GGOV1 | EXAC8B | Closed | 12 | 1.572 | GT | 15 |  | NO | 0 | 0.144 | 1.31 | 0.1965 | 0.01 | 0.08 | 8 | 25 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58124 | G2 | G2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 12.3 | -3.3 | 5.9 | 76 | 3.7 | 16 |  | GENROU |  | GGOV1 | EXAC8B | Closed | 12 | 1.572 | GT | 15 |  | NO | 0 | 0.145 | 1.31 | 0.1965 | 0.01 | 0.08 | 8 | 25 |  |  | GT (Gas Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58124 | G3 | G3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 13.5 | -5.6 | 5.9 | 76 | 2.5 | 16 |  | GENROU |  | GGOV1 | EXAC8B | Closed | 12.3 | 1.572 | GT | 15 |  | NO | 0 | 0.211 | 1.31 | 0.1965 | 0.01 | 0.08 | 8 | 25 |  |  | GT (Gas Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58134 | 7 | 7 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 3.4 | 0.30459 | 0.30459 | 76 | -1.8e-07 | 3.4 |  | GENROU |  | GGOV1 | EXST4B | Closed | 1.5 | 0.305 | IT | 3.4 |  | NO | 0 | 0.287 | 1.2 | 0.0408 | 0.05 | 0.3 | 6 | 6.9 |  |  | IT (Internal Combustion Turbo Charged) | 7
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58134 | 8 | 8 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 3.4 | 0.30459 | 0.30459 | 76 | -1.8e-07 | 3.4 |  | GENROU |  | GGOV1 | EXST4B | Closed | 1.5 | 0.305 | IT | 3.4 |  | NO | 0 | 0.287 | 1.2 | 0.0408 | 0.05 | 0.3 | 6 | 6.9 |  |  | IT (Internal Combustion Turbo Charged) | 8
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58187 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 58 | 190 | -4.8 | 82.7 | 76 | 63 | 253 |  | GENROU | PSS2C | GGOV1 | ESST4B | Closed | 172.101 | 34.9351 | GT | 253 |  | NO | 0 | 0.19 | 4.888 | 12.3666 | 0.09 | 0.17 | 1.8889 | 18 |  |  | GT (Gas Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58210 | G5 | G5 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact | [12 empty] | 20 | 26 | -8.22 | 20.411 | 76 | 6 | 32 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 17.7 | 4.013 | GT | 32 | PF<0.8 | NO | 0.001 | 0.201 | 8 | 2.56 | 0.13 | 0.34 | 2.6154 | 13.8 |  |  | GT (Gas Turbine) | G5 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58226 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0.3 | 3.2 | -1.1 | 1.5 | 76 | 0.4 | 3.6 |  | GENTPJ |  | GGOV1 | EXST1_GE | Closed | 2 | -1.1 | IC | 3.6 |  | NO | 0 | 0.25 | 2 | 0.072 | 0.03 | 0.25 | 8.3333 | 4.16 |  |  | IC (Internal Combustion) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58226 | 2 | 2 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0.3 | 3.2 | -1.1 | 1.5 | 76 | -0.2 | 3 |  | GENTPJ |  | GGOV1 | EXST1_GE | Closed | 2 | -1.1 | IC | 3 |  | NO | 0 | 0.25 | 2 | 0.06 | 0.03 | 0.25 | 8.3333 | 4.16 |  |  | IC (Internal Combustion) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58247 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 48 | -18.5 | 36.332 | 76 | 23.176 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 37.7 | 2.7678 | JE | 71.18 | PF<0.8 | NO | 0.004 | 0.19 | 1.25 | 0.88975 | 0.07 | 0.2 | 2.8571 | 13.8 |  |  | JE (Jet Engine) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58251 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 40.8 | -17.3 | 49.4 | 76 | 7.6e-07 | 40.8 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 34.3 | -1.2707 | JE | 71.18 | PF<0.8 | NO | 0.002 | 0.181 | 1.176 | 0.83708 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58259 | S1 | S1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -7.2 | 0 | 0 | 0 | 76 | 0 |  |  | GENROU |  |  |  | Closed | -6.2 | 0 | MP | 10 |  | NO | 0.005 | 0.357 | 11.3 | 1.13 | 0.2 | 0.6 | 3 | 13.8 |  |  | MP (Motor/Pump) | S1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58264 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 19.5 | 0 | 0 | 76 | -19.5 |  |  | WT2G | WT2P | WT2T | WT2E | Open | 0 | 0 | W4 | 21.8 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W4 (Wind Turbine, Type 4) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58275 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 6 | -2 | 2.9 | 76 | -6 | [6 empty] | Closed | 6 | -2 | IC | 6.7 |  | NO | 0 | 0.232 | 0 |  |  |  | NAN | 25 |  |  | IC (Internal Combustion) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58297 | G9 | G9 | [10 empty] | Unreas Sat | [8 empty] | 1.4 | 93 | -30.56 | 45.04 | 76 | -93 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 65.101 | 17.5168 | GT | 103.2 |  | NO | 0.004 | 0.175 | 6.06 | 6.2539 | 0.025 | 0.348 | 13.92 | 13.8 |  |  | GT (Gas Turbine) | G9
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58334 | 10 | 10 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 1.8 | 9.3 | -5 | 9.7 | 76 | -9.3 |  |  | GENTPJ |  |  |  | Closed | 1.5 | 1.6433 | IT | 11.7 | PF<0.8 | NO | 0 | 0.167 | 6 | 0.702 | 0.866 | 0.295 | 0.34065 | 13.8 |  |  | IT (Internal Combustion Turbo Charged) | 10
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58338 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 27 | -0.081223 | 0.081223 | 76 | -27 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 15 | -0.081 | W3 | 30 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58364 | S2 | S2 | [10 empty] | Unreas Sat | [8 empty] | -7.2 | 0 | 0 | 0 | 76 | 0 |  |  | (GENROU) |  |  |  | Closed | -6.2 | 0 | MP | 10 |  | NO | 0.005 | 0.357 | 0 |  | 0.2 | 0.6 | 3 | 13.8 |  |  | MP (Motor/Pump) | S2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58379 | G1 | G1 | [9 empty] | Unreas H | [9 empty] | 17 | 50 | -16.43 | 24.22 | 76 | 0.4 | 50.4 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 41.8 | -15.2746 | JE | 76.941 |  | NO | 0.005 | 0.18 | 1.38 | 1.0618 | 0.07 | 0.288 | 4.1143 | 13.8 |  |  | JE (Jet Engine) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58380 | G2 | G2 | [9 empty] | Unreas H | [9 empty] | 17 | 50 | -16.43 | 24.22 | 76 | 0.4 | 50.4 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 41.8 | -15.3847 | JE | 76.941 |  | NO | 0.005 | 0.18 | 1.38 | 1.0618 | 0.07 | 0.288 | 4.1143 | 13.8 |  |  | JE (Jet Engine) | G2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58402 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 14.4 | -0.040612 | -0.040612 | 76 | -14.4 |  |  | GENROU |  |  |  | Closed | 0.2 | -0.041 | W1 | 16 |  | NO | 0 | 0.302 | 3 | 0.48 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58402 | 4 | 4 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 18 | -0.040612 | -0.040612 | 76 | -18 |  |  | GENROU |  |  |  | Closed | 0.2 | -0.041 | W1 | 20 |  | NO | 0 | 0.302 | 3 | 0.6 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58445 | 1 | 1 | [14 empty] | Miss Turbine Type |  |  |  |  | 7.334 | 13.487 | -4.43 | 6.53 | 76 | -13.487 |  |  | GENTPJ |  |  | ESAC8B_GE | Open | 0 | 0 | UN | 14.986 |  | NO | 0.003 | 0.132 | 4.4 | 0.65938 | 0.0641 | 0.225 | 3.5101 | 25 |  |  | UN (Unknown) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58670 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 3 | 13.7 | -4.1 | 6.1 | 76 | 0.389 | 14.089 |  | GENTPJ | PSS2A | GPWSCC | REXS | Closed | 12.9 | -1.7999 | HY | 14.089 |  | NO | 0 | 0.33 | 1.35 | 0.1902 | 0.13 | 0.22 | 1.6923 | 13.8 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58750 | 1 | 1 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact | [12 empty] | 20 | 40.8 | -17.3 | 49.4 | 76 | 7.6e-07 | 40.8 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 17.1 | 38.896 | JE | 71.18 | PF<0.8 | NO | 0.004 | 0.181 | 1.176 | 0.83708 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58901 | 3 | 3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 27.72 | 0 | 0 | 76 | -27.72 |  |  | WT2G | WT2P | WT2T | WT2E | Open | 0 | 0 | W1 | 30.8 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W1 (Wind Turbine, Type 1) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58985 | M3 | M3 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.8 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59069 | G1 | G1 | [8 empty] | RX Ratio | [10 empty] | 15 | 47 | -15.6 | 23 | 76 | 5.875 | 52.875 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 31.1 | -10.9338 | JE | 52.875 |  | NO | 0.156 | 0.133 | 4.928 | 2.6057 | 0.15 | 0.45 | 3 | 13.8 |  |  | JE (Jet Engine) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59083 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 32.8 | 1.3752 | 1.3752 | 76 | -32.8 | [6 empty] | Closed | 13.7 | 1.375 | WT | 32.8 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59134 | 1 | 1 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 0 | 9.3 | -1.1542 | -1.1542 | 76 | -9.3 |  |  | GENTPJ |  |  |  | Closed | 8.1 | -1.154 | WT | 11.67 |  | NO | 0 | 0.167 | 0.83 | 0.096861 | 0.2 | 0.8 | 4 | 25 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59145 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 1.8 | 6 | 0 | 0 | 76 | 1.2 | 7.2 |  | GENROU |  | GGOV1 | IEEET1 | Open | 0 | 0 | GT | 7.2 |  | NO | 0.003 | 0.232 | 1.5 | 0.108 | 0.03 | 0.4 | 13.3333 | 25 |  |  | GT (Gas Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59209 | 18 | 18 | [9 empty] | Unreas H | [9 empty] | -6.95 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.4 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 18 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59209 | 19 | 19 | [9 empty] | Unreas H | [9 empty] | -6.5 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.4 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 19 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59209 | 20 | 20 | [9 empty] | Unreas H | [9 empty] | -4 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.4 | 0 | MP | 100 |  | NO | 0 | 0.25 | 0.75 | 0.75 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 20 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59241 | 11 | 11 | [9 empty] | Unreas H | [9 empty] | -4.05 | 0 | -2 | -2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.4 | -2 | MP | 4.5 | PF<0.8 | NO | 0 | 0.3 | 0.785 | 0.035325 | 0.17 | 0.55 | 3.2353 | 4.2 |  |  | MP (Motor/Pump) | 11
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59247 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 48 | -18.5 | 36.332 | 76 | 23.176 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 37.7 | 4.8983 | JE | 71.18 | PF<0.8 | NO | 0.004 | 0.19 | 1.25 | 0.88975 | 0.07 | 0.2 | 2.8571 | 13.8 |  |  | JE (Jet Engine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59251 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 40.8 | -17.3 | 49.4 | 76 | 7.6e-07 | 40.8 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 34.3 | -1.2644 | JE | 71.18 | PF<0.8 | NO | 0.002 | 0.181 | 1.176 | 0.83708 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59297 | G8 | G8 | [10 empty] | Unreas Sat | [8 empty] | 1.4 | 93 | -30.56 | 45.04 | 76 | -93 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 65.201 | 17.6206 | GT | 103.2 |  | NO | 0.004 | 0.175 | 6.06 | 6.2539 | 0.025 | 0.348 | 13.92 | 13.8 |  |  | GT (Gas Turbine) | G8
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59474 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 15 | 3.1077 | 3.1077 | 76 | -15 |  |  | REGC_A |  |  | REEC_A | Closed | 12.4 | 3.108 | WT | 16.7 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59566 | G1 | G1 | [14 empty] | Miss Turbine Type | Missing Model |  |  |  | 0 | 8 | -3.875 | 3.875 | 76 | -8 | [6 empty] | Closed | 5 | 0.78894 | UN | 10 |  | NO | 0.004 | 0.219 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59605 | FD | FD | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 |  |  |  | Missing Model |  | Missing Sub R/X |  | 0 | 0 | -100 | 100 | 76 | 0 | [6 empty] | Closed | 0 | -93.3218 | WT | 100 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 23 |  |  | WT (Wind Turbine) | FD
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59685 | M4 | M4 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.8 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59721 | G1 | G1 | [8 empty] | RX Ratio | [10 empty] | 0 | 105 | -35.7 | 50.85 | 76 | -105 |  |  | REGC_A |  |  | REEC_A | Closed | 8 | -8.6456 | W4 | 127.8 |  | NO | 0.742 | 0.371 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59734 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [9 empty] | -13.05 | 0 | -4.7 | 6.5 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.6 | -4.7 | MP | 14.9 | PF<0.8 | NO | 0.009 | 0.28 | 0.904 | 0.1347 | 0.1 | 0.3 | 3 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59740 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 34.5 | -20.4 | 20.4 | 76 | -34.5 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 5 | -2.2878 | W3 | 33.7 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59835 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 75.6 | 0 | 0 | 76 | -75.6 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 14.4 | 0 | W3 | 79.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59841 | 12 | 12 | [9 empty] | Unreas H | [9 empty] | -4.05 | 0 | -2 | -2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.4 | -2 | MP | 4.5 | PF<0.8 | NO | 0 | 0.3 | 0.785 | 0.035325 | 0.17 | 0.55 | 3.2353 | 4.2 |  |  | MP (Motor/Pump) | 12
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59866 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -26.35 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -19.9 | 0 | MP | 28 |  | NO | 0.004 | 0.21 | 1.2 | 0.336 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59885 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.8 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59885 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.8 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59885 | 3 | 3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.8 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59901 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21.78 | 0 | 0 | 76 | -21.78 |  |  | WT2G | WT2P | WT2T | WT2E | Open | 0 | 0 | W1 | 24.2 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W1 (Wind Turbine, Type 1) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59935 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 73.8 | 0 | 0 | 76 | -73.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 13.9 | 0 | W3 | 77.9 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59941 | M2 | M2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -32.49 | 0 | -15.7 | -15.7 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -4.6 | -15.7 | MP | 36 | PF<0.8 | NO | 0 | 0.2 | 1.2 | 0.432 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | M2
60 | IDAHO | 1 | No owner defined |  | 60003 | 1 | 1 | [18 empty] | No Owner | -80 | 80 | -20.7 | 33.8 | 11 | -80 |  |  | REGC_A |  |  | REEC_C | Closed | 23.2 | -18.05 | BA | 80 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  | HMWY_34.5_T501TER | BA (Energy Storage, Battery) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 60003 | 2 | 2 |  | Missing BA | [17 empty] | -36 | 36 | -8 | 13.5 | 9999 | -36 | [6 empty] | Open | 0 | 0 | BA | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 2
60 | IDAHO | 11 | Idaho Power Company |  | 60151 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 147.8 | -66.5528 | 69.6696 | 11 | 6.2 | 154 |  | GENTPJ | PSS2B | HYG3 |  | Closed | 118.4 | 24.0381 | HY | 145 |  | YES | 0 | 0.295 | 3.53 | 5.1185 | 0.133 | 0.351 | 2.6391 | 14.4 |  | HELLSCYN_14.4_G011 | HY (Hydro) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 60153 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 150.1 | -74.5236 | 74.5236 | 11 | 3.9 | 154 |  | GENTPJ | PSS2B | HYG3 | ESDC4B | Closed | 133.7 | 23.3311 | HY | 166.75 |  | YES | 0 | 0.295 | 3 | 5.0025 | 0.194 | 0.579 | 2.9845 | 14.4 |  | HELLSCYN_14.4_G013 | HY (Hydro) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 60322 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 31.8 | -6 | 6 | 11 | -0.2 | 31.6 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 28.6 | 2.4049 | HY | 30 |  | NO | 0 | 0.305 | 3.53 | 1.059 | 0.18 | 0.35 | 1.9444 | 13.8 |  | STRIKE_13.8_G02 | HY (Hydro) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 60323 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 31.4 | -8.3 | 15.24 | 11 | 0.2 | 31.6 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 29 | 1.5872 | HY | 30 |  | YES | 0 | 0.305 | 3.53 | 1.059 | 0.18 | 0.35 | 1.9444 | 13.8 |  | STRIKE_13.8_G03 | HY (Hydro) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 60530 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -40.6 | 40.6 | -32.2 | 32.2 | 11 | -40.6 |  |  | REGC_A |  |  | REEC_C | Closed | 3.2 | -6.6031 | BA | 38.4 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | BMSU_.48_BAT | BA (Energy Storage, Battery) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 60545 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 204.4 | -91 | 91 | 11 | -204.4 | [6 empty] | Closed | 153.3 | -30.4426 | P4 | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.64 |  | PVS1_.64_PV1 | P4 (Photovoltaic, Tracking) | 1
60 | IDAHO | 605 | US Geothermal | Bonneville Power Admin | 60807 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 10 | 0 | 0 | 11 | -10 | [6 empty] | Closed | 8.7 | 0 | BT | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  | raft_river_geo | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 61081 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | -4 | 4 | -1.8 | 1.8 | 11 | -4 | [6 empty] | Closed | 0.8 | 1.8 | BA | 4.37 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  | WEISER_WRES | BA (Energy Storage, Battery) | 1 | Netting Exempt
60 | IDAHO | 50 | US Bur Reclam | Bonneville Power Admin | 61811 | 6 | 6 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 2.7 | -2 | 1.3 | 11 | 0.66 | 3.36 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 2.6 | 1.3 | HY | 3 | PF<-0.85 | NO | 0.019 | 0.241 | 1.377 | 0.04131 | 0.12 | 0.33 | 2.75 | 2.4 |  | MINIDOKA_2.4_G06 | HY (Hydro) | 6
60 | IDAHO | 50 | US Bur Reclam | Bonneville Power Admin | 61811 | 7 | 7 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 6 | -3 | 3.3 | 11 | 0.1 | 6.1 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 3.5 | 3.3 | HY | 6 |  | NO | 0.006 | 0.32 | 1.967 | 0.11802 | 0.1 | 0.42 | 4.2 | 2.4 |  | MINIDOKA_2.4_G07 | HY (Hydro) | 7
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64098 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 4.8 | 12 | 1 | 1 | 24 | 2.7e-07 | 12 |  | GENTPF |  | GGOV1 | EXAC1 | Closed | 11.9 | 1 | BT | 10 |  | NO | 0 | 0.222 | 4 | 0.4 | 0.19 | 0.676 | 3.5579 | 13.8 |  | RAG_1_2_IPP_GO | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64105 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 13.5 | -0.4 | 10.13 | 24 | 1.5 | 15 |  | GENTPF |  | GGOV1 |  | Closed | 13.5 | 1.17 | BT | 18.75 | PF<0.8 | YES | 0.002 | 0.18 | 1.679 | 0.31481 | 1.084 | 1.28 | 1.1808 | 12.3 |  | STEAMBOT_12_G01 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Closed | 11.2 | 3.4595 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Closed | 10 | 3.4595 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Open | 0 | 0 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G3 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Open | 0 | 0 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G4 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 4
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64150 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 7.5 | 10.97 | -1 | 14.5 | 24 | 5.69 | 16.66 |  | GENROU |  | GGOV1 | ESAC7B | Open | 0 | 0 | BT | 18.9 | PF<0.8 | YES | 0.001 | 0.24 | 7.5 | 1.4175 | 0.212 | 0.75 | 3.5377 | 4.16 |  | BEOWAWE_4.16_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64150 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.72 | 0 | 0 | 24 | 0.28 | 2 |  | GENROU |  | GGOV1 | ESAC7B | Open | 0 | 0 | BT | 3.125 |  | YES | 0.001 | 0.15 | 1 | 0.03125 | 0.2 | 0.5 | 2.5 | 4.16 |  | BEOWAWE_4.16_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64267 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -6.25 | 18.1554 | 24 | 7.5 | 22.5 |  | GENTPF |  | GGOV1 |  | Closed | 3.3035 | -2.7897 | BT | 22.5 | PF<0.8 | YES | 0.002 | 0.15 | 1.6 | 0.36 | 1.084 | 1.28 | 1.1808 | 13.2 |  | JERSEYV_13.8_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64267 | 2 | 2 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 1 | 7.5 | -1.892 | 7.4749 | 24 | 15 | 22.5 |  | GENTPF |  | GGOV1 |  | Closed | 3.0965 | -1.892 | BT | 22.5 | PF<0.8 | YES | 0.003 | 0.144 | 1.6 | 0.36 | 1.084 | 1.28 | 1.1808 | 13.2 |  | JERSEYV_13.8_GEN2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64311 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 5 | 20 | -7 | 19.3461 | 24 | 5 | 25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 7.8996 | -0.53677 | BT | 25 | PF<0.8 | YES | 0 | 0.133 | 1.76 | 0.44 | 0.065 | 0.17 | 2.6154 | 12.47 |  | ORMAT_13.8_G2A | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64350 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 2.2 | 22 | -7 | 8.4 | 24 | -22 | [6 empty] | Closed | 12.1 | 0.23813 | PV | 28.13 |  | NO | 0 | 0.02 | 0 |  |  |  | NAN | 13.8 |  | CRD_IPP_PV_G1 | PV (Photovoltaic) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64467 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -1.6091 | 14.8863 | 24 | 3.75 | 18.75 |  | GENTPF |  | GGOV1 |  | Closed | 4.6024 | 2.8436 | BT | 18.75 | PF<0.8 | YES | 0.002 | 0.187 | 1.679 | 0.31481 | 1.084 | 1.28 | 1.1808 | 13.8 |  | GALENA_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64467 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -1.6091 | 14.8863 | 24 | 3.75 | 18.75 |  | GENTPF |  | GGOV1 |  | Closed | 4.6024 | 2.8436 | BT | 18.75 | PF<0.8 | YES | 0.002 | 0.187 | 1.679 | 0.31481 | 1.084 | 1.28 | 1.1808 | 13.8 |  | GALENA_13.8_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64469 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 4 | 15 | -7.5 | 18.1969 | 24 | 3.75 | 18.75 |  | GENTPF |  | GGOV1 | REXS | Closed | 4.1797 | 3.5427 | BT | 18.75 | PF<0.8 | YES | 0 | 0.15 | 1.08 | 0.2025 | 1.084 | 1.28 | 1.1808 | 13.8 |  | DESRT_PK_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64469 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 2 | 11 | -3.0881 | 11.1881 | 24 | 7.75 | 18.75 |  | GENTPF |  | GGOV1 | REXS | Closed | 4.1797 | 3.5427 | BT | 18.75 | PF<0.8 | YES | 0 | 0.164 | 1.08 | 0.2025 | 1.084 | 1.28 | 1.1808 | 13.8 |  | DESRT_PK_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64502 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 12.4 | 31 | -7.5 | 15 | 24 | -31 |  |  | GENTPF | PSS2A |  | EXAC1 | Open | 0 | 0 | BT | 33 |  | NO | 0 | 0.197 | 4 | 1.32 | 0.19 | 0.676 | 3.5579 | 4.16 |  | SALTWLLS_13.8_G01 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64577 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 5 | 20 | -7 | 19.1641 | 24 | 5 | 25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 8.5996 | -0.21813 | BT | 25 | PF<0.8 | YES | 0 | 0.133 | 1.76 | 0.44 | 0.065 | 0.17 | 2.6154 | 12.47 |  | ORMAT_13.8_G1A | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64593 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 20 | -7 | 8.4 | 24 | -20 | [6 empty] | Closed | 15.5 | 0.70843 | PV | 28.125 |  | NO | 0.004 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | CRD_IPP_PV_G2 | PV (Photovoltaic) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64788 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 27.1 | -15.9452 | 23.7482 | 24 | -27.1 |  |  | GENTPJ | PSS2B |  | ESAC8B_GE | Closed | 16.9367 | 6.5297 | BT | 30.235 | PF<0.8 | YES | 0.003 | 0.17 | 1.15 | 0.3477 | 0.07 | 0.17 | 2.4286 | 12.47 |  | CAITHNES_12.47_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64788 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 7.98 | -3.5416 | 4.7371 | 24 | 7.02 | 15 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 4.0633 | 1.6324 | BT | 6.9 |  | YES | 0.003 | 0.152 | 0.76 | 0.05244 | 0.096 | 0.199 | 2.0729 | 12.47 |  | CAITHNES_12.47_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64801 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 3.4 | 14.2 | -6.1155 | 16.724 | 24 | -14.2 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 11.3357 | 0.52182 | BT | 21.25 | PF<0.8 | YES | 0.003 | 0.15 | 1.17 | 0.24862 | 0.063 | 0.334 | 5.3016 | 12.47 |  | BLUEMTN_12.5_G1A | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64801 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 6.3 | 13.8 | -6.1244 | 16.7955 | 24 | -13.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 11.114 | 0.52182 | BT | 21.25 | PF<0.8 | YES | 0.003 | 0.15 | 1.17 | 0.24862 | 0.063 | 0.334 | 5.3016 | 12.47 |  | BLUEMTN_12.5_G1B | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64801 | 3 | 3 | [9 empty] | Unreas H | [9 empty] | 4.6 | 11.7 | -6.1714 | 17.1709 | 24 | -11.7 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 9.9503 | 0.52182 | BT | 21.25 | PF<0.8 | YES | 0.003 | 0.15 | 1.17 | 0.24862 | 0.063 | 0.334 | 5.3016 | 12.47 |  | BLUEMTN_12.5_G1C | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64855 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 94 | 235 | -79.307 | 128.9408 | 24 | -235 |  |  | GENTPJ | PSS2B |  | REXS | Closed | 180 | 90.7565 | ST | 270 |  | YES | 0.001 | 0.178 | 4.13 | 11.151 | 0.283 | 0.639 | 2.258 | 18 |  | NWMNTGEN_18_G01 | ST (Steam Turbine) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64923 | 3 | 3 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 2 | 15 | -5.322 | 14.4759 | 24 | -6e-07 | 15 |  | GENTPJ | PSS2B | GGOV1 |  | Closed | 6.5895 | 1.2727 | BT | 15 | PF<0.8 | YES | 0.003 | 0.133 | 1.5 | 0.225 | 0.031 | 0.097 | 3.129 | 12.47 |  | FRONTIRS_13.8_GEO6 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64929 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 102.58 | -24.57 | 55.28 | 24 | -102.58 |  |  | REGC_A |  |  | REEC_A | Closed | 101 | 10.87 | PV | 122.85 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | BATMNPV-G_0.63_1 | PV (Photovoltaic) | 1 |  | PSS Exempt
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64945 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 5.5 | 12.4 | -4.5 | 7.85 | 24 | 2e-07 | 12.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 12.4 | 0.86026 | BT | 14.7 |  | YES | 0.002 | 0.129 | 2 | 0.294 | 0.2 | 0.67 | 3.35 | 12.47 |  | PRGATORY_12.5_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64956 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -5.322 | 8.8874 | 24 | -6e-07 | 15 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 6.8195 | 1.3094 | BT | 15 |  | YES | 0.003 | 0.133 | 3.4 | 0.51 | 0.031 | 0.097 | 3.129 | 12.47 |  | FRONTIRS_13.8_GEO3 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
65 | PACE | 7 | PacifiCorp - East |  | 65021 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.5 | -6 | 12 | 7 | 2.2 | 12.7 |  | GENROU |  | GGOV1 |  | Closed | 10.5 | -5.8074 | JE | 18.82 | PF<0.8 | NO | 0.004 | 0.4 | 8.3 | 1.5621 | 0.057 | 0.217 | 3.807 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65021 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.5 | -6 | 12 | 7 | 2.2 | 12.7 |  | GENROU |  | GGOV1 |  | Closed | 10.5 | -5.8074 | JE | 18.82 | PF<0.8 | NO | 0.004 | 0.4 | 8.3 | 1.5621 | 0.055 | 0.201 | 3.6545 | 13.8 |  |  | JE (Jet Engine) | 2
65 | PACE | 7 | PacifiCorp - East |  | 65021 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.5 | -6 | 12 | 7 | 2.2 | 12.7 |  | GENROU |  | GGOV1 |  | Closed | 10.5 | -5.8074 | JE | 18.82 | PF<0.8 | NO | 0.004 | 0.4 | 8.3 | 1.5621 | 0.07 | 0.216 | 3.0857 | 13.8 |  |  | JE (Jet Engine) | 3
65 | PACE | 7 | PacifiCorp - East |  | 65171 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 4.93 | 11 | -6.3 | 7 | 7 | -11 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 9.9 | -0.39258 | CC | 14.12 |  | NO | 0.003 | 0.2 | 4 | 0.5648 | 0.037 | 0.189 | 5.1081 | 12.5 |  |  | CC (Combined Cycle Generic) | 1
65 | PACE | 8 | UAMPS |  | 65363 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -2 | 3.2 | 7 | -4 |  |  | GENTPJ |  |  | ESAC5A | Open | 0 | 0 | IC | 5.12 | PF<0.8 | NO | 0.009 | 0.204 | 1.5 | 0.0768 | 0.233 | 0.497 | 2.133 | 12.5 |  |  | IC (Internal Combustion) | 12
65 | PACE | 8 | UAMPS |  | 65363 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1 | 1.6 | 7 | -2 |  |  | GENTPJ |  |  | ESAC5A | Open | 0 | 0 | IC | 2.27 | PF<0.8 | NO | 0.009 | 0.182 | 1.5 | 0.03405 | 0.233 | 0.497 | 2.133 | 12.5 |  |  | IC (Internal Combustion) | 3
65 | PACE | 7 | PacifiCorp - East |  | 65405 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -5 | 11 | 7 | 3.75 | 18.75 |  | GENTPJ | PSS2A | HYGOV | EXST4B | Closed | 7.5 | 6.4713 | HY | 18.75 |  | NO | 0.003 | 0.3 | 1.8 | 0.3375 | 0.196 | 0.544 | 2.7755 | 6.9 |  |  | HY (Hydro) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65406 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -5 | 11 | 7 | 3.75 | 18.75 |  | GENTPJ | PSS2A | HYGOV | EXST4B | Open | 0 | 0 | HY | 18.75 |  | NO | 0.003 | 0.3 | 1.8 | 0.3375 | 0.196 | 0.544 | 2.7755 | 6.9 |  |  | HY (Hydro) | 1
65 | PACE | 8 | UAMPS |  | 65408 | 45 | 45 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -1 | 2 | 7 | -4 |  |  | GENTPJ |  |  | ESAC5A | Open | 0 | 0 | IC | 4.55 |  | NO | 0.009 | 0.182 | 1.5 | 0.06825 | 0.233 | 0.497 | 2.133 | 12.5 |  |  | IC (Internal Combustion) | 45
65 | PACE | 8 | UAMPS |  | 65408 | 67 | 67 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -1 | 2 | 7 | -4 |  |  | GENTPJ |  |  | ESAC5A | Open | 0 | 0 | IC | 4.55 |  | NO | 0.009 | 0.182 | 1.5 | 0.06825 | 0.233 | 0.497 | 2.133 | 12.5 |  |  | IC (Internal Combustion) | 67
65 | PACE | 8 | UAMPS |  | 65408 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1 | 1.5 | 7 | -2 |  |  | GENTPJ |  |  | ESAC5A | Open | 0 | 0 | IC | 2.27 |  | NO | 0.009 | 0.182 | 1.5 | 0.03405 | 0.233 | 0.497 | 2.133 | 12.5 |  |  | IC (Internal Combustion) | 8
65 | PACE | 7 | PacifiCorp - East |  | 65542 | 1 | 1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4 | 31 | -22 | 38 | 7 | 4.6 | 35.6 |  | GENROU | PSS2A | GGOV1 |  | Closed | 31 | 12.1434 | GT | 57.41 | PF<0.8 | NO | 0.001 | 0.147 | 2.4 | 1.3778 | 0.149 | 0.76 | 5.1007 | 13.8 |  |  | GT (Gas Turbine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65543 | 1 | 1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4 | 31 | -22 | 38 | 7 | 4.6 | 35.6 |  | GENROU | PSS2A | GGOV1 |  | Closed | 31 | 12.1434 | GT | 57.41 | PF<0.8 | NO | 0.001 | 0.147 | 2.4 | 1.3778 | 0.149 | 0.76 | 5.1007 | 13.8 |  |  | GT (Gas Turbine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65544 | 1 | 1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4 | 31 | -22 | 38 | 7 | 4.6 | 35.6 |  | GENROU | PSS2A | GGOV1 |  | Closed | 31 | 12.1434 | GT | 57.41 | PF<0.8 | NO | 0.001 | 0.147 | 2.4 | 1.3778 | 0.149 | 0.76 | 5.1007 | 13.8 |  |  | GT (Gas Turbine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65583 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 86.2 | -27.062 | -26.962 | 7 | 65.6 | 151.8 |  | WT1G |  | WT1T |  | Closed | 21.6 | -27.062 | WT | 151.8 |  | NO | 0 | 0.149 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65600 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 27.61 | 69 | -35 | 37 | 7 | 1.6 | 70.6 |  | GENROU |  | IEEEG1_GE | IEEET1 | Closed | 49.3 | -1.0011 | ST | 70.6 |  | NO | 0.002 | 0.119 | 4.81 | 3.3959 | 0.206 | 0.587 | 2.8495 | 13.8 |  |  | ST (Steam Turbine) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 65605 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 22.61 | 73 | -25 | 45 | 7 | 2 | 75 |  | GENROU |  | IEEEG1_GE | IEEET1 | Closed | 52.1 | 17.2491 | CA | 75 |  | NO | 0.002 | 0.105 | 4.62 | 3.465 | 0.207 | 0.724 | 3.4976 | 13.8 |  |  | CA (Combined Cycle Steam Part) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 65612 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 11.1 | 38 | -21 | 28.58 | 7 | 3.4 | 41.4 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 27.1 | 9.9595 | JE | 71.2 | PF<0.8 | YES | 0.004 | 0.189 | 1.25 | 0.89 | 0.2 | 0.7 | 3.5 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65613 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 10 | 38 | -21 | 28.58 | 7 | 3.4 | 41.4 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 27.1 | 8.4963 | JE | 71.2 | PF<0.8 | YES | 0.004 | 0.189 | 1.258 | 0.8957 | 0.2 | 0.7 | 3.5 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65614 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 13.8 | 38 | -21 | 28.58 | 7 | 3.4 | 41.4 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 27.1 | 13.5003 | JE | 71.2 | PF<0.8 | YES | 0.004 | 0.189 | 1.258 | 0.8957 | 0.2 | 0.7 | 3.5 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65680 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 0 | -40 | 75 | 7 | 0 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 0 | 20.8308 | SC | 75 | PF<0.8 | NO | 0.001 | 0.34 | 1.05 | 0.7875 | 0.19 | 0.38 | 2 | 13.8 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
65 | PACE | 8 | UAMPS |  | 65932 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 38.2 | -22 | 32 | 7 | 0.8 | 39 |  | GENROU | PSS2B | GGOV1 | REXS | Closed | 35 | 2.2774 | JE | 60 | PF<0.8 | NO | 0.004 | 0.198 | 2.54 | 1.524 | 0.092 | 0.24 | 2.6087 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 8 | UAMPS |  | 65933 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 39.1 | -27 | 57 | 7 | 0.9 | 40 |  | GENROU | PSS2B | GGOV1 | REXS | Closed | 35 | -8.9514 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.181 | 1.24 | 0.88258 | 0.142 | 0.394 | 2.7746 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 8 | UAMPS |  | 66069 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 66.5 | -31.1944 | 52.0278 | 7 | -66.5 |  |  | GENTPJ | PSS2C |  | ESAC7B | Closed | 66.5 | 14.8994 | CC | 92 | PF<0.8 | YES | 0.003 | 0.157 | 3.82 | 3.5144 | 0.0657 | 0.5474 | 8.3318 | 13.8 |  |  | CC (Combined Cycle Generic) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66120 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -8.3 | 6.9364 | 7 | -10 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 5 | -5.0462 | HY | 11.11 | PF<-0.85 | YES | 0.003 | 0.11 | 2 | 0.2222 | 0 | 0 | NAN | 6.6 |  |  | HY (Hydro) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66120 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -8.3 | 6.9364 | 7 | -10 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 5 | -5.0462 | HY | 11.11 | PF<-0.85 | YES | 0.003 | 0.11 | 2 | 0.2222 | 0 | 0 | NAN | 6.6 |  |  | HY (Hydro) | 2
65 | PACE | 7 | PacifiCorp - East |  | 66125 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -8.5 | 7.6 | 7 | -10 |  |  | GENTPJ |  |  | ESST1A_GE | Open | 0 | 0 | HY | 11.11 | PF<0.8 | YES | 0.003 | 0.11 | 2 | 0.2222 | 0 | 0 | NAN | 6.6 |  |  | HY (Hydro) | 1
65 | PACE | 50 | US Bur Reclam |  | 66165 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 35.2 | -19.2 | 25.35 | 7 | 6.7 | 41.9 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 17.6 | 14.1271 | HY | 46.46 |  | NO | 0.004 | 0.352 | 1.742 | 0.80933 | 0.146 | 0.33 | 2.2603 | 11.5 |  |  | HY (Hydro) | 2
65 | PACE | 50 | US Bur Reclam |  | 66170 | 3 | 3 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 35.2 | -19.2 | 27.2 | 7 | 0.3 | 35.5 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Open | 0 | 0 | HY | 46.464 | PF<0.8 | NO | 0.004 | 0.352 | 1.742 | 0.8094 | 0.146 | 0.37 | 2.5342 | 11.5 |  |  | HY (Hydro) | 3
65 | PACE | 50 | US Bur Reclam |  | 66175 | 4 | 4 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 35.2 | -19.2 | 27.2 | 7 | 0.3 | 35.5 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Open | 0 | 0 | HY | 46.464 | PF<0.8 | NO | 0.004 | 0.352 | 1.742 | 0.8094 | 0.146 | 0.37 | 2.5342 | 11.5 |  |  | HY (Hydro) | 4
65 | PACE | 8 | UAMPS |  | 66550 | Z4 | Z4 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | 0 | 57.6 | -49.7 | 33.7 | 7 | -57.6 |  |  | WT4G |  | WT4T | WT4E | Closed | 14.4 | -14.3612 | W1 | 165 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.6 |  |  | W1 (Wind Turbine, Type 1) | Z4 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 66801 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 38 | -19 | 53 | 7 | 12 | 50 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 27.1 | -13.7499 | JE | 71.2 | PF<0.8 | NO | 0.004 | 0.18 | 1.176 | 0.83731 | 0.128 | 0.48 | 3.75 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66802 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 38 | -19 | 53 | 7 | 12 | 50 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 27.1 | -13.8539 | JE | 71.2 | PF<0.8 | NO | 0.004 | 0.18 | 1.176 | 0.83731 | 0.128 | 0.48 | 3.75 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66803 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 38 | -19 | 53 | 7 | 12 | 50 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 27.1 | -13.7499 | JE | 71.2 | PF<0.8 | NO | 0.004 | 0.18 | 1.176 | 0.83731 | 0.128 | 0.48 | 3.75 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66804 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 38 | -19 | 53 | 7 | 12 | 50 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 27.1 | -13.8539 | JE | 71.2 | PF<0.8 | NO | 0.004 | 0.18 | 1.176 | 0.83731 | 0.128 | 0.48 | 3.75 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66805 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 38 | -19 | 53 | 7 | 12 | 50 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 27.1 | -13.8539 | JE | 71.2 | PF<0.8 | NO | 0.004 | 0.18 | 1.176 | 0.83731 | 0.128 | 0.48 | 3.75 | 13.8 |  |  | JE (Jet Engine) | 1
65 | PACE | 8 | UAMPS |  | 66842 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -2 | 3 | 7 | -4 |  |  | GENTPJ |  |  | ESAC5A | Open | 0 | 0 | IC | 5.12 |  | NO | 0.009 | 0.204 | 1.5 | 0.0768 | 0.233 | 0.497 | 2.133 | 12.5 |  |  | IC (Internal Combustion) | 12
65 | PACE | 7 | PacifiCorp - East |  | 67939 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 0 | -35 | 65 | 7 | 0 |  |  | GENTPJ |  |  | ESAC2A | Closed | 0 | -8.1437 | SC | 65 | PF<0.8 | NO | 0.002 | 0.16 | 1.93 | 1.2545 | 0.168 | 0.294 | 1.75 | 12.47 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 68020 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12 | -8 | 8.9 | 7 | 2.7e-07 | 12 |  | GENTPJ |  | GGOV1 | ESAC5A | Closed | 12 | 0.11468 | GT | 14.86 | PF<-0.85 | NO | 0 | 0.157 | 1.44 | 0.21398 | 0.1 | 0.3 | 3 | 13.8 |  |  | GT (Gas Turbine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 68020 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12 | -8 | 8.9 | 7 | 2.7e-07 | 12 |  | GENTPJ |  | GGOV1 | ESAC5A | Closed | 12 | 0.11468 | GT | 14.86 | PF<-0.85 | NO | 0 | 0.157 | 1.44 | 0.21398 | 0.1 | 0.3 | 3 | 13.8 |  |  | GT (Gas Turbine) | 2
65 | PACE | 7 | PacifiCorp - East |  | 68161 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 9 | -5.295 | 14.77 | 7 | 10.25 | 19.25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 8.1 | 3.0427 | OT | 19.25 | PF<0.8 | YES | 0.003 | 0.2 | 1.59 | 0.30608 | 0.0591 | 0.1236 | 2.0914 | 12.5 |  |  | OT (Other) | 1
65 | PACE | 7 | PacifiCorp - East |  | 68162 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 9 | -5.295 | 14.77 | 7 | 10.25 | 19.25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 8.1 | 3.0427 | OT | 19.25 | PF<0.8 | YES | 0.003 | 0.2 | 1.59 | 0.30608 | 0.0591 | 0.1236 | 2.0914 | 12.5 |  |  | OT (Other) | 1
65 | PACE | 8 | UAMPS |  | 68830 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2.7 | -1 | 2 | 7 | -2.7 |  |  | GENTPJ |  |  | ESAC8B_GE | Open | 0 | 0 | IC | 3.4 |  | NO | 0.012 | 0.093 | 1 | 0.034 | 0.23 | 0.946 | 4.113 | 4.2 |  |  | IC (Internal Combustion) | 12
65 | PACE | 8 | UAMPS |  | 68830 | 34 | 34 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2.5 | -1 | 2 | 7 | -2.5 |  |  | GENTPJ |  |  | ESAC8B_GE | Open | 0 | 0 | IC | 3.4 | PF<0.8 | NO | 0.012 | 0.093 | 1 | 0.034 | 0.23 | 0.946 | 4.113 | 4.2 |  |  | IC (Internal Combustion) | 34
65 | PACE | 8 | UAMPS |  | 68831 | 56 | 56 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.5 | -0.8 | 1.2 | 7 | -1.5 |  |  | GENTPJ |  |  | ESAC8B_GE | Open | 0 | 0 | IC | 2.02 | PF<0.8 | NO | 0.02 | 0.147 | 1 | 0.0202 | 0.224 | 1 | 4.4643 | 4.2 |  |  | IC (Internal Combustion) | 56
65 | PACE | 8 | UAMPS |  | 68831 | 78 | 78 | [10 empty] | Unreas Sat | [8 empty] | 0 | 3.7 | -2 | 3 | 7 | -3.7 |  |  | GENTPJ |  |  | ESAC8B_GE | Open | 0 | 0 | IC | 5 | PF<0.8 | NO | 0.018 | 0.137 | 1 | 0.05 | 0.206 | 0.909 | 4.4126 | 4.2 |  |  | IC (Internal Combustion) | 78
65 | PACE | 8 | UAMPS |  | 68844 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 6.5 | -2 | 3.2 | 7 | 0.72 | 7.22 |  | GENTPJ |  | HYGOV | ESAC8B_GE | Open | 0 | 0 | IC | 7.22 |  | NO | 0.01 | 0.223 | 1.3 | 0.09386 | 0.19 | 0.575 | 3.0263 | 12.5 |  |  | IC (Internal Combustion) | 1
65 | PACE | 8 | UAMPS |  | 68844 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 2 | 6.5 | -2 | 3.2 | 7 | 0.72 | 7.22 |  | GENTPJ |  | HYGOV | ESAC8B_GE | Open | 0 | 0 | IC | 7.22 |  | NO | 0.01 | 0.223 | 1.3 | 0.09386 | 0.19 | 0.575 | 3.0263 | 12.5 |  |  | IC (Internal Combustion) | 2
65 | PACE | 7 | PacifiCorp - East |  | 69102 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 19.5 | -9.438 | 9.438 | 7 | -19.5 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 4.9 | 1.5593 | W1 | 23 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | W1 (Wind Turbine, Type 1) | 1
65 | PACE | 7 | PacifiCorp - East |  | 69523 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 43.2 | -13.5 | 18.8 | 7 | -43.2 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.8 | 10.3133 | W1 | 47.08 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.7 |  |  | W1 (Wind Turbine, Type 1) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 69707 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 60 | -18.1 | 18.1 | 7 | -60 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 15 | -18.1 | W4 | 100 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.7 |  |  | W4 (Wind Turbine, Type 4) | 1 |  | PSS EXEMPT
70 | PSCOLORADO | 65 | PSColorado |  | 70120 | C2 | C2 | [5 empty] | At Mvar Limit | [13 empty] | 195 | 365 | -67.3 | 120.3 | 65 | -5 | 360 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 354.5465 | 120.3 | CA | 440 |  | NO | 0.003 | 0.28 | 3.8 | 16.72 | 0.075 | 0.474 | 6.32 | 24 |  | COMA_24_ | CA (Combined Cycle Steam Part) | C2
70 | PSCOLORADO | 65 | PSColorado |  | 70146 | G6 | G6 | [5 empty] | At Mvar Limit | [13 empty] | 54.1 | 178 | -46.1 | 96.5 | 65 | -4 | 174 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 174 | 96.5 | CT | 218 |  | NO | 0 | 0.175 | 5.35 | 11.663 | 0.123 | 0.393 | 3.1951 | 18 |  | CHER_17.5_G6 | CT (Combined Cycle Combustion Turbine Part) | G6
70 | PSCOLORADO | 65 | PSColorado |  | 70310 | C1 | C1 | [5 empty] | At Mvar Limit | [13 empty] | 224.2 | 526 | -126.7 | 241.5 | 65 | 20.994 | 546.994 |  | GENROU | PSS2C | IEEEG1_GE | ESAC7B | Closed | 525 | 241.5 | ST | 614 |  | NO | 0.004 | 0.205 | 2.13 | 13.0782 | 0.099 | 0.455 | 4.596 | 22 |  | PAWN_22_NO_1 | ST (Steam Turbine) | C1
70 | PSCOLORADO | 65 | PSColorado |  | 70314 | G1 | G1 | [7 empty] | PSS No Ex | [11 empty] | 110.3 | 131.5 | -39 | 54.5 | 65 | 18.5 | 150 |  | GENROU | PSS2C | GGOV1 |  | Closed | 130 | 36.6181 | GT | 150 |  | NO | 0.003 | 0.202 | 7.068 | 10.602 | 0.14 | 0.49 | 3.5 | 16 |  | MANG_15.2_GSU11 | GT (Gas Turbine) | G1
70 | PSCOLORADO | 65 | PSColorado |  | 70315 | G2 | G2 | [7 empty] | PSS No Ex | [11 empty] | 110 | 131 | -35 | 46 | 65 | 19 | 150 |  | GENROU | PSS2C | GGOV1 |  | Closed | 130 | 36.6181 | GT | 150 |  | NO | 0.003 | 0.202 | 7.068 | 10.602 | 0.14 | 0.49 | 3.5 | 16 |  | MANG_15.2_GSU12 | GT (Gas Turbine) | G2
70 | PSCOLORADO | 65 | PSColorado |  | 70407 | G3 | G3 | [5 empty] | At Mvar Limit | [13 empty] | 55.2 | 156 | -21.6 | 71.8 | 65 | 4 | 160 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 155 | 71.8 | CT | 206 |  | NO | 0.003 | 0.22 | 5.4 | 11.124 | 0.073 | 0.236 | 3.2329 | 18 |  | FSVR_18_NO_3 | CT (Combined Cycle Combustion Turbine Part) | G3
70 | PSCOLORADO | 65 | PSColorado |  | 70409 | ST | ST | [5 empty] | At Mvar Limit | [13 empty] | 44.19 | 317.8 | -103.5 | 118.31 | 65 | -317.8 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 316 | 118.31 | CC | 403 |  | NO | 0.003 | 0.25 | 3.3 | 13.299 | 0.067 | 0.286 | 4.2687 | 22 |  | FSVR_22_NO_1 | CC (Combined Cycle Generic) | ST
70 | PSCOLORADO | 65 | PSColorado |  | 70486 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 4.7 | 18.1 | -6.3 | 13.6 | 65 | -0.1 | 18 |  | GENTPJ |  | GGOV1 | ESST2A | Closed | 15 | 4.8799 | GT | 29.6 | PF<0.8 | NO | 0.004 | 0.169 | 7.4 | 2.1904 | 0.095 | 0.305 | 3.2105 | 13.8 |  | ATER_13.8_GEN2 | GT (Gas Turbine) | G2
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70487 | G4 | G4 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 12.8 | 35.3 | -0.5 | 22.8 | 65 | 6.7 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 29.3 | 3.7582 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT4 | CC (Combined Cycle Generic) | G4
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70487 | G5 | G5 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 14.1 | 33 | -0.4 | 23.8 | 65 | 9 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT5 | CC (Combined Cycle Generic) | G5
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70490 | G3 | G3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 14.8 | 37.8 | 1 | 22.5 | 65 | 4.2 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 30.8 | 3.6582 | CC | 57.4 |  | NO | 0 | 0.18 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT3 | CC (Combined Cycle Generic) | G3
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70495 | G1 | G1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 12.9 | 36.3 | 4.3 | 23.2 | 65 | 5.7 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 29.3 | 4.3 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT1 | CC (Combined Cycle Generic) | G1
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70495 | G2 | G2 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 14.8 | 35 | 4.6 | 23.2 | 65 | 7 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 28 | 4.6 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT2 | CC (Combined Cycle Generic) | G2
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70498 | G3 | G3 | [16 empty] | Missing PS |  |  | 17 | 34.1 | -7 | 14 | 65 | 14.9 | 49 |  | GENTPF |  | GGOV1 | EXST2A | Closed | 33 | -2.2536 | CT | 49 |  | NO | 0.005 | 0.192 | 5.84 | 2.8616 | 0.0545 | 0.657 | 12.055 | 13.8 |  | CPP1_13.8_GT3 | CT (Combined Cycle Combustion Turbine Part) | G3
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70498 | ST | ST | [16 empty] | Missing PS |  |  | 17 | 36 | -7 | 24 | 65 | 11 | 47 |  | GENTPF |  | GGOV1 | EXST2A | Closed | 35 | -2.2536 | CA | 47 |  | NO | 0.005 | 0.122 | 6.116 | 2.8745 | 0.124 | 0.55 | 4.4355 | 13.8 |  | CPP1_13.8_ST2 | CA (Combined Cycle Steam Part) | ST
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70501 | ST | ST | [16 empty] | Missing PS |  |  | 10 | 27 | -5 | 15 | 65 | 12 | 39 |  | GENTPF |  | GGOV1 | EXST2A | Closed | 26 | 1.4914 | CA | 39 |  | NO | 0 | 0.18 | 4.4 | 1.716 | 0.13 | 0.45 | 3.4615 | 13.8 |  | CPP1_13.8_ST_1 | CA (Combined Cycle Steam Part) | ST
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70553 | G5 | G5 | [6 empty] | Limit Power Fact | [12 empty] | 9.75 | 39 | -19.4 | 38.9 | 65 | 1.7 | 40.7 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Closed | 35 | -2.7108 | JE | 71.18 | PF<0.8 | NO | 0.005 | 0.19 | 1.2 | 0.85416 | 0.105 | 0.412 | 3.9238 | 13.8 |  | ARAP_13.2_NO_5 | JE (Jet Engine) | G5
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70553 | G6 | G6 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 39.5 | -19.5 | 39.5 | 65 | 1.2 | 40.7 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Closed | 35 | -2.7108 | JE | 71.18 | PF<0.8 | NO | 0.005 | 0.19 | 1.2 | 0.85416 | 0.105 | 0.412 | 3.9238 | 13.8 |  | ARAP_13.2_NO_6 | JE (Jet Engine) | G6
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70556 | ST | ST | [16 empty] | Missing PS |  |  | 17 | 70 | -13 | 35 | 65 | -20 | 50 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 49.5 | -11.6766 | CA | 40 |  | NO | 0.005 | 0.132 | 4 | 1.6 | 0.124 | 0.55 | 4.4355 | 12.5 |  | CPP1_12.5_ST4 | CA (Combined Cycle Steam Part) | ST
70 | PSCOLORADO | 65 | PSColorado |  | 70557 | G7 | G7 | [6 empty] | Limit Power Fact | [12 empty] | 15.3 | 40.7 | -14.5 | 31.4 | 65 | 30.48 | 71.18 |  | GENROU | PSS2C | GGOV3 | ESAC7B | Closed | 39 | -6.2555 | JE | 71.18 | PF<0.8 | NO | 0.005 | 0.193 | 1.2 | 0.85416 | 0.08 | 0.45 | 5.625 | 13.8 |  | VALM_13.8_NO_7 | JE (Jet Engine) | G7
70 | PSCOLORADO | 65 | PSColorado |  | 70558 | G8 | G8 | [6 empty] | Limit Power Fact | [12 empty] | 14.6 | 41.7 | -11.5 | 32.5 | 65 | 29.48 | 71.18 |  | GENROU | PSS2C | GGOV3 | ESAC7B | Closed | 40 | -6.2161 | JE | 71.18 | PF<0.8 | NO | 0.005 | 0.193 | 1.2 | 0.85416 | 0.08 | 0.45 | 5.625 | 13.8 |  | VALM_13.8_NO_8 | JE (Jet Engine) | G8
70 | PSCOLORADO | 65 | PSColorado |  | 70562 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 79.3 | 136.5 | -71.6 | -25.2 | 65 | 97.5 | 234 |  | GENROU | PSS2B | GGOV1 | ESST4B | Closed | 135 | -25.2 | GT | 234 |  | NO | 0.003 | 0.196 | 4.85 | 11.349 | 0.07 | 0.29 | 4.1429 | 18 |  | BSNG_18_GEN1 | GT (Gas Turbine) | G1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70593 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 79.42 | 143.07 | -60.61 | 108.53 | 65 | 11.33 | 154.4 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 142 | 31.8076 | GT | 247 | PF<0.8 | NO | 0.003 | 0.205 | 4.87 | 12.0289 | 0.068 | 0.58 | 8.5294 | 18 |  | SPIN_18_SPINDLE_G1 | GT (Gas Turbine) | G1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70704 | W1 | W1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 75 | -36.32 | 36.32 | 65 | -75 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 18.75 | -36.32 | W3 | 83.5 |  | YES | 0 | 0.15 | 0 |  |  |  | NAN | 0.575 |  | COGR_0.5 | W3 (Wind Turbine, Type 3) | W1
70 | PSCOLORADO | 73 | Tri-State G&T |  | 70725 | PV | PV | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 40.2 | -23.2 | 23.2 | 65 | -40.2 |  |  | REGC_A |  |  | REEC_A | Closed | 38.2 | -7.4695 | UN | 46.3 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | UN (Unknown) | PV
70 | PSCOLORADO | 65 | PSColorado |  | 70742 | W2 | W2 | [5 empty] | At Mvar Limit | [13 empty] | 24 | 132 | -43.39 | 43.39 | 65 | -132 |  |  | REGC_B | WTGPT_A | WTGT_A | REEC_D | Closed | 33 | -43.39 | W3 | 139.56 |  | NO | 0.065 | 0.26 | 0 |  |  |  | NAN | 0.69 |  | Not_In_WSM | W3 (Wind Turbine, Type 3) | W2
70 | PSCOLORADO | 65 | PSColorado |  | 70777 | C3 | C3 | [5 empty] | At Mvar Limit | [13 empty] | 493 | 804.9 | -74.1 | 94.9 | 65 | 50.1 | 855 |  | GENROU | IEEEST | IEEEG1_GE | ESST1A_GE | Closed | 780 | 94.9 | CA | 1008 |  | NO | 0.002 | 0.266 | 3.91 | 39.4128 | 0.199 | 0.633 | 3.1809 | 27 |  | COMA_24_ | CA (Combined Cycle Steam Part) | C3
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70824 | W2 | W2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 80 | -65.699 | 65.699 | 65 | -80 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 20 | -4.1016 | W3 | 84.21 | PF<0.8 | NO | 0 | 0.8 | 0 |  |  |  | NAN | 34.5 |  | CEDARCK_34.5_WIND_UN3 | W3 (Wind Turbine, Type 3) | W2 |  | PSS Exempt
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70933 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 30.965 | -21.679 | 21.679 | 65 | -30.965 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | P3 | 37.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | P3 (Photovoltaic, Fixed) | S1 |  | PSS Exempt
70 | PSCOLORADO | 65 | PSColorado |  | 70951 | G6 | G6 | [5 empty] | At Mvar Limit | [13 empty] | 63.9 | 154.5 | -7.9 | 48.4 | 65 | -2.5 | 152 |  | GENQEC | PSS2B | GGOV1 | ESST4B | Closed | 150 | 48.4 | GT | 165 |  | NO | 0 | 0.141 | 6.85 | 11.3025 |  |  | NAN | 18 |  | FSVR_18_NO_6 | GT (Gas Turbine) | G6
70 | PSCOLORADO | 73 | Tri-State G&T |  | 70994 | PV | PV | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 100.2 | -58.7 | 58.7 | 65 | -100.2 |  |  | REGC_A |  |  | REEC_A | Closed | 95.2 | -7.4695 | UN | 115 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.62 |  |  | UN (Unknown) | PV
70 | PSCOLORADO | 66 | West Plains G&T |  | 71003 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 | REXS | Closed | 36 | 0.52211 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT41 | JE (Jet Engine) | G1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71003 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 | REXS | Closed | 36 | 0.52211 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT42 | JE (Jet Engine) | G2
70 | PSCOLORADO | 66 | West Plains G&T |  | 71004 | G1 | G1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 |  | Closed | 36 | 0.51318 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT51 | JE (Jet Engine) | G1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71004 | G2 | G2 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 |  | Closed | 36 | 0.51318 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT52 | JE (Jet Engine) | G2
70 | PSCOLORADO | 66 | West Plains G&T |  | 71004 | S1 | S1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 24.8 | -4.7 | 15.6 | 65 | -24.8 |  |  | GENROU | PSS2B |  |  | Closed | 20 | 0.51318 | CC | 29.53 |  | NO | 0.002 | 0.35 | 5.52 | 1.6301 | 0.132 | 0.439 | 3.3258 | 13.8 |  | BACUMESA_13.8_ST5 | CC (Combined Cycle Generic) | S1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71005 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 40 | -25 | 25 | 65 | 0.32 | 40.32 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 71.176 | PF<-0.85 | NO | 0.005 | 0.175 | 1.1 | 0.78294 | 0.075 | 0.26 | 3.4667 | 13.8 |  | BACUMESA_13.8_CT6 | JE (Jet Engine) | G1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71009 | W1 | W1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 28.8 | -13.92 | 9.44 | 65 | -28.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.9 | -0.82545 | W3 | 32 |  | NO | 0 | 0.173 | 0 |  |  |  | NAN | 0.7 |  |  | W3 (Wind Turbine, Type 3) | W1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71016 | W1 | W1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 60 | -27.2 | 27.2 | 65 | -60 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 22.8 | -7.1788 | W3 | 64.2 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.7 |  |  | W3 (Wind Turbine, Type 3) | W1
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72004 | W1 | W1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 145 | -47.7 | 47.7 | 26 | -145 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 100 | -28.0377 | UN | 149.3 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.7 |  |  | UN (Unknown) | W1
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72021 | PV | PV |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [8 empty] | Miss Turbine Type |  |  |  |  | 2 | 13 | 0 | 8.7 | 26 | -13 |  |  | REGC_A |  |  | REEC_B | Closed | 13 | 8.7 | UN | 20 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.2 |  |  | UN (Unknown) | PV
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72023 | PV | PV | [12 empty] | Gen on HV |  | Miss Turbine Type |  |  |  |  | 1 | 16 | -2 | 2 | 26 | -16 |  |  | REGC_A |  |  | REEC_A | Closed | 16 | 1.6616 | UN | 16.725 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | UN (Unknown) | PV
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72714 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 2.4 | 51.2 | -16.7 | 16.7 | 26 | -51.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 10.4 | -16.7 | W3 | 56.8 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1
73 | WAPA R.M. | 606 | EDP Renewables |  | 72719 | W | W | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 3.5 | 104.2 | -42.4 | 38.3 | 26 | -104.2 |  |  | REGC_A |  |  | REEC_A | Closed | 21 | -17.1615 | UN | 115 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | UN (Unknown) | W
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72724 | PV | PV | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 150.2 | -57.3 | 57.3 | 26 | -150.2 |  |  | REGC_A |  |  | REEC_A | Closed | 138 | 14.9198 | UN | 157 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | UN (Unknown) | PV
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72729 | PV | PV | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 110.2 | -43.5 | 43.5 | 26 | -110.2 |  |  | REGC_A |  |  | REEC_A | Closed | 104.7 | -12.6503 | UN | 118 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | UN (Unknown) | PV
73 | WAPA R.M. | 451 | NextEra Energy |  | 72739 | W | W | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 200.2 | -97.4 | 62.5 | 26 | -200.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 40.2 | -25.3623 | UN | 221.6 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | UN (Unknown) | W
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72739 | W1 | W1 | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 200 | -75 | 75 | 26 | -200 | [6 empty] | Open | 0 | 0 | UN | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | UN (Unknown) | W1
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72742 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 7.4 | -2.4 | 2.4 | 26 | -7.4 | [6 empty] | Closed | 7.4 | -0.000419 | HY | 8 |  | NO | 0 | 0.179 | 0 |  |  |  | NAN | 4.2 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72742 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 0.8 | -0.3 | 0.3 | 26 | -0.8 | [6 empty] | Closed | 0.8 | -0.000419 | HY | 0.9 |  | NO | 0 | 0.221 | 0 |  |  |  | NAN | 4.2 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73226 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 0 | 75.657 | -33.056 | 42.5 | 26 | -8.144 | 67.513 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 65 | 15.1803 | HY | 75.657 |  | NO | 0.004 | 0.227 | 2.57 | 1.9444 | 0.05 | 0.35 | 7 | 13.8 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73306 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15.7 | -11.5 | 11.098 | 26 | 4.4 | 20.1 |  | GENTPJ |  | HYGOV4 | ESST6B | Closed | 15 | 8.5979 | HY | 19.2 | PF<-0.85 | NO | 0.003 | 0.19 | 3 | 0.576 | 0.0732 | 0.2745 | 3.75 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73307 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15.7 | -11.5 | 11.098 | 26 | 4.4 | 20.1 |  | GENTPJ |  | HYGOV4 | ESST6B | Closed | 15 | 8.4309 | HY | 19.2 | PF<-0.85 | NO | 0.003 | 0.19 | 3 | 0.576 | 0.0575 | 0.274 | 4.7652 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73308 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15.7 | -11.5 | 11.098 | 26 | 4.4 | 20.1 |  | GENTPJ |  | HYGOV4 | ESST6B | Closed | 15 | 8.4309 | HY | 19.2 | PF<-0.85 | NO | 0.003 | 0.19 | 3 | 0.576 | 0.0525 | 0.2388 | 4.5486 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73316 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 14.444 | -10 | 9.016 | 26 | -1.444 | 13 |  | GENTPJ |  | HYGOV4 |  | Closed | 11.5 | 1.7925 | HY | 14.444 | PF<-0.85 | NO | 0.005 | 0.3 | 2.197 | 0.31733 | 0.05 | 0.24 | 4.8 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73317 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 14.444 | -10 | 9.016 | 26 | -0.944 | 13.5 |  | GENTPJ |  | HYGOV4 |  | Closed | 13 | 1.7925 | HY | 14.444 | PF<-0.85 | NO | 0.005 | 0.3 | 2.197 | 0.31733 | 0.05 | 0.24 | 4.8 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73324 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 37.8 | -25 | 21.49 | 26 | -1.8 | 36 |  | GENTPJ | PSS2C | HYGOV4 | ST6C | Closed | 34.5 | 3.5761 | HY | 40.25 | PF<-0.85 | NO | 0.002 | 0.21 | 2.66 | 1.0707 | 0.11 | 0.46 | 4.1818 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73333 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7.5 | -2.1 | 4.4 | 26 | -3e-07 | 7.5 |  | GENTPJ |  | HYGOV4 |  | Closed | 7 | -2.1 | HY | 8.333 |  | NO | 0.005 | 0.227 | 2.25 | 0.18749 | 0.13 | 0.43 | 3.3077 | 4.2 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73333 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7.5 | -2.5 | 4.4 | 26 | -3e-07 | 7.5 |  | GENTPJ |  | HYGOV4 |  | Closed | 7 | -2.5 | HY | 8.333 |  | NO | 0.005 | 0.227 | 2.25 | 0.18749 | 0.13 | 0.43 | 3.3077 | 4.2 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 95 | CSU |  | 73381 | G1 | G1 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 5 | 18 | -10.4 | 14.2 | 26 | -0.353 | 17.647 |  | GENTPJ |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | UN | 17.647 | PF<0.8 | NO | 0.002 | 0.18 | 4.5 | 0.79411 | 0.05 | 0.3 | 6 | 13.8 |  |  | UN (Unknown) | G1
73 | WAPA R.M. | 95 | CSU |  | 73382 | G2 | G2 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 5 | 18 | -10.4 | 14.2 | 26 | -0.353 | 17.647 |  | GENTPJ |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | UN | 17.647 | PF<0.8 | NO | 0.002 | 0.18 | 4.5 | 0.79411 | 0.05 | 0.3 | 6 | 13.8 |  |  | UN (Unknown) | G2
73 | WAPA R.M. | 95 | CSU |  | 73383 | G3 | G3 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 6 | 23 | -14.3 | 20 | 26 | 4.059 | 27.059 |  | GENTPJ |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | UN | 27.059 | PF<0.8 | NO | 0.002 | 0.18 | 4.5 | 1.2177 | 0.05 | 0.3 | 6 | 13.8 |  |  | UN (Unknown) | G3
73 | WAPA R.M. | 95 | CSU |  | 73418 | C1 | C1 | [14 empty] | Miss Turbine Type |  |  |  |  | 110.7 | 225 | -3.52 | 45.43 | 26 | 5 | 230 |  | GENTPJ | PSS2B | IEEEG1_GE | ESST4B | Closed | 213.4 | 36.2273 | UN | 230 |  | NO | 0.002 | 0.15 | 3.1645 | 7.2783 | 0.123 | 0.5208 | 4.2341 | 20 |  |  | UN (Unknown) | C1
73 | WAPA R.M. | 95 | CSU |  | 73424 | H1 | H1 | [5 empty] | At Mvar Limit | [8 empty] | Miss Turbine Type |  |  |  |  | 0.5 | 28 | -5 | 3 | 26 | 0.5 | 28.5 |  | GENTPJ |  | HYGOV | ESST1A_GE | Closed | 24.2 | -5 | UN | 28 |  | NO | 0.003 | 0.23 | 3 | 0.84 | 0.15 | 0.45 | 3 | 13.8 |  |  | UN (Unknown) | H1
73 | WAPA R.M. | 95 | CSU |  | 73434 | G1 | G1 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  | Missing PS |  |  | 19.8 | 27 | -10.2 | 23.7 | 26 | -27 | [6 empty] | Open | 0 | 0 | UN | 41 | PF<0.8 | NO | 0.002 | 0.2 | 0 |  |  |  | NAN | 12.5 |  |  | UN (Unknown) | G1
73 | WAPA R.M. | 95 | CSU |  | 73435 | G1 | G1 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  | Missing PS |  |  | 19.8 | 27 | -7.5 | 22.2 | 26 | -27 | [6 empty] | Open | 0 | 0 | UN | 41 | PF<0.8 | NO | 0.002 | 0.2 | 0 |  |  |  | NAN | 12.5 |  |  | UN (Unknown) | G1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73438 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 19.8 | -12.5 | 11.8 | 26 | 1.2 | 21 |  | GENTPJ | PSS2A | HYGOV4 | ST4C | Closed | 19 | -1.5178 | HY | 21.8 | PF<-0.85 | NO | 0.004 | 0.35 | 2.57 | 0.56026 | 0.09 | 0.61 | 6.7778 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73444 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 3.2 | 0 | 1.8 | 26 | 0.5 | 3.7 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 3 | 1.428 | HY | 3.2 |  | NO | 0.004 | 0.168 | 2.1 | 0.0672 | 0.23 | 0.48 | 2.087 | 2.4 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 95 | CSU |  | 73507 | G1 | G1 | [14 empty] | Miss Turbine Type |  |  |  |  | 55 | 140.5 | -41 | 63 | 26 | 33.5 | 174 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 139.8 | 54.63 | UN | 181 |  | NO | 0.001 | 0.12 | 4.785 | 8.6608 | 0.0575 | 0.4411 | 7.6713 | 18 |  |  | UN (Unknown) | G1
73 | WAPA R.M. | 95 | CSU |  | 73508 | G2 | G2 | [14 empty] | Miss Turbine Type |  |  |  |  | 55 | 141.3 | -42 | 59 | 26 | 32.7 | 174 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 137 | 54.2918 | UN | 181 |  | NO | 0.001 | 0.12 | 4.785 | 8.6608 | 0.0575 | 0.4411 | 7.6713 | 18 |  |  | UN (Unknown) | G2
73 | WAPA R.M. | 95 | CSU |  | 73509 | ST | ST | [10 empty] | Unreas Sat |  |  |  | Miss Turbine Type |  |  |  |  | 37 | 208.2 | -48 | 132 | 26 | -208.2 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 207.7 | 79.6447 | UN | 274.5 |  | NO | 0.001 | 0.12 | 4 | 10.98 | 0.04 | 0.111 | 2.775 | 21 |  |  | UN (Unknown) | ST
73 | WAPA R.M. | 773 | Colorado Highland Wind, LLC |  | 73631 | W | W |  |  |  | Unapproved Gen Model | [15 empty] | 12.3 | 67.1 | -32.6 | 32.6 | 26 | -67.1 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 13.5 | 4.827 | W3 | 70.14 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | W |  | PSS Exempt
73 | WAPA R.M. | 773 | Colorado Highland Wind, LLC |  | 73635 | W | W |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 23.1 | -10.4 | 10.4 | 26 | -23.1 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 4.7 | 3.3164 | W3 | 26.18 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | W |  | PSS Exempt
73 | WAPA R.M. | 700 | Non Utility Owned - PSCO Area |  | 73719 | S1 | S1 | [15 empty] | Missing Model |  |  |  | 0 | 175 | -40 | 40 | 26 | -175 | [6 empty] | Closed | 96.3 | -5.2443 | P4 | 175 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.6 |  |  | P4 (Photovoltaic, Tracking) | S1
73 | WAPA R.M. | 700 | Non Utility Owned - PSCO Area |  | 73721 | S1 | S1 | [15 empty] | Missing Model |  |  |  | 0 | 60 | -30 | 30 | 26 | -60 | [6 empty] | Closed | 33 | -3.0991 | P4 | 60 |  | NO | 0.009 | 999 | 0 |  |  |  | NAN | 0.6 |  |  | P4 (Photovoltaic, Tracking) | S1
73 | WAPA R.M. | 95 | CSU |  | 73729 | G1 | G1 | [7 empty] | PSS No Ex | [11 empty] | 5 | 25 | -6 | 13 | 26 | 12 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 8.5488 | JE | 28 |  | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 95 | CSU |  | 73729 | G2 | G2 | [7 empty] | PSS No Ex | [11 empty] | 5 | 25 | -6 | 13 | 26 | 12 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 8.5488 | JE | 28 |  | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G2
73 | WAPA R.M. | 95 | CSU |  | 73729 | G3 | G3 | [7 empty] | PSS No Ex | [11 empty] | 5 | 25 | -6 | 13 | 26 | 12 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 8.5488 | JE | 28 |  | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G3
73 | WAPA R.M. | 95 | CSU |  | 73730 | G1 | G1 | [7 empty] | PSS No Ex | [11 empty] | 5 | 25 | -6 | 13 | 26 | 12 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 16 | 10.0222 | JE | 28 |  | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 95 | CSU |  | 73730 | G2 | G2 | [7 empty] | PSS No Ex | [11 empty] | 5 | 25 | -6 | 13 | 26 | 12 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 13 | 10.0222 | JE | 28 |  | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G2
73 | WAPA R.M. | 95 | CSU |  | 73730 | G3 | G3 | [7 empty] | PSS No Ex | [11 empty] | 5 | 25 | -6 | 13 | 26 | 12 | 37 |  | GENROU | PSS2B | GGOV1 |  | Open | 0 | 0 | JE | 28 |  | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G3
73 | WAPA R.M. | 60 | Black Hills |  | 74017 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 65 | 100 | -7.7 | 8.3 | 26 | -100 |  |  | GENTPJ | PSS2B |  | EXST4B | Closed | 100 | 8.3 | ST | 118.9 |  | NO | 0.001 | 0.199 | 3.94 | 4.6847 | 0.073 | 0.391 | 5.3562 | 13.8 |  |  | ST (Steam Turbine) | 1
73 | WAPA R.M. | 60 | Black Hills |  | 74061 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -24 | 39 | 26 | 6 | 46 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 30 | 3.6138 | JE | 71.176 | PF<0.8 | NO | 0.001 | 0.15 | 1.244 | 0.88543 | 0.128 | 0.351 | 2.7422 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 60 | Black Hills |  | 74061 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -24 | 39 | 26 | 6 | 46 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 30 | 3.6138 | JE | 71.18 | PF<0.8 | NO | 0.001 | 0.15 | 1.244 | 0.88548 | 0.128 | 0.351 | 2.7422 | 13.8 |  |  | JE (Jet Engine) | G2
73 | WAPA R.M. | 60 | Black Hills |  | 74062 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -24 | 39 | 26 | 6 | 46 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 71.176 | PF<0.8 | NO | 0.001 | 0.15 | 1.244 | 0.88543 | 0.128 | 0.351 | 2.7422 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 60 | Black Hills |  | 74716 | PV | PV | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 162 | -121.5 | 121.5 | 26 | -162 |  |  | REGC_A |  |  | REEC_A | Closed | 150 | -15.409 | UN | 162 | PF<0.8 | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.6 |  |  | UN (Unknown) | PV
73 | WAPA R.M. | 94 | Basin Electric Power Coop. |  | 76313 | FD | FD | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 0 | 0 | -16 | 16 | 26 | 0 | [6 empty] | Open | 0 | 0 | UN | 16 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.5 |  |  | UN (Unknown) | FD
73 | WAPA R.M. | 94 | Basin Electric Power Coop. |  | 76314 | FD | FD | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 0 | 0 | -20 | 20 | 26 | 0 | [6 empty] | Open | 0 | 0 | UN | 20 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.5 |  |  | UN (Unknown) | FD
73 | WAPA R.M. | 94 | Basin Electric Power Coop. |  | 76351 | 1 | 1 |  |  |  |  | Exceed Gen Limit | At Mvar Limit | [13 empty] | 0 | 200 | -10 | 10 | 26 | -200 | [6 empty] | Closed | -130 | 10 | DC | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 230 | BES Exempt |  | DC (Represents DC ties) | 1 | Netting Exempt | PSS Exempt
73 | WAPA R.M. | 73 | Tri-State G&T |  | 79015 | 1 | 1 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact |  |  |  |  | Gen at 0.0 | [7 empty] | 152.3 | 470 | -111.2 | 470 | 26 | -470 |  |  | GENTPJ | PSS2B |  | EXST4B | Closed | 0 | 36.868 | ST | 496 | PF<0.8 | NO | 0 | 0.203 | 2.6 | 12.896 | 0.15 | 0.485 | 3.2333 | 22 |  |  | ST (Steam Turbine) | 1
73 | WAPA R.M. | 73 | Tri-State G&T |  | 79016 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 151 | 470 | -98.5 | 470 | 26 | -470 |  |  | GENTPJ | PSS2B |  | EXST4B | Closed | 250 | 36.8681 | ST | 496 | PF<0.8 | NO | 0 | 0.203 | 2.6 | 12.896 | 0.15 | 0.485 | 3.2333 | 22 |  |  | ST (Steam Turbine) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79019 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 81 | -56 | 59 | 26 | -2.4e-07 | 81 |  | GENQEC | PSS2C | HYGOVR | ST4C | Closed | 80 | -7.7448 | HY | 96.297 | PF<-0.85 | NO | 0.008 | 0.3 | 1.84 | 1.7719 |  |  | NAN | 12.5 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79019 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 81 | -56 | 59 | 26 | -2.4e-07 | 81 |  | GENQEC | PSS2C | HYGOVR | ST4C | Closed | 80 | -7.7448 | HY | 96.297 | PF<-0.85 | NO | 0.008 | 0.3 | 1.84 | 1.7719 |  |  | NAN | 12.5 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 65 | PSColorado |  | 79041 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 125 | 285 | -70 | 110 | 26 | 9.54e-06 | 285 |  | GENTPJ | PSS2A | IEEEG1_GE | REXS | Closed | 280 | -70 | ST | 306 |  | NO | 0.003 | 0.27 | 3.7 | 11.322 | 0.16 | 0.61 | 3.8125 | 22 |  |  | ST (Steam Turbine) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79164 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 12.1 | -6 | 6.13 | 26 | -0.4 | 11.7 |  | GENTPJ | PFQRG | HYG3 | ESST4B | Closed | 11.5 | -1.8099 | HY | 12.1 |  | NO | 0.004 | 0.22 | 1.6 | 0.1936 | 0.07 | 0.31 | 4.4286 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79166 | 1 | 1 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 4.9 | -1.2 | 2.3 | 26 | 0.77 | 5.67 |  | GENTPJ | PSS2B | HYGOVR |  | Closed | 4 | 0.89256 | HY | 6.2 |  | NO | 0.003 | 0.192 | 1.52 | 0.09424 | 0.1842 | 0.4949 | 2.6868 | 4.2 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79172 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 8.6 | -2 | 4.1 | 26 | -8.6 |  |  | GENTPJ | PSS2B |  |  | Closed | 8 | 1.2986 | HY | 11 |  | NO | 0.003 | 0.24 | 1.45 | 0.1595 | 0.0762 | 0.3248 | 4.2625 | 4.2 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79176 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 1.3 | 0 | 0 | 26 | -1.3 |  |  | GENTPJ | PFQRG |  | ESST6B | Closed | 1 | 0 | HY | 1.35 |  | NO | 0.009 | 0.23 | 0.9 | 0.01215 | 0.05 | 0.39 | 7.8 | 2.4 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79612 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20 | -1.78 | 17.02 | 26 | 51.2 | 71.2 |  | GENTPJ | PSS2A | GGOV1 | ESAC6A | Closed | 20 | 10.7555 | CC | 32.5 | PF<0.8 | NO | 0.002 | 0.15 | 4.45 | 1.4462 | 0.1476 | 0.3251 | 2.2026 | 13.8 |  |  | CC (Combined Cycle Generic) | 2
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79639 | 1 | 1 | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 30 | -2 | 2 | 26 | -30 | [6 empty] | Open | 0 | 0 | UN | 30 |  | NO | 0 | 0.077 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79640 | 1 | 1 | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 30 | -2 | 2 | 26 | -30 | [6 empty] | Open | 0 | 0 | UN | 30 |  | NO | 0 | 0.077 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79642 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16 | -3 | 3 | 26 | 0.8 | 16.8 |  | GENTPJ |  | HYGOV | EXST1_GE | Closed | 14 | 2.0969 | HY | 16.8 |  | NO | 0 | 0.171 | 3.6 | 0.6048 | 0.187 | 0.539 | 2.8824 | 13.8 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79642 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16 | -3 | 3 | 26 | 0.8 | 16.8 |  | GENTPJ |  | HYGOV | EXST1_GE | Open | 0 | 0 | HY | 16.8 |  | NO | 0 | 0.171 | 3.6 | 0.6048 | 0.187 | 0.539 | 2.8824 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80000 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -0.58 | 0.81 | 10 | -4 |  |  | GENROU |  |  |  | Open | 0 | 0 | HY | 1.968 |  | NO | 0 | 0.13 | 2.49 | 0.049003 | 0.077 | 0.196 | 2.5455 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80130 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.8 | -1.2 | 1.2 | 10 | -1.8 |  |  | GENROU |  |  |  | Closed | 1.688 | 0.13042 | ST | 2 | PF<-0.85 | NO | 0 | 0.14 | 2.49 | 0.0498 | 0.077 | 0.196 | 2.5455 | 0.6 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80159 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.8 | -1.2 | 1.2 | 10 | -1.8 |  |  | GENROU |  |  |  | Open | 0 | 0 | ST | 2 | PF<-0.85 | NO | 0 | 0.14 | 2.49 | 0.0498 | 0.077 | 0.196 | 2.5455 | 0.6 |  |  | ST (Steam Turbine) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80365 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 13.6 | -7 | 8.4 | 10 | 0.4 | 14 |  | GENQEC | PSS2C | HYG3 |  | Closed | 12.772 | 3.567 | HY | 16 |  | NO | 0.006 | 0.243 | 1.45 | 0.232 |  |  | NAN | 6.6 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80375 | 13 | 13 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 12 | -16.8 | 16.8 | 10 | -12 | [6 empty] | Open | 0 | 0 | CC | 31.93 | PF<0.8 | NO | 0.002 | 0.14 | 0 |  |  |  | NAN | 13.8 |  |  | CC (Combined Cycle Generic) | 13
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 8.583 | 0.080739 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 8.583 | 0.080739 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 8.583 | 0.080739 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 8.583 | 0.080739 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 4
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80389 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 3.285 | -1.47 | 1.87 | 10 | 0.365 | 3.65 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 2.741 | 0.32939 | HY | 3.65 |  | NO | 0 | 0.185 | 0.88 | 0.03212 | 0.06 | 0.29 | 4.8333 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80389 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7.76 | -3.21 | 3.51 | 10 | 0.862 | 8.622 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 6.474 | 0.32939 | HY | 8.622 |  | NO | 0 | 0.25 | 1.17 | 0.10088 | 0.038 | 0.155 | 4.0789 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80389 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7.76 | -3.25 | 3.6 | 10 | 0.862 | 8.622 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 6.474 | 0.32939 | HY | 8.622 |  | NO | 0 | 0.25 | 1.17 | 0.10088 | 0.038 | 0.155 | 4.0789 | 6.9 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80394 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 0.56 | -0.27 | 0.27 | 10 | -0.56 | [6 empty] | Closed | 0.5 | 0 | HY | 0.62 |  | NO | 0 | 0.13 | 0 |  |  |  | NAN | 0.6 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80416 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.08 | -4.84 | 4.84 | 10 | 0.02 | 10.1 |  | GENTPJ |  | G2WSCC | EXAC8B | Closed | 8.326 | 0.21264 | HY | 11.2 |  | NO | 0 | 0.225 | 1.06 | 0.11872 | 0.3 | 0.95 | 3.1667 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80416 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.68 | -1.9 | 1.9 | 10 | 0.02 | 4.7 |  | GENTPJ |  | G2WSCC | EXAC8B | Closed | 3.866 | 0.21264 | HY | 5.2 |  | NO | 0 | 0.261 | 1.06 | 0.05512 | 0.3 | 0.95 | 3.1667 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80440 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.5 | -3.53 | 3.92 | 10 | -1.5 | 9 |  | GENROU |  | IEEEG1_GE | EXAC8B | Closed | 8 | -0.31369 | ST | 9 |  | NO | 0.004 | 0.195 | 1.61 | 0.1449 | 0.05 | 0.125 | 2.5 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80507 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 25.5 | -8.8 | 12.3 | 10 | 2.82 | 28.32 |  | GENTPJ |  | HYGOV | EXAC8B | Closed | 21.594 | 3.1839 | HY | 28.32 |  | NO | 0 | 0.2 | 1.38 | 0.39082 | 0.2 | 0.7 | 3.5 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80534 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 7.74 | -3.75 | 3.75 | 10 | 1.1e-07 | 7.74 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 6.499 | -1.2331 | HY | 8.6 |  | NO | 0 | 0.29 | 0.7401 | 0.063649 | 0.03 | 0.2 | 6.6667 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80535 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 8.28 | -4.01 | 4.01 | 10 | -9e-08 | 8.28 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 6.953 | -1.2547 | HY | 9.2 |  | NO | 0 | 0.13 | 0.97 | 0.08924 | 0.1398 | 0.3403 | 2.4342 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80536 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 9.72 | -4.71 | 4.71 | 10 | -6.2e-07 | 9.72 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 8.162 | -1.87 | HY | 10.8 |  | NO | 0 | 0.16 | 0.64 | 0.06912 | 0.25 | 0.4 | 1.6 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80536 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 9.72 | -4.71 | 4.71 | 10 | -6.2e-07 | 9.72 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 8.162 | -1.87 | HY | 10.8 |  | NO | 0 | 0.16 | 0.64 | 0.06912 | 0.25 | 0.4 | 1.6 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80585 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 25 | -8.53 | 11.71 | 10 | 2.778 | 27.778 |  | GENTPJ |  | IEEEG1_GE | REXS | Open | 0 | 0 | CC | 27.778 |  | NO | 0 | 0.22 | 3.35 | 0.93056 | 0.19 | 0.52 | 2.7368 | 13.8 |  |  | CC (Combined Cycle Generic) | 4
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 80587 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 19.55 | -12.11 | 12.11 | 10 | -19.55 |  |  | GENROU |  |  |  | Open | 0 | 0 | ST | 23 |  | NO | 0 | 0.18 | 1.2 | 0.276 | 0.05 | 0.3 | 6 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80620 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -2.28 | 3 | 10 | 1 | 5 |  | GENTPJ |  | HYGOV |  | Closed | 3.318 | -0.40601 | HY | 5 |  | NO | 0 | 0.142 | 4.45 | 0.2225 | 0.337 | 0.982 | 2.9139 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80657 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 62.5 | -21.7 | 30.2 | 10 | -62.5 |  |  | GENROU |  |  | REXS | Open | 0 | 0 | ST | 69.444 |  | NO | 0 | 0.221 | 2.3 | 1.5972 | 0.05 | 0.19 | 3.8 | 13.8 |  |  | ST (Steam Turbine) | 1 |  | PSS Exempt
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80730 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 8.9 | -4.25 | 4.25 | 10 | 0.86 | 9.76 |  | GENTPJ | PSS2B | HYG3 | ESST1A_GE | Closed | 7.242 | -0.12172 | HY | 9.76 |  | NO | 0 | 0.212 | 0.8 | 0.07808 | 0.1 | 0.22 | 2.2 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80730 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 8.9 | -4.25 | 4.25 | 10 | 0.86 | 9.76 |  | GENTPJ | PSS2B | HYG3 | ESST1A_GE | Closed | 7.242 | -0.12172 | HY | 9.76 |  | NO | 0 | 0.212 | 0.8 | 0.07808 | 0.1 | 0.22 | 2.2 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80750 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.48 | -1.8 | 3.2 | 10 | -6.48 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 6.204 | 0.4885 | ST | 7.2 |  | NO | 0 | 0.128 | 2 | 0.144 | 0.07 | 0.16 | 2.2857 | 4.16 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80750 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.48 | -1.8 | 3.2 | 10 | -6.48 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 6.204 | 0.4885 | CC | 7.2 |  | NO | 0 | 0.128 | 2 | 0.144 | 0.07 | 0.16 | 2.2857 | 4.16 |  |  | CC (Combined Cycle Generic) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80902 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6 | -2.082 | 2.906 | 10 | -6 |  |  | GENTPJ |  |  | EXAC8B | Closed | 4.91 | -1.8563 | HY | 6.7 |  | NO | 0 | 0.216 | 1.89 | 0.12663 | 0.07 | 0.18 | 2.5714 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 81014 | C | C | [6 empty] | Limit Power Fact | [12 empty] | 0 | 32 | -23 | 23 | 10 | -32 |  |  | GENROU | PSS2A |  | EXAC8B | Open | 0 | 0 | CC | 38.4 | PF<-0.85 | NO | 0 | 0.13 | 3.3 | 1.2672 | 0.097 | 0.487 | 5.0206 | 13.8 |  |  | CC (Combined Cycle Generic) | C
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 81127 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 3.2 | -1.55 | 1.55 | 10 | -3.2 |  |  | GENTPJ |  |  | EXAC8B | Closed | 2.718 | -0.63539 | HY | 3.56 |  | NO | 0 | 0.16 | 0.75 | 0.0267 | 0.1 | 0.4 | 4 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 81130 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 43 | -18.7 | 18.7 | 10 | -43 |  |  | GENROU |  |  | EXST4B | Open | 0 | 0 | ST | 43 |  | NO | 0 | 0.22 | 2.02 | 0.8686 | 0.095 | 0.362 | 3.8105 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 81143 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15 | -12 | 12 | 10 | -15 |  |  | REGC_A |  |  | REEC_A | Closed | 12.95 | -0.027439 | W3 | 15 | PF<0.8 | NO | 0 | 0.674 | 0 |  |  |  | NAN | 0.4 |  |  | W3 (Wind Turbine, Type 3) | 1
14 | APS | 2 | Arizona Public Service |  | 85393 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 6.4 | -2.1 | 2.1 | 2 | -6.4 | [6 empty] | Closed | 2.6 | -0.48676 | IC | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 12.47 |  | WASTEMGT_12.47_BIOGAS | IC (Internal Combustion) | 1
14 | APS | 2 | Arizona Public Service |  | 85647 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 19.9 | 0 | 0 | 2 | -19.9 | [6 empty] | Closed | 15 | 0 | P4 | 19.9 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.36 |  | CHVLYSLR_0.36 | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85650 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -0.81223 | -0.81223 | 2 | -15 | [6 empty] | Closed | 12 | -0.81223 | P4 | 15 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 12.5 |  | BAGDAD_SOLAR_12.5_PV | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85771 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -0.20306 | -0.20306 | 2 | -15 | [6 empty] | Closed | 14 | -0.20306 | P4 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.48 |  | GILSPIE_0.48_PV_U1 | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85775 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | 0 | 0 | 2 | -15 | [6 empty] | Closed | 12 | 0 | P4 | 15 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.3 |  | SADDLEMOUNTAIN_0.3_PV | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85781 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -0.20306 | 0.20306 | 2 | -15 | [6 empty] | Closed | 12 | 0 | P4 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.69 |  | BADGER_.69_PV | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85792 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 4.5 | -0.31225 | -0.31225 | 2 | -4.5 | [6 empty] | Closed | 2.7 | -0.31225 | P4 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 12.47 |  | DARBY_12.47 | P4 (Photovoltaic, Tracking) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 150003 | ES | ES | [15 empty] | Missing Model |  |  |  | -25 | 25 | 0 | 0 | 80 | -25 | [6 empty] | Closed | 25 | 0 | BA | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.5 |  | SRP_Q46_12.5_SOLAR | BA (Energy Storage, Battery) | ES
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 150029 | PV | PV | [6 empty] | Limit Power Fact | [12 empty] | 0 | 68.4 | -43.2 | 43.2 | 80 | -68.4 |  |  | REGC_A |  |  |  | Closed | 67 | 1.8976 | PV | 71.99 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.63 |  | ANPP HVS_Q24 PV | PV (Photovoltaic) | PV
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 150030 | ST | ST | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | [7 empty] | -79.75 | 79.75 | -50.38 | 50.38 | 80 | -79.75 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 9.2123 | BA | 57.75 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | ANPP HVS_Q24 Batt | BA (Energy Storage, Battery) | ST
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 150034 | PV | PV | [6 empty] | Limit Power Fact | [12 empty] | 0 | 167.58 | -105.84 | 105.84 | 80 | -167.58 |  |  | REGC_A |  |  |  | Closed | 154 | 5.2469 | PV | 162.89 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.63 |  | ANPP HVS_Q25 PV | PV (Photovoltaic) | PV
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 150035 | ST | ST | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | [7 empty] | -188 | 188.22 | -118.89 | 118.89 | 80 | -188.22 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 21.9045 | BA | 183.645 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | ANPP HVS_Q25 Batt | BA (Energy Storage, Battery) | ST
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 151495 | S2 | S2 | [6 empty] | Limit Power Fact | [12 empty] | -153 | 157.75 | -123.46 | 123.46 | 80 | -157.75 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 205.76 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | HVQ27_T42_ES2 | BA (Energy Storage, Battery) | S2
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 151545 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | -153 | 157.75 | -123.46 | 123.46 | 80 | -157.75 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 205.76 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | HVQ27_T41_ES1 | BA (Energy Storage, Battery) | S1
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP [Bus] | 151620 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | -86.5 | 90 | -71.15 | 71.15 | 80 | -90 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 118.57 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | HVQ27_T1_BES_1 | BA (Energy Storage, Battery) | S1
15 | SRP | 801 | NON SRP Owned - other | SRP [Bus] | 154727 | 1 | 1 | [11 empty] | Gen at 0.0 | [5 empty] | Missing Sub R/X |  | -89.2 | 89.2 | -44.73 | 44.73 | 80 | -89.2 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | -1.9525 | BA | 101.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | SRP_Q55-BESS | BA (Energy Storage, Battery) | 1
15 | SRP | 801 | NON SRP Owned - other | SRP [Bus] | 154828 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 50.8 | -16.943 | 16.943 | 80 | -50.8 |  |  | REGC_A |  |  | REEC_A | Closed | 50 | -4.7711 | P4 | 53.551 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | PVPC_Q07 PV1 | P4 (Photovoltaic, Tracking) | 1
15 | SRP | 801 | NON SRP Owned - other | SRP [Bus] | 155449 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 50.8 | -16.943 | 16.943 | 80 | -50.8 |  |  | REGC_A |  |  | REEC_A | Closed | 50 | 0.9303 | P4 | 53.551 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | PVPC_Q07 PV2 | P4 (Photovoltaic, Tracking) | 2
15 | SRP | 801 | NON SRP Owned - other | SRP [Bus] | 156330 | P1 | P1 | [17 empty] | Missing Sub R/X |  | 0 | 156.3 | -94 | 94 | 80 | -156.3 |  |  | REGC_A |  |  | REEC_A | Closed | 156 | 2.0073 | PV | 172.4801 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | PVPCQ13_PV1 | PV (Photovoltaic) | P1
15 | SRP | 801 | NON SRP Owned - other | SRP [Bus] | 156334 | P2 | P2 | [17 empty] | Missing Sub R/X |  | 0 | 156.3 | -94 | 94 | 80 | -156.3 |  |  | REGC_A |  |  | REEC_A | Closed | 156 | -0.85246 | PV | 168.3735 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | PVPCQ13_PV2 | PV (Photovoltaic) | P2
15 | SRP | 80 | Salt River Project | SRP [Bus] | 156395 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 49.5 | -28.5 | 26 | 80 | 8.735 | 58.235 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 58.235 |  | NO | 0.043 | 0.148 | 1.18 | 0.68717 | 0.11 | 0.49 | 4.4545 | 13.8 |  | SRPQ98_G1 | JE (Jet Engine) | 1
15 | SRP | 80 | Salt River Project | SRP [Bus] | 156396 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 49.5 | -28.5 | 26 | 80 | 8.735 | 58.235 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 58.235 |  | NO | 0.043 | 0.148 | 1.18 | 0.68717 | 0.11 | 0.49 | 4.4545 | 13.8 |  | SRPQ98_G2 | JE (Jet Engine) | 2
15 | SRP | 137 | Sempra US Gas and Power | SRP [Bus] | 159013 | S1 | S1 | [17 empty] | Missing Sub R/X |  | 0 | 167.95 | -41.74 | 41.74 | 80 | -167.95 |  |  | REGC_A |  |  | REEC_A | Closed | 150 | -12.9819 | PV | 173.06 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | ANPP_Q02-1 | PV (Photovoltaic) | S1
15 | SRP | 137 | Sempra US Gas and Power | SRP [Bus] | 159014 | S1 | S1 | [17 empty] | Missing Sub R/X |  | 0 | 101.3 | -32.87 | 34.35 | 80 | -101.3 |  |  | REGC_A |  |  | REEC_A | Closed | 100 | -1.3224 | PV | 110 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | ANPP_Q02-2 | PV (Photovoltaic) | S1
15 | SRP | 137 | Sempra US Gas and Power | SRP [Bus] | 159015 | S1 | S1 | [17 empty] | Missing Sub R/X |  | 0 | 154 | -49.63 | 49.63 | 80 | -154 |  |  | REGC_A |  |  | REEC_A | Closed | 150 | -2.3735 | PV | 168 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | ANPP_Q02-3 | PV (Photovoltaic) | S1
15 | SRP | 801 | NON SRP Owned - other |  | 159962 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | -1510.5 | 1415.5 | -219.77 | 819.73 | 80 | -1415.5 | [6 empty] | Open | 0 | 0 | WT | 1637.9 |  | NO | 0 | 0.051 | 0 |  |  |  | NAN | 332 |  | PVPC_Q06-U1 | WT (Wind Turbine) | 1
15 | SRP | 801 | NON SRP Owned - other |  | 159963 | 2 | 2 | [12 empty] | Gen on HV | [6 empty] | -1510.5 | 1415.5 | -219.77 | 819.73 | 80 | -1415.5 | [6 empty] | Open | 0 | 0 | WT | 1637.9 |  | NO | 0 | 0.051 | 0 |  |  |  | NAN | 332 |  | PVPC_Q06-U2 | WT (Wind Turbine) | 2
16 | TEP | 79 | Tucson Electric Power |  | 160938 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 202.6 | -86.29 | 86.29 | 79 | -202.6 | [6 empty] | Closed | 200 | 86.29 | BA | 220.21 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.69 |  | Q109_0.69_BESS | BA (Energy Storage, Battery) | 1
16 | TEP | 150 | Unisource Energy Services |  | 161901 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 5 | 20 | -25 | 15 | 79 | 1 | 21 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 20 | -9.6971 | JE | 67.5 | PF<0.8 | NO | 0.004 | 0.16 | 1.3 | 0.8775 | 0.136 | 0.481 | 3.5368 | 13.2 |  | VALENTEP_13.2_GEN4 | JE (Jet Engine) | 4
16 | TEP | 150 | Unisource Energy Services |  | 162902 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 55 | -19.6 | 19.6 | 79 | -55 |  |  | REGC_A |  |  | REEC_A | Closed | 33.4 | -9.8588 | PV | 55 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | GREYHAWK_0.6_SG | PV (Photovoltaic) | 1 |  | PSS Exempt
16 | TEP | 150 | Unisource Energy Services |  | 162903 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 10.5 | -0.1 | 0.1 | 79 | -10.5 | [6 empty] | Open | 0 | 0 | W1 | 53.7 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | GRIFFITH_69_WG | W1 (Wind Turbine, Type 1) | 1 |  | PSS Exempt
16 | TEP | 150 | Unisource Energy Services |  | 162904 | 1 | 1 | [16 empty] | Missing PS |  |  | 15 | 76.94 | -25 | 32.5 | 79 | -76.94 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN1 | JE (Jet Engine) | 1
16 | TEP | 150 | Unisource Energy Services |  | 162905 | 2 | 2 | [16 empty] | Missing PS |  |  | 15 | 76.94 | -25 | 32.5 | 79 | -76.94 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN1 | JE (Jet Engine) | 2
16 | TEP | 150 | Unisource Energy Services |  | 162906 | 3 | 3 | [16 empty] | Missing PS |  |  | 15 | 76.94 | -25 | 32.5 | 79 | -76.94 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN2 | JE (Jet Engine) | 3
16 | TEP | 150 | Unisource Energy Services |  | 162907 | 4 | 4 | [16 empty] | Missing PS |  |  | 15 | 76.94 | -25 | 32.5 | 79 | -76.94 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN2 | JE (Jet Engine) | 4
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 170000 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 20 | 0 | 0 | 4 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 13.2 | 0 | P3 | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | APACHE_34.5_SOLAR | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 170001 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 4 | 40.8 | -13.9261 | 29.1609 | 4 | 7.6e-07 | 40.8 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 20 | -10.1109 | JE | 71 |  | YES | 0 | 1e-05 | 1.27 | 0.9017 | 0.116 | 0.311 | 2.681 | 13.8 |  | APACHE_GT5_13.8 | JE (Jet Engine) | 1
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 179999 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 32.5 | 0 | 0 | 4 | -32.5 |  |  | REGC_A |  |  | REEC_A | Closed | 21 | 0 | P3 | 32.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 230 | BES Exempt | CAP-AZ_230.0_SOLAR_1 | P3 (Photovoltaic, Fixed) | 1
17 | AEPCO | 1 | No owner defined |  | 179999 | 2 | 2 | [17 empty] | Missing Sub R/X | No Owner | 0 | 32.5 | 0 | 0 | 4 | -32.5 |  |  | REGC_A |  |  | REEC_A | Closed | 21 | 0 | P3 | 32.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 230 | BES Exempt | CAP-AZ_230.0_SOLAR_1 | P3 (Photovoltaic, Fixed) | 2
18 | NEVADA | 18 | N3 Nevada |  | 180655 | 3 | 3 | [9 empty] | Unreas H | [9 empty] | 113.9 | 227.925 | -92.5 | 110.3891 | 24 | -1.45e-05 | 227.925 |  | GENQEC | PSS2B | GGOV3 | ESST4B | Closed | 225.9 | 95.2264 | GT | 253.25 |  | NO | 0 | 0.17 | 1.052 | 2.6642 |  |  | NAN | 18 |  | SILVERHAPKR_18_CT3 | GT (Gas Turbine) | 3
18 | NEVADA | 18 | N3 Nevada |  | 180656 | 4 | 4 | [9 empty] | Unreas H | [9 empty] | 113.9 | 225.393 | -92 | 115.472 | 24 | -9.19e-06 | 225.393 |  | GENQEC | PSS2B | GGOV3 | ESST4B | Closed | 220.4 | 94.7099 | GT | 253.25 |  | NO | 0 | 0.17 | 1.052 | 2.6642 |  |  | NAN | 18 |  | SILVERHAPKR_18_CT4 | GT (Gas Turbine) | 4
18 | NEVADA | 18 | N3 Nevada |  | 181006 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 99 | -66 | 66 | 24 | -99 |  |  | REGC_A |  |  |  | Closed | 83.0333 | -20.8229 | PV | 110 | PF<-0.85 | NO | 1 | 10 | 0 |  |  |  | NAN | 0.385 |  | NSO_34.5_SOLAR1 | PV (Photovoltaic) | 1
18 | NEVADA | 18 | N3 Nevada |  | 181033 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | -75.24 | 75.24 | -45.14 | 45.14 | 24 | -75.24 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 75.24 |  | NO | 0.022 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HALLEN_34.5_DRYLAKEB1 | BA (Energy Storage, Battery) | 1
18 | NEVADA | 18 | N3 Nevada |  | 181036 | 2 | 2 | [11 empty] | Gen at 0.0 | [7 empty] | -75.24 | 75.24 | -45.14 | 45.14 | 24 | -75.24 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | -2.4391 | BA | 75.24 |  | NO | 0.002 | 0.022 | 0 |  |  |  | NAN | 34.5 |  | HALLEN_34.5_DRYLAKEB2 | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 74 | Southern California Edison |  | 240019 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -106.1 | 106.1 | -82.3527 | 82.3527 | 999 | -106.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 134.31 | PF<0.8 | NO | 0.01 | 0.2 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240027 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -125.46 | 125.46 | -115.308 | 115.308 | 999 | -125.46 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 172.8 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240034 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -125.46 | 125.46 | -115.308 | 115.308 | 999 | -125.46 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 170.4 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240041 | 7 | 7 | [6 empty] | Limit Power Fact | [12 empty] | -127.229 | 127.229 | -116.93 | 116.93 | 999 | -127.229 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 172.8 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 7
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240048 | 8 | 8 | [6 empty] | Limit Power Fact | [12 empty] | -127.523 | 127.523 | -116.93 | 116.93 | 999 | -127.523 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 170.4 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 8
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240054 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -67.59 | 67.59 | -62.6188 | 62.6188 | 999 | -67.59 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 72.306 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240057 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.3662 | -12.8889 | 12.8889 | 999 | -20.3662 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 24.102 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240059 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -59.368 | 59.368 | -52.1824 | 52.1824 | 999 | -59.368 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 60.255 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240065 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -91.5876 | 91.5876 | -83.4918 | 83.4918 | 999 | -91.5876 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 86.408 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240066 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 115.504 | -72.886 | 72.886 | 999 | -115.504 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 138.578 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240077 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -41.25 | 41.25 | -36.478 | 36.478 | 999 | -41.25 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 41.25 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240079 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -61.88 | 61.88 | -54.717 | 54.717 | 999 | -61.88 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 61.88 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240080 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -66 | 66 | -58.365 | 58.365 | 999 | -66 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 66 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240092 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -305 | 305 | -191.2 | 191.2 | 999 | -305 |  |  | REGC_A |  |  | REEC_C | Closed | 50 | 45.8394 | BA | 360 | PF<-0.85 | NO | 0 | 999 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240108 | SC | SC | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 4 | 0 | 0 | 999 | -4 | [6 empty] | Open | 0 | 0 | UN | 8 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 12.47 |  |  | UN (Unknown) | SC
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240109 | EQ | EQ | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 17.4 | 0 | 0 | 999 | -17.4 | [6 empty] | Open | 0 | 0 | UN | 17.4 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 16 |  |  | UN (Unknown) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240112 | SC | SC | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 0.02 | 0 | 0 | 999 | -0.02 | [6 empty] | Open | 0 | 0 | UN | 0.02 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 16 |  |  | UN (Unknown) | SC
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240115 | SC | SC | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 5.549 | 0 | 0 | 999 | -5.549 | [6 empty] | Open | 0 | 0 | UN | 5.549 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 16 |  |  | UN (Unknown) | SC
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240153 | W1 | W1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 5.05 | 0 | 0 | 999 | -5.05 | [6 empty] | Open | 0 | 0 | UN | 5.32 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 4 |  |  | UN (Unknown) | W1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240157 | EQ | EQ | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 1.1 | 0 | 0 | 999 | -1.1 | [6 empty] | Open | 0 | 0 | UN | 1.16 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 12.47 |  |  | UN (Unknown) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240159 | EQ | EQ | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 2.6 | 0 | 0 | 999 | -2.6 | [6 empty] | Open | 0 | 0 | UN | 2.74 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 12.47 |  |  | UN (Unknown) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240196 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -15.84 | 15.84 | -11.37 | 11.37 | 999 | -15.84 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 19.5 | PF<-0.85 | NO | 9999 | 99999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240288 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -66 | 66 | -47 | 47 | 999 | -66 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 81 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.55 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240289 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -21.3 | 21.33 | -13.4 | 13.4 | 999 | -21.33 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 25.2 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240324 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -63.635 | 63.635 | -46.16 | 46.16 | 999 | -63.635 | [6 empty] | Open | 0 | 0 | BA | 106.08 | PF<-0.85 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240327 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -117.48 | 117.48 | -85.2 | 85.2 | 999 | -117.48 | [6 empty] | Open | 0 | 0 | BA | 195.84 | PF<-0.85 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240329 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -118.46 | 118.46 | -86 | 86 | 999 | -118.46 | [6 empty] | Open | 0 | 0 | BA | 197.47 | PF<-0.85 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240332 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -23.49 | 23.49 | -18 | 18 | 999 | -23.49 | [6 empty] | Open | 0 | 0 | BA | 39.16 | PF<0.8 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240425 | 1 | 1 | [6 empty] | Limit Power Fact | [5 empty] | Gen on HV | [6 empty] | -15 | 15.1 | -18.6 | 18.6 | 999 | -15.1 |  |  | REGC_A |  |  | REEC_C | Closed | 14 | 2.8566 | BA | 24 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 66 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240438 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -4.4 | 4.4 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 66 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 300140 | 2 | 2 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 20.8 | -11 | 14 | 9999 | 4.2 | 25 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Closed | 20.8 | 9.1165 | JE | 34.92 |  | NO | 0 | 0.116 | 2.3788 | 0.83068 | 0.1224 | 0.4172 | 3.4085 | 13.8 |  |  | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 300141 | 3 | 3 |  | Missing BA | [14 empty] | Missing PS |  |  | 0 | 20.7 | -11 | 14 | 9999 | 4.3 | 25 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Closed | 20.7 | 9.1164 | JE | 34.92 |  | NO | 0 | 0.116 | 2.3788 | 0.83068 | 0.1224 | 0.4172 | 3.4085 | 13.8 |  |  | JE (Jet Engine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 318683 | 1 | 1 |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | -9998.9998 | 1.1 | 0 | 0 | 9999 | -1.1 | [6 empty] | Closed | 1.1 | 0 | HY | 1.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | HATLOS_6_LSCRK unit 1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 318684 | 1 | 1 |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | -9998.9998 | 0.445 | 0 | 0 | 9999 | -0.445 | [6 empty] | Closed | 0.445 | 0 | HY | 0.445 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | HATLOS_6_LSCRK unit 2 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 346912 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -9998.9998 | 8.16 | -4 | 4 | 999 | -8.16 |  |  | REGC_A |  |  | REEC_A | Closed | 5.712 | -0.8082 | PV | 8.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | AVENAL_6_AVSLR1 0124-WD unit 1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 346914 | 2 | 2 | [17 empty] | Missing Sub R/X |  | -9998.9998 | 8.16 | -4 | 4 | 999 | -8.16 |  |  | REGC_A |  |  | REEC_A | Closed | 5.712 | -0.8082 | PV | 8.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | AVENAL_6_AVSLR2 0124-WD unit 2 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 364362 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 25.41 | -8.87 | 8.87 | 999 | -25.41 |  |  | REGC_A |  |  | REEC_A | Closed | 17.787 | 6.6297 | PV | 28.08 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit A3 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 364363 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 169.4 | -59.18 | 59.18 | 999 | -169.4 |  |  | REGC_A |  |  | REEC_A | Closed | 118.58 | 5.427 | PV | 187.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit B3 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365158 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.041 | 0 | 0 | 999 | -1.041 | [6 empty] | Closed | 0.7287 | 0 | PV | 1.041 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2111-RD | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365170 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 12.276 | -0.2 | 0.2 | 999 | -12.276 |  |  | REGC_A |  |  | REEC_A | Closed | 5 | 0 | PV | 13.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | BLCKWL_6_SOLAR1 0023-WD | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365198 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -118.1 | 118.1 | -56.8 | 56.8 | 999 | -118.1 |  |  | REGC_A |  |  | REEC_C | Closed | 82.67 | -9.6655 | BA | 131.07 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q0954 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365209 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -68.367 | 68.367 | -58.53 | 58.53 | 999 | -68.367 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 90 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365211 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -68.367 | 68.367 | -58.53 | 58.53 | 999 | -68.367 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 90 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365219 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 127.3 | -50 | 50 | 999 | -127.3 |  |  | REGC_A |  |  | REEC_A | Closed | 89.11 | -12.7838 | P4 | 136.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365220 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -114.45 | 114.45 | -100.6 | 100.6 | 999 | -114.45 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 150 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365221 | 3 | 3 | [17 empty] | Missing Sub R/X |  | 0 | 127.3 | -50 | 50 | 999 | -127.3 |  |  | REGC_A |  |  | REEC_A | Closed | 89.11 | -13.0117 | P4 | 136.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P4 (Photovoltaic, Tracking) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365222 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -114.45 | 114.45 | -100.6 | 100.6 | 999 | -114.45 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 150 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365226 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 205.5 | -72.16 | 72.16 | 999 | -205.5 |  |  | REGC_A |  |  | REEC_A | Closed | 143.85 | 40.0631 | P4 | 217.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1135 SPV1 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365228 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 205.5 | -72.16 | 72.16 | 999 | -205.5 |  |  | REGC_A |  |  | REEC_A | Closed | 143.85 | 40.0668 | P4 | 217.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1135 SPV2 | P4 (Photovoltaic, Tracking) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365325 | 3 | 3 | [17 empty] | Missing Sub R/X |  | 0 | 40.96 | -14.7 | 14.7 | 999 | -40.96 |  |  | REGC_A |  |  | REEC_A | Closed | 28.672 | -2.6403 | PV | 43.52 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  |  | PV (Photovoltaic) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365327 | 4 | 4 | [17 empty] | Missing Sub R/X |  | 0 | 30.72 | -14.7 | 14.7 | 999 | -30.72 |  |  | REGC_A |  |  | REEC_A | Closed | 21.504 | -2.6404 | PV | 32.64 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  |  | PV (Photovoltaic) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365338 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 5.093 | 0 | 0 | 999 | -5.093 | [6 empty] | Closed | 3.5651 | 0 | PV | 5.093 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | 2115-RD | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365339 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 3.6 | 0 | 0 | 999 | -3.6 | [6 empty] | Closed | 2.52 | 0 | PV | 3.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2560-RD | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365340 | RN | RN | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 7.875 | 0 | 0 | 999 | -7.875 | [6 empty] | Closed | 5.5125 | 0 | PV | 7.875 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | 2571-RD | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365343 | RN | RN | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 12.685 | 0 | 0 | 999 | -12.685 | [6 empty] | Open | 0 | 0 | UN | 12.685 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | 2740-WD | UN (Unknown) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365364 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -9.69 | 9.69 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Closed | 14 | 8.1787 | PV | 22.222 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.8 |  | Q0653B SPV | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365374 | 1 | 1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20 | -9.165 | 9.165 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Closed | 14 | 9.165 | P4 | 22.222 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.8 |  | Q0654 SPV | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365504 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 18.9 | -5.9 | 5.9 | 9999 | -18.9 |  |  | REGC_A |  |  | REEC_B | Closed | 13.23 | 3.8902 | PV | 19.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365514 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20 | -9.16 | 9.16 | 9999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | 0.3379 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | TRNQL8_2_AMASR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365517 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20 | -9.16 | 9.16 | 9999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | 0.3379 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | TRNQL8_2_AZUSR1 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365520 | 3 | 3 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 102.5 | -41.35 | 41.35 | 9999 | -102.5 |  |  | REGC_A |  |  | REEC_A | Closed | 71.75 | 0.33795 | PV | 112.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | TRNQL8_2_ROJSR1 | PV (Photovoltaic) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365523 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 100.7 | -42.5 | 42.5 | 9999 | -100.7 |  |  | REGC_A |  |  | REEC_A | Closed | 70.49 | -42.5 | P4 | 109.52 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1036 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365524 | 2 | 2 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 50.37 | -25.28 | 25.28 | 9999 | -50.37 |  |  | REGC_A |  |  | REEC_A | Closed | 35.259 | -25.28 | P4 | 56.53 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1036 | P4 (Photovoltaic, Tracking) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365526 | 4 | 4 | [17 empty] | Missing Sub R/X |  | 0 | 61.2 | -25.73 | 25.73 | 999 | -61.2 |  |  | REGC_A |  |  | REEC_A | Closed | 42.84 | 0.3379 | PV | 68.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | TRNQL8_2_VERSR1 | PV (Photovoltaic) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365540 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [13 empty] | 0 | 17.85 | -5 | 10 | 9999 | -17.85 |  |  | GENTPJ | PSS2A |  | EXAC8B | Closed | 17.85 | 10 | ST | 21 |  | NO | 0 | 0.23 | 3 | 0.63 | 0.05 | 0.25 | 5 | 12.47 |  | Q1016 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365547 | RN | RN |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 24.58 | -4.42 | 6.64 | 9999 | -24.58 |  |  | REGC_A |  |  | REEC_B | Closed | 17.206 | -1.7664 | PV | 25.35 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365555 | RN | RN |  | Missing BA | [17 empty] | 0 | 6 | 0 | 0 | 9999 | -6 | [6 empty] | Open | 0 | 0 | IC | 6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | -- | IC (Internal Combustion) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365556 | RN | RN |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 2 | 0 | 0 | 9999 | -2 |  |  | DER_A |  |  |  | Closed | 0.6 | 0 | W3 | 2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | -- | W3 (Wind Turbine, Type 3) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365557 | RE | RE |  | Missing BA | [12 empty] | Miss Turbine Type |  |  |  |  | 0 | 5 | 0 | 0 | 9999 | -5 | [6 empty] | Open | 0 | 0 | UN | 6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | UN (Unknown) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365558 | RN | RN |  | Missing BA | [17 empty] | -2 | 2 | 0 | 0 | 9999 | -2 | [6 empty] | Open | 0 | 0 | BA | 2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | BA (Energy Storage, Battery) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365559 | RN | RN |  | Missing BA | [17 empty] | 0 | 3.5 | 0 | 0 | 9999 | -3.5 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 3.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | RN |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365560 | RN | RN |  | Missing BA | [13 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 4.873 | 0 | 0 | 9999 | -4.873 | [6 empty] | Closed | 3.4111 | 0 | PV | 4.873 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1248-RD 1366-RD 3059-RD | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365563 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 10 | -4.5 | 4.5 | 9999 | -10 |  |  | REGC_A |  |  | REEC_A | Closed | 7 | 2.908 | P4 | 10.98 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | SKERN_6_SOLAR2 Q0885 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365564 | RE | RE |  | Missing BA | [12 empty] | Miss Turbine Type |  |  |  |  | 0 | 5 | 0 | 0 | 9999 | -5 | [6 empty] | Open | 0 | 0 | UN | 6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | -- | UN (Unknown) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365566 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 15.337 | -8.258 | -8.258 | 9999 | -15.337 |  |  | WT2G |  | WT2T | WT2E | Closed | 10 | -8.258 | W2 | 15.49 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWNDR_2_SMUD | W2 (Wind Turbine, Type 2) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365574 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 88 | -25.38 | 18.13 | 9999 | -88 |  |  | REGC_A | WTGPT_A | WTGT_A |  | Closed | 26.4 | 13.9824 | W3 | 98.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 1 |  | USWNDR_2_SMUD | W3 (Wind Turbine, Type 3) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365585 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 74.95 | -34.3 | 34.3 | 9999 | -74.95 |  |  | (REGC_A) |  |  | (REEC_A) | Closed | 52.465 | 22.5328 | PV | 67.784 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  | PNCHVS_2_SOLAR Q0829 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365586 | 2 | 2 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 74.95 | -34.3 | 34.3 | 9999 | -74.95 |  |  | (REGC_A) |  |  | (REEC_A) | Closed | 52.465 | 22.5328 | PV | 86.061 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  | PNCHVS_2_SOLAR Q0829 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365593 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 46.2 | -22.8 | 22.8 | 9999 | -46.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 13.86 | -1.9832 | W3 | 52.77 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q1010 | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365597 | 5 | 5 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 11.878 | -5.283 | 5.283 | 9999 | -11.878 |  |  | REGC_A |  |  |  | Closed | 8.3146 | 2.1638 | PV | 13 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  |  | PV (Photovoltaic) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365600 | 3 | 3 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 129.842 | -45.219 | 33.12 | 9999 | -129.842 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 38.9526 | 14.4176 | W3 | 143.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 1 |  | USWNDR_2_SMUD2 | W3 (Wind Turbine, Type 3) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365604 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 41 | -23.05 | 23.05 | 9999 | -41 |  |  | REGC_A |  |  | REEC_B | Closed | 28.7 | -3.6984 | P4 | 45.65 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365608 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 10 | -4.84 | 4.84 | 9999 | -10 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 3 | 0.5425 | W3 | 11.11 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWPFK_6_FRICK | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365624 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 41.88 | -21.228 | 21.228 | 9999 | -41.88 |  |  | REGC_A |  |  | REEC_B | Closed | 29.316 | -9.004 | PV | 48.7 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | Q0356 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365629 | FW | FW |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 101 | -45 | 45 | 9999 | -101 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 30.3 | -24.9657 | W4 | 113.85 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12 |  |  | W4 (Wind Turbine, Type 4) | FW
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365648 | 1 | 1 |  | Missing BA | [17 empty] | -25.3 | 25.3 | -14.25 | 14.25 | 9999 | -25.3 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 29.04 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1272 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365649 | 2 | 2 |  | Missing BA | [17 empty] | -20.25 | 20.25 | -8.01 | 8.01 | 9999 | -20.25 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 21.78 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1835 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365659 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 20.709 | -6.869 | 6.869 | 9999 | -20.709 |  |  | REGC_A |  |  | REEC_A | Closed | 20.709 | 1.4268 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | ADOBEE_1_SOLAR Q0622B | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365663 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 21.344 | -11.52 | 11.52 | 9999 | -21.344 |  |  | REGC_A |  |  | REEC_B | Closed | 14.9408 | -4.9205 | P4 | 24.255 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1127 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365669 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 17.6 | -11.5 | 11.5 | 999 | -17.6 | [6 empty] | Open | 0 | 0 | W3 | 21.24 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365673 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 51.83 | -27.98 | 27.98 | 9999 | -51.83 |  |  | REGC_A |  |  | REEC_B | Closed | 36.281 | -4.9212 | P4 | 58.905 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1128 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365675 | 1 | 1 |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 51.83 | -27.98 | 27.98 | 9999 | -51.83 |  |  | REGC_A |  |  | REEC_B | Closed | 36.281 | -4.921 | P4 | 58.905 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1128 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365679 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20.28 | -7.435 | 7.435 | 999 | -20.28 |  |  | REGC_A |  |  | REEC_A | Closed | 14.196 | -7.435 | PV | 21 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q1136 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365683 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 40.381 | -19.95 | 19.95 | 9999 | -40.381 |  |  | REGC_A |  |  | REEC_A | Closed | 28.2667 | -0.76128 | P4 | 45.045 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | CENT40_1_C40SR1 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365685 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 10.855 | -6.72 | 6.72 | 999 | 2.8e-07 | 10.855 |  | GENTPJ | PSS2B | TGOV1 | EXAC8B | Closed | 7.5985 | 6.72 | ST | 12.77 |  | NO | 0 | 1e-05 | 2.9 | 0.37033 | 0.116 | 0.46 | 3.9655 | 12 |  |  | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365688 | RE | RE | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 27.37 | -11.24 | 11.24 | 999 | -27.37 |  |  | REGC_A |  |  | REEC_A | Closed | 19.159 | 11.24 | P4 | 29.592 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | 2509-RD | P4 (Photovoltaic, Tracking) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365694 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 145.69 | -65.52 | 65.52 | 999 | -145.69 |  |  | REGC_A |  |  | REEC_A | Closed | 101.983 | 65.52 | P4 | 159.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.645 |  | Q1158 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365698 | 3 | 3 | [17 empty] | Missing Sub R/X |  | 0 | 158.64 | -71.33 | 71.33 | 999 | -158.64 |  |  | REGC_A |  |  | REEC_A | Closed | 111.048 | 64.2246 | P4 | 173.95 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.645 |  | Q1158 | P4 (Photovoltaic, Tracking) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365724 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 101.7 | -48.17 | 48.17 | 999 | -101.7 |  |  | REGC_A |  |  | REEC_A | Closed | 71.19 | 6.5789 | P4 | 112.53 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365729 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 9 | -4.36 | 4.36 | 999 | -9 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 2.7 | -0.65645 | W3 | 10.02 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365749 | 1 | 1 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 153 | 0 | 0 | 9999 | -153 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 45.9 | 0 | W3 | 178.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365773 | 1 | 1 |  | Missing BA | [17 empty] | -208 | 208 | -115 | 115 | 9999 | -208 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 237.762 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365936 | 1 | 1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 9.535 | -9.98 | 9.98 | 999 | -9.535 |  |  | REGC_A |  |  | REEC_B | Closed | 6.6745 | -0.24645 | PV | 14.123 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.12 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365940 | 2 | 2 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 2.88 | -3.01 | 3.01 | 999 | -2.88 |  |  | REGC_A |  |  | REEC_B | Closed | 2.016 | 0.33174 | PV | 4.264 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.12 |  |  | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365999 | 3 | 3 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 12.51 | -9.64 | 9.64 | 999 | -12.51 |  |  | REGC_A |  |  | REEC_A | Closed | 8.757 | -1.1535 | P3 | 15.798 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q0946-Q1259 spv3 | P3 (Photovoltaic, Fixed) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 366107 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -63.9 | 63.9 | -47.18 | 47.18 | 999 | -63.9 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 79.43 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.505 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 366108 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -60.85 | 60.85 | -45.23 | 45.23 | 999 | -60.85 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 75.82 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.505 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 366109 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -60.85 | 60.85 | -45.23 | 45.23 | 999 | -60.85 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 75.82 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.505 |  |  | BA (Energy Storage, Battery) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366130 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 6.011 | -2.08 | 2.08 | 9999 | -6.011 |  |  | REGC_A |  |  | REEC_A | Closed | 4.2077 | -2.08 | P3 | 6.54 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | P3 (Photovoltaic, Fixed) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366131 | 1 | 1 |  | Missing BA |  |  |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 14.339 | -4.93 | 4.93 | 9999 | -14.339 |  |  | REGC_A |  |  | REEC_A | Closed | 10.0373 | -4.93 | P3 | 15.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | P3 (Photovoltaic, Fixed) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366211 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 81.76 | -34.3 | 34.3 | 999 | -81.76 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 24.528 | 24.8963 | W3 | 88.66 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366241 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -77.46 | 77.46 | -73.43 | 73.43 | 999 | -77.46 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 106.73 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS1 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366242 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -77.46 | 77.46 | -73.43 | 73.43 | 999 | -77.46 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 106.73 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS2 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366243 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -104.27 | 104.27 | -98.85 | 98.85 | 999 | -104.27 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 143.675 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS3 | BA (Energy Storage, Battery) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366244 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -104.27 | 104.27 | -98.85 | 98.85 | 999 | -104.27 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 143.675 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS4 | BA (Energy Storage, Battery) | 4
30 | PG AND E | 470 | Calpine Corp. |  | 366344 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -25.27 | 25.27 | -17.6 | 17.6 | 999 | -25.27 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 30.8 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366361 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 203.9 | -76.561 | 76.561 | 999 | -203.9 |  |  | REGC_A |  |  | REEC_A | Closed | 142.73 | 6.5794 | P4 | 217.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366367 | RE | RE |  | Missing BA |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 30.33 | -16.75 | 16.75 | 9999 | -30.33 |  |  | REGC_A |  |  | REEC_B | Closed | 21.231 | -2.0099 | P4 | 29.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P4 (Photovoltaic, Tracking) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366380 | 4 | 4 |  | Missing BA | [15 empty] | Missing Sub R/X |  | 0 | 93.346 | -32.6 | 43.8 | 9999 | -93.346 |  |  | REGC_A |  |  | REEC_A | Closed | 28.0038 | 13.2325 | W4 | 102.26 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.72 |  | Q1463 | W4 (Wind Turbine, Type 4) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366608 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -105.92 | 105.92 | -73.1 | 73.1 | 999 | -105.92 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 128.7 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1470 BESS | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366613 | 1 | 1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 65.929 | -26.511 | 26.511 | 999 | -65.929 |  |  | REGC_A |  |  | REEC_B | Closed | 46.1503 | 26.511 | PV | 74 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.645 |  | Q1495 SPV | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366614 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -25.85 | 25.85 | -34.223 | 34.223 | 999 | -25.85 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 28 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1495 BESS | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366711 | 1 | 1 |  | Missing BA | [17 empty] | -103.9 | 103.9 | -54.12 | 54.12 | 9999 | -103.9 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 117.15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1472 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366712 | 2 | 2 |  | Missing BA | [17 empty] | -103.9 | 103.9 | -54.12 | 54.12 | 9999 | -103.9 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 117.15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1472 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366713 | 3 | 3 |  | Missing BA | [17 empty] | -100.75 | 100.75 | -52.48 | 52.48 | 9999 | -100.75 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 113.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1472 | BA (Energy Storage, Battery) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366715 | 4 | 4 |  | Missing BA | [17 empty] | -102.2 | 102.2 | -62.31 | 62.31 | 9999 | -102.2 |  |  | (REGC_A) |  |  | (REEC_C) | Open | 0 | 0 | BA | 119.7 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q1472 | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366806 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -20.325 | 20.325 | -14 | 14 | 999 | -20.325 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 25.2 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1443-BESS | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366807 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 41.02 | -20 | 20 | 999 | -41.02 |  |  | REGC_A |  |  | REEC_D | Closed | 28.714 | 4.0605 | P4 | 46.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1443-SPV | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366955 | RE | RE | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 18.9 | -6.48 | 6.48 | 999 | -18.9 |  |  | REGC_A |  |  | REEC_A | Closed | 13.23 | 6.48 | PV | 19.98 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.645 |  | 2446-RD | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366966 | 1 | 1 |  | Missing BA | [17 empty] | -15.2 | 15.2 | -7.4 | 7.4 | 9999 | -15.2 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 23.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 399997 | EW | EW |  | Missing BA | [10 empty] | Gen on HV | [6 empty] | 0 | 17.3 | 0 | 0 | 9999 | -17.3 | [6 empty] | Open | 0 | 0 | BA | 17.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 60 |  | CAISO-RPS | BA (Energy Storage, Battery) | EW
40 | NORTHWEST | 493 | Power Resources Cooperative | Bonneville Power Admin | 400151 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model | Missing PS |  |  | 0 | 5.66 | 0 | 0 | 14 | -5.66 | [6 empty] | Closed | 5.6 | 0 | GT | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | GT (Gas Turbine) | 1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 402010 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 6 | -2.7 | 2.55 | 14 | 0.49 | 6.49 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 5 | -2.7 | HY | 6.315 |  | YES | 0 | 0.2 | 1.555 | 0.098198 | 0.05 | 0.41 | 8.2 | 4.16 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 402010 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6 | -3.5 | 3.75 | 14 | 0.49 | 6.49 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Open | 0 | 0 | HY | 6.315 |  | YES | 0 | 0.2 | 1.555 | 0.098198 | 0.05 | 0.41 | 8.2 | 4.16 |  |  | HY (Hydro) | 2
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 403441 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 70 | -31.9 | 27.2671 | 14 | -70 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 51.8 | 13.192 | HY | 63.9 |  | YES | 0 | 0.2 | 4.4 | 2.8116 | 0.2 | 0.47 | 2.35 | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 403442 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 70 | -33.5 | 36.5 | 14 | -70 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Open | 0 | 0 | HY | 63.9 |  | YES | 0 | 0.2 | 4.4 | 2.8116 | 0.2 | 0.47 | 2.35 | 13.8 |  |  | HY (Hydro) | 2
40 | NORTHWEST | 929 | Columbia Basin Hydro | Bonneville Power Admin | 404670 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 2.4 | 0 | 0 | 14 | -2.4 | [6 empty] | Closed | 2 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC |  | 405144 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC |  | 405145 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC |  | 405184 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC |  | 405185 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin [Bus] | 406365 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 406366 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 9 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC |  | 406374 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC |  | 406375 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 497 | Middlefork Irrigation | Bonneville Power Admin | 408130 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 2 | 0 | 0 | 14 | -2 | [6 empty] | Closed | 2 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 497 | Middlefork Irrigation | Bonneville Power Admin | 408130 | 2 | 2 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 0.5 | 0 | 0 | 14 | -0.5 | [6 empty] | Closed | 0.5 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | HY (Hydro) | 2
40 | NORTHWEST | 497 | Middlefork Irrigation | Bonneville Power Admin | 408130 | 3 | 3 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 0.8 | 0 | 0 | 14 | -0.8 | [6 empty] | Closed | 0.8 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | HY (Hydro) | 3
40 | NORTHWEST | 1473 | Mckinley Paper Company | Bonneville Power Admin | 408412 | 1 | 1 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 12.6 | -12.7 | 17.8 | 14 | -12.6 |  |  | GENTPJ | PSS2B |  | ESAC8B_GE | Closed | 12 | 14.5787 | ST | 25 | PF<0.8 | YES | 0 | 1e-05 | 3.2 | 0.8 | 0.043 | 0.405 | 9.4186 | 13.8 |  |  | ST (Steam Turbine) | 1
40 | NORTHWEST | 1478 | Goose Prairie Solar LLC | Bonneville Power Admin | 408665 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 48.4 | -29 | 29 | 14 | -48.4 | [6 empty] | Closed | 36 | 1.6198 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.645 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1478 | Goose Prairie Solar LLC | Bonneville Power Admin | 408666 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 48.4 | -29 | 29 | 14 | -48.4 | [6 empty] | Closed | 36 | -4.3171 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.645 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 929 | Columbia Basin Hydro | Bonneville Power Admin | 408870 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 2.4 | 0.3 | 0.3 | 14 | -2.4 | [6 empty] | Closed | 2 | 0.3 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 929 | Columbia Basin Hydro | Bonneville Power Admin | 409591 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 6 | 0 | 0 | 14 | -6 | [6 empty] | Closed | 6 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 106 | Northern Lights Electric Co-op | Bonneville Power Admin | 410970 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 3 | 0 | 0 | 14 | -3 | [6 empty] | Closed | 3 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 1458 | Energy Northwest Packwood | Bonneville Power Admin | 470473 | 1 | 1 | [12 empty] | Gen on HV |  |  |  | Missing PS |  |  | 0 | 26 | -8 | 23 | 14 | -26 | [6 empty] | Open | 0 | 0 | HY | 100 | PF<0.8 | YES | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 473851 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 152.5 | -58.5 | 58.5 | 14 | -152.5 |  |  | REGC_A |  |  | REEC_A | Closed | 135 | -6.8689 | PV | 166.95 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 473911 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 107.3 | -20.6 | 20.6 | 14 | -107.3 | [6 empty] | Closed | 51 | -12.3384 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 473921 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 107.3 | -49.9 | 49.9 | 14 | -107.3 | [6 empty] | Closed | 107.3 | -8.7172 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474412 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 6.8 | 2.8 | 2.8 | 14 | 2.2 | 9 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 6.8 | 0 | ST | 9 |  | NO | 0 | 1 | 3 | 0.27 | 0 | 0 | NAN | 13.8 |  | CHEM_WE4_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474414 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | 1.8 | 1.8 | 14 | -0.2 | 6 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 4.9 | 0 | ST | 6 |  | NO | 0 | 1 | 3 | 0.18 | 0 | 0 | NAN | 13.8 |  | CHEM_WE4_13.8_G02 | ST (Steam Turbine) | 1
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474415 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 39.2 | 13.5 | 13.5 | 14 | 0.8 | 40 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 37.2 | 0 | ST | 40 |  | NO | 0 | 1 | 3 | 1.2 | 0 | 0 | NAN | 13.8 |  | CHEM_WE4_13.8_G05 | ST (Steam Turbine) | 1 |  | PSS Exempt
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474422 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 18.8 | -5.43 | 7.18 | 14 | -2.8 | 16 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 14.7 | 0 | ST | 16 |  | YES | 0 | 1 | 3 | 0.48 | 0 | 0 | NAN | 13.8 |  | COFFINRK_13.8_G04 | ST (Steam Turbine) | 1
40 | NORTHWEST | 29 | Avista Corp. | Avista | 481871 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 19.2 | -6.54 | 6.54 | 29 | -19.2 | [6 empty] | Closed | 8 | 3.5923 | PV | 19.2 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  | LIND SOLAR UN1 | PV (Photovoltaic) | PV
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 542525 | 6 | 6 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 412.5 | -170 | 230 | 76 | -2.42 | 410.08 |  | GENTPJ | PSS2B | GGOV1 | ESST1A_GE | Closed | 385.57 | -89.2528 | UN | 479 |  | NO | 0 | 0.225 | 4.73 | 22.6567 | 0.13 | 0.57 | 4.3846 | 20 |  |  | UN (Unknown) | 6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 542867 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | 0 | 407.5 | -132.5 | 195 | 76 | -4.3 | 403.2 |  | GENROU | PSS2B | GGOV1 | ESST1A_GE | Closed | 358.303 | 78.8333 | ST | 497 |  | NO | 0.003 | 0.214 | 4.66 | 23.1602 | 0.19 | 0.84 | 4.4211 | 13.8 |  |  | ST (Steam Turbine) | 12
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 542868 | 13 | 13 | [10 empty] | Unreas Sat | [8 empty] | 0 | 407.5 | -132.5 | 195 | 76 | -4.3 | 403.2 |  | GENROU | PSS2B | GGOV1 | ESST1A_GE | Closed | 358.303 | 78.9342 | ST | 497 |  | NO | 0.003 | 0.214 | 4.66 | 23.1602 | 0.19 | 0.84 | 4.4211 | 13.8 |  |  | ST (Steam Turbine) | 13
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 543525 | 7 | 7 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 412.5 | -170 | 230 | 76 | -2.42 | 410.08 |  | GENTPJ | PSS2B | GGOV1 | ESST1A_GE | Closed | 385.57 | -89.2528 | UN | 479 |  | NO | 0 | 0.225 | 4.73 | 22.6567 | 0.13 | 0.57 | 4.3846 | 20 |  |  | UN (Unknown) | 7
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 548307 | G2 | G2 | [6 empty] | Limit Power Fact |  |  | Unreas H | [9 empty] | 17.25 | 34.5 | -13.5 | 29 | 76 | 1.2e-07 | 34.5 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 47.8 | PF<0.8 | NO | 0 | 0.217 | 1.22 | 0.58316 | 0.165 | 0.539 | 3.2667 | 13.8 |  |  | GT (Gas Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 549110 | FD | FD | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -50 | 50 | 76 | 0 | [6 empty] | Open | 0 | 0 | WT | 50 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  |  | WT (Wind Turbine) | FD
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 550003 | G1 | G1 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0.686 | 13.72 | 1.9258 | 1.9258 | 76 | -13.72 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 4.2 | 1.926 | XC | 15.248 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | XC (Cross Compound Steam) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 550004 | G2 | G2 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0.772 | 15.435 | 1.6086 | 1.6086 | 76 | -15.435 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 3.6 | 1.609 | XC | 17.154 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | XC (Cross Compound Steam) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552433 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 25 | 2.9496 | 2.9496 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Closed | 20.7 | 2.95 | PV | 25 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552448 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 25 | -5.1378 | -5.1378 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Closed | 20.5 | -5.138 | PV | 26.4 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.66 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552450 | G3 | G3 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 25 | -5.1378 | -5.1378 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Closed | 20.5 | -5.138 | WT | 26.4 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.66 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553256 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12.5 | -8.25 | 8.25 | 76 | -12.5 |  |  | REGC_A |  |  | REEC_A | Closed | 10.3 | -5.1436 | WT | 14.4 | PF<-0.85 | NO | 0 | 0.53 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553260 | G5 | G5 | [8 empty] | RX Ratio | [10 empty] | 0 | 17.25 | -5.67 | 8.35 | 76 | -17.25 |  |  | REGC_A |  |  | REEC_A | Closed | 0.8 | 1.9012 | WS | 20 |  | NO | 0.6 | 0.29 | 0 |  |  |  | NAN | 0.65 |  |  | WS (Wind Turbine, Offshore) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553448 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 25 | -5.1378 | -5.1378 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Closed | 20.5 | -5.138 | WT | 26.4 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.66 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554246 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 7.5 | -2.47 | 3.63 | 76 | -7.5 | [6 empty] | Closed | 0.1 | -0.74073 | PV | 9.38 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554254 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 17 | -8.23 | 8.23 | 76 | -17 | [6 empty] | Closed | 10.6 | 1.0217 | WT | 18.89 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.55 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554448 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 25 | -2.9781 | -2.9781 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Closed | 20.9 | -2.978 | PV | 25 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554986 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 23 | -2.6219 | -2.6219 | 76 | -23 |  |  | REGC_A |  |  | REEC_A | Closed | 18.4 | -2.622 | PV | 25.56 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557004 | 16 | 16 | [7 empty] | PSS No Ex |  | Unreas H | [9 empty] | 17 | 41.5 | -15 | 22 | 76 | 35.441 | 76.941 |  | GENROU | PSS2B | GGOV1 |  | Closed | 37.8 | 18.3684 | JE | 76.94 |  | NO | 0.005 | 0.196 | 1.088 | 0.83711 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 16
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557014 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 108.4 | 466.5 | -149.8 | 220.7 | 76 | 82.5 | 549 |  | GENTPJ | PSS2B | IEEEG1_GE | ESST6B | Closed | 420 | -149.8 | GT | 549 |  | NO | 0.002 | 0.174 | 5.361 | 29.4319 | 0.134 | 0.687 | 5.1269 | 22 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557037 | G1 | G1 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 36 | 120 | 65.7 | 96.9 | 76 | 24 | 144 |  | GENROU | IEEEST | IEEEG1_GE | ESST4B | Open | 0 | 0 | UN | 144 | PF<0.8 | NO | 0.002 | 0.13 | 5.263 | 7.5787 | 0.0533 | 0.331 | 6.2101 | 12 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557051 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 50 | -19.72 | 29.06 | 76 | -50 |  |  | REGC_A |  |  | REEC_A | Closed | 0.9 | 29.06 | WT | 55.56 |  | NO | 0 | 0.66 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557066 | G1 | G1 | [9 empty] | Unreas H |  |  |  |  | Miss Turbine Type |  |  |  |  | 10 | 46 | -15.12 | 22.28 | 76 | 0.843 | 46.843 |  | GENROU | PSS2B | GGOV1 | REXS | Closed | 45.8 | -6.7146 | UN | 71.2 |  | NO | 0 | 0.156 | 1.341 | 0.95479 | 0.11 | 0.49 | 4.4545 | 13.8 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557113 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 3.1 | 0 | 0 | 76 | -3.1 | [6 empty] | Closed | 2.2 | 0 | IC | 3.874 |  | NO | 0 | 0.102 | 0 |  |  |  | NAN | 0.48 |  |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557113 | G3 | G3 | [15 empty] | Missing Model |  |  |  | 0 | 2.95 | 0 | 0 | 76 | -2.95 | [6 empty] | Closed | 2.1 | 0 | IC | 3.686 |  | NO | 0 | 0.095 | 0 |  |  |  | NAN | 0.48 |  |  | IC (Internal Combustion) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G1 | G1 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 2.67 | 2.67 | -0.29923 | -0.29923 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.299 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G2 | G2 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 2.67 | 2.67 | -0.29923 | -0.29923 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.299 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G3 | G3 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 2.67 | 2.67 | -0.29923 | -0.29923 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.299 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G4 | G4 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 2.67 | 2.67 | -0.29923 | -0.29923 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.299 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557120 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 22 | -2.2514 | -2.2514 | 76 | -22 |  |  | REGC_A |  |  |  | Closed | 15.8 | -2.251 | PV | 23 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.6 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557147 | 2 | 2 | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 212 | -7 | 105 | 76 | -212 | [6 empty] | Open | 0 | 0 | UN | 235.6 |  | NO | 0.003 | 0.175 | 0 |  |  |  | NAN | 18 |  |  | UN (Unknown) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557215 | G1 | G1 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | [9 empty] | 0 | 13.4 | 0.85398 | 0.85398 | 76 | -13.4 |  |  | GENTPJ |  |  |  | Closed | 11 | 0.854 | WT | 13.726 |  | NO | 0 | 0.095 | 0.893 | 0.12257 | 0.136 | 0.428 | 3.1471 | 13.8 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557216 | G5 | G5 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 1.8 | 2.67 | -0.38024 | -0.38024 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.38 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557216 | G6 | G6 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 1.8 | 2.67 | -0.38024 | -0.38024 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.38 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557269 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 20 | -2.3654 | -2.3654 | 76 | -20 |  |  | REGC_A |  |  |  | Closed | 16.6 | -2.365 | PV | 22.05 |  | NO | 1000 | 1000 | 0 |  |  |  | NAN | 25 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557277 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 19 | -2.2514 | -2.2514 | 76 | -19 |  |  | REGC_A |  |  |  | Closed | 15.8 | -2.251 | PV | 22.05 |  | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557342 | G1 | G1 | [9 empty] | Unreas H |  |  |  |  | Miss Turbine Type |  |  |  |  | 0 | 21.15 | -6.95 | 10.25 | 76 | 50.026 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | UN | 23.5 |  | NO | 0.001 | 0.19 | 1.25 | 0.29375 | 0.136 | 0.4 | 2.9412 | 13.8 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557399 | G1 | G1 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 11.3 | -3.714 | 5.473 | 76 | -11.3 |  |  | REGC_A |  |  |  | Closed | 7.2 | -3.6005 | UN | 14.125 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557442 | G2 | G2 | [9 empty] | Unreas H |  |  |  |  | Miss Turbine Type |  |  |  |  | 0 | 21.15 | -6.95 | 10.25 | 76 | 50.026 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | UN | 23.5 |  | NO | 0.001 | 0.19 | 1.25 | 0.29375 | 0.136 | 0.4 | 2.9412 | 13.8 |  |  | UN (Unknown) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557448 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.56856 | 0.56856 | 76 | -3.6 | [6 empty] | Closed | 2.8 | 0.569 | PV | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 25 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557448 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.56856 | 0.56856 | 76 | -3.6 | [6 empty] | Closed | 2.8 | 0.569 | PV | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 25 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557448 | G3 | G3 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.56856 | 0.56856 | 76 | -3.6 | [6 empty] | Closed | 2.8 | 0.569 | WT | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557448 | G4 | G4 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.56856 | 0.56856 | 76 | -3.6 | [6 empty] | Closed | 2.8 | 0.569 | WT | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557542 | G3 | G3 | [9 empty] | Unreas H |  |  |  |  | Miss Turbine Type |  |  |  |  | 0 | 21.15 | -6.95 | 10.25 | 76 | 50.026 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | UN | 23.5 |  | NO | 0.001 | 0.19 | 1.25 | 0.29375 | 0.136 | 0.4 | 2.9412 | 13.8 |  |  | UN (Unknown) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557554 | 3 | 3 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type | Missing Model | Missing PS |  |  | 0 | 6 | -2.7 | 5.4 | 76 | -6 | [6 empty] | Closed | 1.1 | -0.10383 | UN | 100 | PF<0.8 | NO | 0 | 0.15 | 0 |  |  |  | NAN | 13.2 |  |  | UN (Unknown) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557566 | 4 | 4 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type | Missing Model | Missing PS |  |  | 0 | 8.4 | -3.78 | 7.56 | 76 | -8.4 | [6 empty] | Closed | 2.8 | -0.93636 | UN | 100 | PF<0.8 | NO | 0 | 0.21 | 0 |  |  |  | NAN | 13.2 |  |  | UN (Unknown) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557642 | G4 | G4 | [10 empty] | Unreas Sat |  |  |  | Miss Turbine Type |  |  |  |  | 0 | 29.7 | -9.8 | 14.4 | 76 | -29.7 |  |  | GENTPJ | PSS2A |  | ESAC8B_GE | Open | 0 | 0 | UN | 33 |  | NO | 0.003 | 0.25 | 5.51 | 1.8183 | 0.207 | 0.48 | 2.3188 | 13.8 |  |  | UN (Unknown) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557690 | G5 | G5 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 5.28 | 0.71246 | 0.71246 | 76 | -5.28 | [6 empty] | Closed | 5 | 0.712 | IC | 7.5 |  | NO | 0 | 0.13 | 0 |  |  |  | NAN | 0.6 |  |  | IC (Internal Combustion) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557709 | 17 | 17 | [9 empty] | Unreas H | [9 empty] | 17 | 44 | -15 | 22 | 76 | 4.2 | 48.2 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 40.9 | 3.4226 | JE | 76.941 |  | NO | 0.006 | 0.195 | 1.117 | 0.85943 |  |  | NAN | 13.8 |  |  | JE (Jet Engine) | 17
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557742 | M1 | M1 | [14 empty] | Miss Turbine Type | Missing Model |  |  |  | -17.9 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -2 | 0 | UN | 17.9 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | M1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557742 | M2 | M2 | [14 empty] | Miss Turbine Type | Missing Model |  |  |  | -11.6 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -1.3 | 0 | UN | 11.6 |  | NO | 0.005 | 0.25 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | M2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557842 | M3 | M3 | [14 empty] | Miss Turbine Type | Missing Model |  |  |  | -8.6 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -1 | 0 | UN | 8.6 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | M3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557942 | M4 | M4 | [14 empty] | Miss Turbine Type | Missing Model |  |  |  | -8.2 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -0.9 | 0 | UN | 8.2 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | M4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557942 | M5 | M5 | [14 empty] | Miss Turbine Type | Missing Model |  |  |  | -5.6 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -0.7 | 0 | UN | 5.6 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | M5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558037 | G2 | G2 | [14 empty] | Miss Turbine Type |  |  |  |  | 84 | 280 | 52.6 | 77.5 | 76 | 3.9 | 283.9 |  | GENROU | PSS2A | GGOV1 | ESST4B | Open | 0 | 0 | UN | 334 |  | NO | 0.003 | 0.215 | 6.76 | 22.5784 | 0.0538 | 0.3531 | 6.5632 | 18 |  |  | UN (Unknown) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558259 | GX | GX | [5 empty] | At Mvar Limit | [13 empty] | 0 | 25 | -7.395 | 10.897 | 76 | -25 |  |  | REGC_A |  |  |  | Closed | 17.9 | -7.395 | PV | 22.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | GX
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558263 | 1 | 1 | [5 empty] | At Mvar Limit |  |  | RX Ratio | [10 empty] | 0 | 11.122 | -3.65 | 5.387 | 76 | -11.122 |  |  | REGC_A |  |  | REEC_A | Closed | 0.6 | -3.65 | WT | 12.4 |  | NO | 2.25 | 1.09 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558266 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 1 | 7.5 | -1.0559 | -1.0559 | 76 | -7.5 | [6 empty] | Closed | 5.2 | -1.056 | WT | 9.375 |  | NO | 0 | 0.211 | 0 |  |  |  | NAN | 13.8 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558321 | G1 | G1 | [10 empty] | Unreas Sat |  |  |  | Miss Turbine Type |  |  |  |  | 0 | 16 | -6.73 | 9.39 | 76 | 13.529 | 29.529 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | UN | 21.56 |  | NO | 0.004 | 0.102 | 5.116 | 1.103 | 0.282 | 0.906 | 3.2128 | 13.8 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558366 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 14 | -2.5991 | -2.5991 | 76 | -14 |  |  | GENTPJ |  |  |  | Closed | 12.8 | -2.599 | WT | 17.5 |  | NO | 0 | 0.144 | 1.52 | 0.266 | 0.2 | 0.8 | 4 | 6.9 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560003 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 200.4 | -76.363 | 76.363 | 76 | -200.4 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 14.9 | 76.363 | WT | 214.5 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560026 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 156.71 | -98.407 | 98.407 | 76 | -156.71 |  |  | REGC_A |  |  | REEC_A | Closed | 156.701 | 25.1383 | PV | 183.6 | PF<-0.85 | NO | 0 | 10 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560503 | G4 | G4 | [6 empty] | Limit Power Fact | [12 empty] | -8.7 | 8.7 | -8 | 5.6 | 76 | -8.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 11.18 | PF<-0.85 | NO | 0 | 99999 | 0 |  |  |  | NAN | 0.48 |  |  | WT (Wind Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560608 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 133 | -43.72 | 64.42 | 76 | -133 |  |  | REGC_A |  |  | REEC_A | Closed | 4.5 | -43.72 | WT | 148 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560894 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 57.2 | -39.124 | 39.124 | 76 | -57.2 |  |  | REGC_A |  |  | REEC_A | Closed | 1.2 | -1.7759 | PV | 157.5 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561003 | G2 | G2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 46.8 | -15.382 | 15.382 | 76 | -46.8 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 3.5 | 15.382 | WT | 49.3 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561026 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 156.71 | -98.407 | 98.407 | 76 | -156.71 |  |  | REGC_A |  |  | REEC_A | Closed | 153.401 | 24.4492 | PV | 183.6 | PF<-0.85 | NO | 0 | 10 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561336 | B1 | B1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10 | -6.5 | 6.5 | 76 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 11.97 | PF<-0.85 | NO | 0 | 10 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | B1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561608 | G2 | G2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 133 | -43.72 | 64.42 | 76 | -133 |  |  | REGC_A |  |  | REEC_A | Closed | 4.5 | -43.72 | WT | 148 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561894 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 72.8 | -49.794 | 49.794 | 76 | -72.8 |  |  | REGC_A |  |  | REEC_A | Closed | 1.6 | -2.3319 | PV | 88.2 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561990 | G2 | G2 | [8 empty] | RX Ratio | [10 empty] | 0 | 151.2 | -52.164 | 71.988 | 76 | -151.2 |  |  | REGC_A |  |  | REEC_A | Closed | 10 | -30.7956 | W4 | 168 |  | NO | 0.3 | 0.17 | 0 |  |  |  | NAN | 0.65 |  |  | W4 (Wind Turbine, Type 4) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 562026 | G3 | G3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 156.71 | -98.407 | 98.407 | 76 | -156.71 |  |  | REGC_A |  |  | REEC_A | Closed | 153.401 | 23.51 | PV | 183.6 | PF<-0.85 | NO | 0 | 10 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 563308 | G3 | G3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 54 | -33.6 | 33.6 | 76 | -54 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | WT | 63.6 | PF<-0.85 | NO | 0.3 | 1.2 | 0 |  |  |  | NAN | 0.72 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 567004 | G1 | G1 | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 102.34 | -40.098 | 40.098 | 76 | -102.34 |  |  | REGC_A |  |  | REEC_A | Closed | 1.1 | -17.6763 | UN | 110 |  | NO | 0.008 | 0.2 | 0 |  |  |  | NAN | 0.69 |  |  | UN (Unknown) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 568006 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 9.2 | 0 | 0 | 76 | -9.2 | [6 empty] | Closed | 7.4 | 0 | WT | 9.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 568007 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 9.2 | 0 | 0 | 76 | -9.2 | [6 empty] | Closed | 7.4 | 0 | WT | 9.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 568010 | G2 | G2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 9.2 | -3.02 | 4.45 | 76 | -9.2 |  |  | REGC_A |  |  | REEC_A | Closed | 7.857 | -3.02 | WT | 10.22 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 568011 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 9.2 | -3.02 | 4.45 | 76 | -9.2 |  |  | REGC_A |  |  | REEC_A | Closed | 7.497 | -3.02 | WT | 10.22 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
60 | IDAHO | 11 | Idaho Power Company |  | 600263 | 1 | 1 | [15 empty] | Missing Model |  |  |  | -38.5 | 38.5 | -12.6 | 12.6 | 11 | -38.5 | [6 empty] | Closed | 7.7 | -1.6739 | BA | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | HPVY_.69_BS1 | BA (Energy Storage, Battery) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 600265 | 1 | 1 | [15 empty] | Missing Model |  |  |  | -38.5 | 38.5 | -12.6 | 12.6 | 11 | -38.5 | [6 empty] | Closed | 7.7 | -1.6739 | BA | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | HPVY_.69_BS2 | BA (Energy Storage, Battery) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 600275 | 1 | 1 | [15 empty] | Missing Model |  |  |  | -153.3 | 153.3 | -58.2 | 58.2 | 11 | -153.3 | [6 empty] | Closed | 30.7 | -23.6494 | ES | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.8 |  | KUNA_.80_BESS | ES (Energy Storage, Other) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 600276 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 3.2 | 0 | 0 | 11 | -3.2 | [6 empty] | Closed | 3.19 | 0 | IC | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  | West Point RNG | IC (Internal Combustion) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 2
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 3 | 3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 3
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 4 | 4 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 4
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 5 | 5 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 5
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 6 | 6 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 6
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 7 | 7 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 7
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 8 | 8 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 8
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 9 | 9 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 9
62 | MONTANA | 78 | NorthWestern Energy |  | 622531 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 5 | 11.5 | -6 | 6.2 | 78 | -1.9 | 9.6 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 5 | 2.6827 | HY | 10 |  | YES | 0 | 0.124 | 4.71 | 0.471 | 0.216 | 0.478 | 2.213 | 6.6 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622531 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 5 | 11.5 | -6 | 6.2 | 78 | -1.9 | 9.6 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 5 | 2.6827 | HY | 10 |  | YES | 0 | 0.203 | 4.71 | 0.471 | 0.216 | 0.478 | 2.213 | 6.6 |  |  | HY (Hydro) | 3 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622532 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 5 | 11.5 | -7.5 | 6.5 | 78 | -1.9 | 9.6 |  | GENTPJ |  | HYG3 | ESST4B | Open | 0 | 0 | HY | 10 | PF<-0.85 | YES | 0 | 0.124 | 4.71 | 0.471 | 0.216 | 0.478 | 2.213 | 6.6 |  |  | HY (Hydro) | 5 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622532 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 5 | 11.5 | -7.5 | 6.5 | 78 | -1.9 | 9.6 |  | GENTPJ |  | HYG3 | ESST4B | Open | 0 | 0 | HY | 10 | PF<-0.85 | YES | 0 | 0.203 | 4.71 | 0.471 | 0.216 | 0.478 | 2.213 | 6.6 |  |  | HY (Hydro) | 6 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622541 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 11 | 32 | -24.1744 | 22.9987 | 78 | -32 |  |  | GENTPJ |  |  |  | Closed | 22.3 | 7.0422 | HY | 35.5 | PF<-0.85 | YES | 0 | 0.345 | 2.47 | 0.87685 | 0.3017 | 0.6096 | 2.0206 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622541 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 11 | 34 | -23.6718 | 22.6936 | 78 | -34 |  |  | GENTPJ |  |  |  | Closed | 23.7 | 7.0422 | HY | 35.5 | PF<-0.85 | YES | 0.005 | 0.29 | 2.47 | 0.87685 | 0.3017 | 0.6096 | 2.0206 | 13.8 |  |  | HY (Hydro) | 2 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622551 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 9 | 24.5 | -13.4643 | 21.2857 | 78 | 0.9 | 25.4 |  | GENTPJ | PSS2A | HYG3 | ESST4B | Closed | 16.5 | 4.9742 | HY | 35 | PF<0.8 | YES | 0.006 | 0.51 | 1.68 | 0.588 | 0.29 | 0.472 | 1.6276 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 622573 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 73.32 | -35.51 | 35.51 | 78 | -73.32 | [6 empty] | Closed | 22 | 1.7401 | WT | 81.47 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 622591 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 7.8 | -3.58 | 3.58 | 78 | -7.8 | [6 empty] | Closed | 6.5 | -2.4851 | HY | 8.22 |  | NO | 0 | 0.194 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 622591 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 5.4 | -2.57 | 2.57 | 78 | -5.4 | [6 empty] | Closed | 4.5 | -2.4851 | HY | 5.89 |  | NO | 0 | 0.213 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 623511 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 1 | 6 | -1.15 | 1.75 | 78 | -6 | [6 empty] | Closed | 4 | 1.177 | HY | 7.5 |  | NO | 0 | 0.203 | 0 |  |  |  | NAN | 6.6 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 623511 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 1 | 6 | -1.15 | 1.75 | 78 | -6 | [6 empty] | Closed | 4 | 1.177 | HY | 7.5 |  | NO | 0 | 0.203 | 0 |  |  |  | NAN | 6.6 |  |  | HY (Hydro) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 623531 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 58.428 | -28.298 | 36.21 | 78 | -58.428 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 58.428 | 3.2482 | CA | 68.74 |  | NO | 0 | 0.182 | 1.3 | 0.89362 | 0.14 | 0.38 | 2.7143 | 13.8 |  |  | CA (Combined Cycle Steam Part) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 623532 | 1 | 1 | [9 empty] | Unreas H |  |  |  |  | Miss Turbine Type |  | Missing PS |  |  | 0 | 58.428 | -28.298 | 36.21 | 78 | -58.428 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 58.428 | 3.2482 | UN | 68.74 |  | NO | 0 | 0.182 | 1.3 | 0.89362 | 0.14 | 0.38 | 2.7143 | 13.8 |  |  | UN (Unknown) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 623533 | 1 | 1 | [9 empty] | Unreas H |  |  |  |  | Miss Turbine Type |  | Missing PS |  |  | 0 | 58.428 | -28.298 | 36.21 | 78 | -58.428 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 58.428 | 3.2482 | UN | 68.74 |  | NO | 0 | 0.182 | 1.3 | 0.89362 | 0.14 | 0.38 | 2.7143 | 13.8 |  |  | UN (Unknown) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 623565 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 82.08 | -51.84 | 51.84 | 78 | -82.08 | [6 empty] | Closed | 80 | 42.6338 | P3 | 86.4 | PF<-0.85 | NO | 99999 | 99999 | 0 |  |  |  | NAN | 0.63 |  |  | P3 (Photovoltaic, Fixed) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 626511 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 1.5 | 3.2 | -0.83 | 0.83 | 78 | -3.2 |  |  | GENTPJ |  |  |  | Closed | 1.5 | 0.83 | HY | 2.25 |  | NO | 0 | 0.24 | 3.644 | 0.08199 | 0.152 | 0.59 | 3.8816 | 4 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 626511 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 1.5 | 3.2 | -0.83 | 0.83 | 78 | -3.2 |  |  | GENTPJ |  |  |  | Closed | 1.5 | 0.83 | HY | 2.25 |  | NO | 0 | 0.24 | 3.644 | 0.08199 | 0.152 | 0.59 | 3.8816 | 4 |  |  | HY (Hydro) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 626511 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 1.5 | 3.2 | -0.83 | 0.83 | 78 | -3.2 |  |  | GENTPJ |  |  |  | Closed | 1.5 | 0.83 | HY | 2.25 |  | NO | 0 | 0.24 | 3.644 | 0.08199 | 0.152 | 0.59 | 3.8816 | 4 |  |  | HY (Hydro) | 3
62 | MONTANA | 78 | NorthWestern Energy |  | 626511 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 1.5 | 3.2 | -0.83 | 0.83 | 78 | -3.2 |  |  | GENTPJ |  |  |  | Closed | 1.5 | 0.83 | HY | 2.25 |  | NO | 0 | 0.24 | 3.644 | 0.08199 | 0.152 | 0.59 | 3.8816 | 4 |  |  | HY (Hydro) | 4
62 | MONTANA | 78 | NorthWestern Energy |  | 627521 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 1.7 | 2.8 | -0.39 | 0.39 | 78 | -2.8 | [6 empty] | Closed | 2.5 | -0.20028 | HY | 2.8 |  | NO | 0 | 0.108 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 627521 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 1.7 | 3.4 | -0.39 | 0.39 | 78 | -3.4 | [6 empty] | Closed | 3.1 | -0.20028 | HY | 3.4 |  | NO | 0 | 0.108 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 627521 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 1.7 | 2.8 | -0.39 | 0.39 | 78 | -2.8 | [6 empty] | Closed | 2.5 | -0.20028 | HY | 2.8 |  | NO | 0 | 0.108 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 3
62 | MONTANA | 78 | NorthWestern Energy |  | 627522 | 4 | 4 | [15 empty] | Missing Model |  |  |  | 1.7 | 3.4 | -0.39 | 0.39 | 78 | -3.4 | [6 empty] | Closed | 3.1 | -0.20028 | HY | 3.4 |  | NO | 0 | 0.108 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 4
62 | MONTANA | 78 | NorthWestern Energy |  | 627522 | 5 | 5 | [15 empty] | Missing Model |  |  |  | 1.7 | 3.4 | -0.39 | 0.39 | 78 | -3.4 | [6 empty] | Closed | 3.1 | -0.20028 | HY | 3.4 |  | NO | 0 | 0.108 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 5
62 | MONTANA | 78 | NorthWestern Energy |  | 627522 | 6 | 6 | [15 empty] | Missing Model |  |  |  | 2.5 | 3.75 | -2.25 | 2.25 | 78 | -3.75 | [6 empty] | Closed | 3.4 | -0.20028 | HY | 3.75 |  | NO | 0 | 0.14 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 6
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 627531 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 9.66 | -4.21 | 4.21 | 78 | -9.66 | [6 empty] | Closed | 4 | 4.21 | HY | 9.66 |  | NO | 0 | 0.22 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 629521 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -7.6286 | 5.5429 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 3 | 1.5678 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629521 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -7.6286 | 5.5429 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 3 | 1.5678 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 2 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629521 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -7.6286 | 5.5429 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 3 | 1.5678 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 3 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629522 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -7.6286 | 5.5429 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 3 | 1.5678 | HY | 8.75 | PF<0.8 | YES | 0.007 | 0.192 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 4 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629522 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -7.6286 | 5.5429 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 3 | 1.5678 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 5 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629522 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -7.6286 | 5.5429 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 3 | 1.5678 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 6 |  | PSS Exempt
63 | WAPA U.W. | 43 | US Army Corps of Engrs |  | 631002 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 18 | -9 | 11 | 77 | 1.21 | 19.21 |  | GENTPJ | PSS2A | HYGOV4 | ESST1A_GE | Closed | 18 | 10.4738 | HY | 19.21 |  | NO | 0.004 | 0.25 | 2.03 | 0.38996 | 0.17 | 0.33 | 1.9412 | 13.8 |  |  | HY (Hydro) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 640063 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 50 | -28.4804 | 28.4804 | 24 | -50 |  |  | REGC_A |  |  | REEC_B | Closed | 45.7 | -1.0193 | PV | 51.7 |  | YES | 1.754 | 2.355 | 0 |  |  |  | NAN | 0.55 |  | LUNING_0.48_SOLAR | PV (Photovoltaic) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 640076 | CL | CL | [16 empty] | Missing PS |  |  | -1.5 | 0 | -0.5 | -0.5 | 24 | 0 | [6 empty] | Open | 0 | 0 | GT | 183 | PF<0.8 | YES | 0.002 | 0.156 | 0 |  |  |  | NAN | 34.5 |  | TSLACHLR | GT (Gas Turbine) | CL
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 640080 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10.1 | -1.0779 | 1.0779 | 24 | -10.1 | [6 empty] | Closed | 3.2795 | 0.013443 | PV | 10 |  | NO | 0 | 0.179 | 0 |  |  |  | NAN | 0.38 |  | PATUA_PV | PV (Photovoltaic) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640251 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 43.53 | -13.59 | 14.8 | 24 | -2.23 | 41.3 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 38.5 | -2.6267 | BT | 43.53 |  | NO | 0 | 100000 | 1.56 | 0.67907 | 0.05 | 0.4 | 8 | 12.47 |  | TUNGSTEN | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640251 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 25.5 | -10.8 | 15.75 | 24 | 4.5 | 30 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | BT | 30 |  | NO | 0 | 100000 | 1.6 | 0.48 | 0.05 | 0.4 | 8 | 12.47 |  | TUNGSTEN | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640252 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 8 | -2.63 | 2.63 | 24 | -8 |  |  | REGC_A |  |  | REEC_A | Closed | 7.2 | 0.033822 | PV | 8 |  | NO | 0.297 | 0.005 | 0 |  |  |  | NAN | 0.69 |  | TUNGSTEN | PV (Photovoltaic) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640252 | 2 | 2 | [8 empty] | RX Ratio | [10 empty] | 0 | 8 | -2.63 | 2.63 | 24 | -8 |  |  | REGC_A |  |  | REEC_A | Closed | 6.5 | 0.033822 | PV | 8 |  | NO | 0.297 | 0.005 | 0 |  |  |  | NAN | 0.69 |  | TUNGSTEN | PV (Photovoltaic) | 2
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640920 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 37 | -12.1613 | 22.9305 | 24 | 1 | 38 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 25 | -4.9721 | BT | 30 |  | NO | 0.03 | 0.191 | 1.65 | 0.495 | 0.05 | 0.4 | 8 | 12.47 |  | BEOWAWE_RPWR_12.47_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 641041 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 37 | -11.6404 | 22.85 | 24 | -10.15 | 26.85 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 11.4853 | 1.3076 | BT | 43.53 |  | NO | 0.005 | 0.189 | 1.76 | 0.76613 | 0.08 | 0.16 | 2 | 12.47 |  | EAGLE_SANEMIDIO_12.47_1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 641041 | 2 | 2 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 37 | -11.6404 | 22.85 | 24 | -10.15 | 26.85 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 11.4853 | 1.3076 | BT | 43.53 |  | NO | 0.005 | 0.189 | 1.76 | 0.76613 | 0.08 | 0.16 | 2 | 12.47 |  | EAGLE_SANEMIDIO_12.47_2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 186 | Ormat Nevada INC. |  | 641048 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 18.5 | -17.25 | 17.25 | 24 | 4.9 | 23.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | BT | 28.75 | PF<0.8 | NO | 0 | 100000 | 1.68 | 0.483 | 0.08 | 0.16 | 2 | 13.7998 |  | N_VALLEY2_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 641048 | 2 | 2 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 18.5 | -17.25 | 17.25 | 24 | 4.9 | 23.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | BT | 28.75 | PF<0.8 | NO | 0 | 100000 | 1.68 | 0.483 | 0.08 | 0.16 | 2 | 13.7998 |  | N_VALLEY2_13.8_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 641110 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 24.8 | -22.93 | 22.93 | 24 | 4.1e-07 | 24.8 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 24 | -1.7871 | BT | 29.17 | PF<0.8 | NO | 0 | 100000 | 1.76 | 0.51339 | 0.08 | 0.16 | 2 | 12.47 |  | FRONTIRS_12.5_GEO9 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1