## Input data Error checking
Anchor Data Set (ADS) Production Cost Model (PCM)
Input Data Error Checking
Data Set Element | Review Error check results | Comments | Persons Responsible
Loads
Year 10 loads | Year 10 loads match values submitted by BAs in 2022 L&R submittal, and review the load forecast shapes, submitted to LnR. | Done. Feb is different due to leap year. But not off by lot (less than 1%). All other months matches. | Tyler, Jon and Amanda looking into it. 80% complete. Most of L&R data verified. New LA loads updated. ID ok. BPA haven't heard back yet.
Load profiles | Need to come up with a criteria, review load forecast shapes, check for BTM, make sure we are not double counting. Making sure that we use 2022 LnR submittal. Ensure we are accounting for energy for BTM units, and not just the peak. | Done. BTM accounted in latest loads spreadsheet. BTM is not being double counted | Jon, Tyler
Resources
Bus assignments | Bus assignments are as approved by APFWG | Done. APFWG recommendation used to finalize bus assginment. | APFWG
Hourly Resource shape files | Validate multiplier and Shape files for hourly resource Shape files. All hourly resource shape files have a consistent entry "0 to 1" or "0 to 10,000". | Done. Hitachi. | Tyler
Generator capacity | Compare Gen cap for generators to previous case, change is with in ± 10%. | Hitachi did system level checks. Tyler and Stan are comapring it to L&R. Finish date 7/20 | Tyler, Stan
Generator model type | Correct model types are applied to all generators. | Done. Completed by Hitachi | Hitachi for mdoel type, Kevin for turbine Type
Generator Changes | Identify Generator changes between two consequent LnR Submittals. | Done | All WECC Staff
Transmission Topology
Topology for current case | All submitted changes from previous case are included. Topology matches the topology approved by APFWG, making sure the latest regional Tr. Plans submitted for FERC order compliance are implemented. Keep track of which Tr. Plan is approved to be in the case. | Done. Topology came from base case provided by APFWG | Tyler, Nick
Nomograms | All nomograms approved by APFWG and provided by TPs are entered correctly into Gridview | Done. PCDS/APFWG agreed to not update for initial release. Maybe be revisted later. | NA
Other Data
Fuel prices | Fuel prices used to create the case match the input fuel prices approved by PCDS | Done | Jon
Generator fuel type | All generators are assigned the correct fuel types | Done | Tyler
Tariffs and wheeling rates | All tariffs and wheeling rates used in the case match those posted by BAs in OASIS | Done-Did not change | NA
Emission costs | Emission costs used to create the case match the input emission costs approved by PCDS | Done | Stan, Tyler
Variable operating costs (VOM) | All thermal VOM costs match the values developed by INTERTEK | Done.PCDS has decided not to update it with initial release. | NA
| VOM from previous case are escalated using the correct escalators (Thermal and Battery) | Need to apply escalation rate based on 2022 $ vrs @2020 $. (assgined to Tyler) | Tyler
Heat Rates | Heat rates match values approved by PCDS | Done | Jon, BK, Tyler
Hydro shapes | 2018 shapes are used for all hydro units | Done | Bhavana, BK
Wind and solar shapes | Wind and solar shapes match 2018 data provided by NREL | Done | Bhavana, BK, Jon
Dispatch prices | Pump storage, hydro, battery, solar and wind dispatch prices approved by PCDS are entered correctly into Gridview | Not determined by PCDS as of 7/15/2022. Implemented LA Hydro dispatch cost to be same as wind and solar. | NA
Inflation rates | Inflation rates approved by PCDS are entered correctly into Gridview | Done. applied to fuel prices, emission costs. | Jon
Storage costs | Charging, discharging and VOM costs for pump storage and battery storage as approved by PCDS are entered correctly into Gridview | Done. PCDS decided not to update it. | NA
VOM Costs | All hydro, solar and wind VOM costs match the values approved by PCDS | Done. PCDS has decided not to update it with initial release. | NA
DC losses for PCDI | DC Losses for the PDCI were analyzed, PCDS decided to keep as is | Done | BK

## Performace Criteria metrics
Anchor Data Set (ADS) Production Cost Model (PCM)
Performance Criteria metrics
Data Set Element | Review Error check results | Comments
Loads
Unserved Energy | Check for unserved energy by BA or Area level, generally there should be No unserved load in any BA/Area, Identify if it’s a resource issue or a transmission issue | Unserved energy in latest run case. Working with Hitachi to resolve it.
| *run without EFOR, and verify if the unserved load goes away. Check transmission utilization. | consider along with previous item.
| *run a resource adequacy check | RA check will be done after initial release of the the case
Resources
Generation Summary | Change in generation by unit/sub type is within ± 10% of previous case | need a run case with no unserved energy
Avg loading of a unit = Cap factor/Connection factor | If Avg loading is very low for a particular unit, need to check why is that happening | need a run case with no unserved energy
Connection factor = (Operating hrs./Hrs. in the period). | % of time its connected to the grid. | need a run case with no unserved energy
By model type compare Cap factor, Number of Starts and operating Hours | eg: Solar cap factor > 30% is to be looked into the hourly shape assigned to Solar units. | need a run case with no unserved energy
Transmission Topology |  | need a run case with no unserved energy
Transmission paths and branches | No path or branch flows exceed ratings in the Path Rating Catalogue. Check Transmission congestion at Area level. | need a run case with no unserved energy
Number of PhaseShifter Operations | Depends on the location typically not operated much, with an exception of a few in CA. | need a run case with no unserved energy
DC Losses | Validate DC losses for PDCI | Need latest run. How to validate? Check with Yi. (assgined to BK)