## Standard Disturbances
Standard Disturbances |  |  |  | Disturbances listed below are simulated during the review stage and after approval of each WECC base case to test the model.
Distrubance ID | Disturbance Name | Category | Base Case Area | Time, Object, Actions, Criteria, Criteria Status, and Comment | Associated Remedial Action Scheme | Memo
ST-0 | No Disturbances | A | NA
ST-DSW-1 | Palo Verde Generating Station Outage Double Unit Outage | D | 14 | 1.0 "GEN 14931 1" "OPEN" "" "ALWAYS" "" 1.0 "GEN 14932 1" "OPEN" "" "ALWAYS" "" | None | Switch file provided by Barrie Kokanos
ST-NWC-1 | Chief Joe Brake Insertion |  | 40 | 1.0 "CHIEF J2" 230 "bB" "A" 14. 0.0 "inserts 14 PU shunt at Chief Jo" 1.5 "CHIEF J2" 230 "bB" "D" "removes shunt"
ST-CAL-S | Colorado River - Red Bluff #1 & 2 | C | 24 | 1.0 "BUS 24900" "FAULT 3PB IMPEDANCE X.XXX X.XXX" "" "ALWAYS" "" 1.067 "BRANCH 24900 24374 1" "OPEN" "" "ALWAYS" "" 1.067 "BRANCH 24900 24374 2" "OPEN" "" "ALWAYS
ST-CAL-N | Gates - Midway #1 & Diablo - Midway #2 500 kV | P2.3 | 30 | 1.0 "BUS 30060" "FAULT 3PB IMPEDANCE X.XXX X.XXX" "" "ALWAYS" "" 1.067 "BRANCH 30060 30055 1" "OPEN" "" "ALWAYS" "" 1.067 "BRANCH 30060 30057 2" "OPEN" "" "ALWAYS" "" |  | Switch file provided by Michael Detmers
ST-IMW-1 | N-1: Brownlee - Hells Canyon 230 kV Line | B | 60 | 1.0 "BRANCH 60095 60150 1" "FAULT 10 3PB SOLID" "" "ALWAYS" "" 1.067 "BRANCH 60095 60150 1" "OPEN" "" "ALWAYS" "" | Hells Canyon Generation Run Back
ST-UCN-1 | N-2: Daniel Park - Comanche #1 & #2 345 kV Lines SLG | C | 70 | 1.0 "BUS 70654" "FAULT 3PB IMPEDANCE X.XXX X.XXX" "" "ALWAYS" "" 1.067 "BRANCH 70654 70601 1" "OPEN" "" "ALWAYS" "" 1.067 "BRANCH 70654 70601 2" "OPEN" "" "ALWAYS" "" | N/A | Contingency definition verified by PSCo. Bus Fault at Comanchee with Daniel Park - Comanchee 1 & 2 345 kV opened 4 cycles after fault inception.
ST-CAL-S2 | N-1: North Gila - Imperial Valley 500kV line | P1 | 22 | 1.0 "BUS 22360" "FAULT 3PB SOLID" "ALWAYS" 1.067 "BRANCH 22536 22360 1" "OPEN" "ALWAYS" | N/A