## Linear MW
[5 empty] | MTRhrs: | 8
[5 empty] | m: | 0.125
|  | SERIES EQUIPMENT | SITE | FITS | MTBFhrs | FAILURE RATE | UNAVAIL. | DOWNTIME (min/yr)
[6 empty] | l | l / (l + m)
| 1 | TT | A | 4000 | 250000 | 4e-06 | 3.1999e-05 | 16.8302
| 2 | CB | A | 3000 | 333333.3333 | 3e-06 | 2.3999e-05 | 12.6227
| 3 | RF HS | A | 275 | 3636363.6364 | 2.75e-07 | 2.2e-06 | 1.1571
| 4 | Site Power (EG, Battery, Etc.) | A | 25 | 40000000 | 2.5e-08 | 2e-07 | 0.10519
| 5 | RF HS | B | 275 | 3636363.6364 | 2.75e-07 | 2.2e-06 | 1.1571
| 6 | RF HS/SD | B | 275 | 3636363.6364 | 2.75e-07 | 2.2e-06 | 1.1571
| 7 | Site Power (EG, Battery, Etc.) | B | 100 | 10000000 | 1e-07 | 8e-07 | 0.42077
| 8 | RF HS/SD | C | 275 | 3636363.6364 | 2.75e-07 | 2.2e-06 | 1.1571
| 9 | RF HS | C | 275 | 3636363.6364 | 2.75e-07 | 2.2e-06 | 1.1571
| 10 | Site Power (EG, Battery, Etc.) | C | 100 | 10000000 | 1e-07 | 8e-07 | 0.42077
| 11 | RF HS | D | 275 | 3636363.6364 | 2.75e-07 | 2.2e-06 | 1.1571
| 12 | CB | D | 3000 | 333333.3333 | 3e-06 | 2.3999e-05 | 12.6227
| 13 | TT | D | 4000 | 250000 | 4e-06 | 3.1999e-05 | 16.8302
| 14 | Site Power (EG, Battery, Etc.) | D | 25 | 40000000 | 2.5e-08 | 2e-07 | 0.10519
TOTAL: |  |  |  | 15900 |  | 1.59e-05 | 0.0001272 | 66.9004
|  |  | PATH |  |  |  | % Availability | ERRORED SECONDS
|  |  | A |  | B |  | 100% | 315.576
|  |  | B |  | C |  | 100% | 31.5576
|  |  | C |  | D |  | 100% | 315.576
[6 empty] | TOTAL ERRORED SEC. : |  | 662.7096
[6 empty] | TOTAL ERRORED MIN. : |  | 11.0452
[7 empty] | TOTAL DOWNTIME (min/yr): | 77.9456
[7 empty] | SOFTWARE/ PROCEDURAL DOWNTIME (min/yr): | 0
[7 empty] | CIRCUIT TOTAL DOWNTIME (min/yr): | 77.9456
[7 empty] | CIRCUIT AVAILABILITY: | 99.99%
MW
HS
CB
TT
CB
TT
Linear Microwave System
MW
HS
MW
HS/SD
MW
HS/SD
MW
HS
MW
HS
Site A
Site B
Site C
Site D
Path A-B
Path B-C
Path C-D

## SH Multi Ring - Fiber
[5 empty] | MTRhrs: | 8
[5 empty] | m: | 0.125
|  | SERIES EQUIPMENT (Ring Interface and End Equipment) | SITE | FITS | MTBFhrs | FAILURE RATE |  | FAILURE FREE STATE (P0) | UNAVAIL. (P1) | DOWNTIME (min/yr)
[6 empty] | l |  | m / (l + m) | l / (l + m)
| 1 | TT | A | 4000 | 250000 | 4e-06 |  | 0.99997 | 3.1999e-05 | 16.8302
| 2 | CB | A | 3000 | 333333.3333 | 3e-06 |  | 0.99998 | 2.3999e-05 | 12.6227
| 3 | DCS | A | 2000 | 500000 | 2e-06 |  | 0.99998 | 1.6e-05 | 8.4152
| 4 | DCS | D | 2000 | 500000 | 2e-06 |  | 0.99998 | 1.6e-05 | 8.4152
| 5 | DCS | J | 2000 | 500000 | 2e-06 |  | 0.99998 | 1.6e-05 | 8.4152
| 6 | CB | J | 3000 | 333333.3333 | 3e-06 |  | 0.99998 | 2.3999e-05 | 12.6227
| 7 | TT | J | 2000 | 500000 | 2e-06 |  | 0.99998 | 1.6e-05 | 8.4152
TOTAL: |  |  |  | 18000 | 55555.5556 | 1.8e-05 |  | 0.99986 | 0.000144 | 75.7366
[5 empty] | MTRhrs: | 8
[5 empty] | m: | 0.125
| RING |  |  | TOTAL EQUIP. FITS | MTBFhrs | FAILURE RATE | FAILURE FREE STATE (P0) | 1st FAILURE (P1) | UNAVAIL. (P2) | DOWNTIME (min/yr) | RING RESTORATIONS (/yr)
[6 empty] | l | m2 / ((l + m)2+l2) | 2lm / ((l + m)2+l2) | 2l2 / ((l + m)2+l2) | (P2)*525960 | 2*l*P0*365.25*24
| 1 |  |  | 28175.0001 | 35492.4578 | 2.8175e-05 | 0.99955 | 0.0004506 | 1.0156e-07 | 0.053419 | 0.49374
| 2 |  |  | 28175.0001 | 35492.4578 | 2.8175e-05 | 0.99955 | 0.0004506 | 1.0156e-07 | 0.053419 | 0.49374
3
4
5
TOTAL: |  |  |  | 56350.0001 | 17746.2289 | 5.635e-05 | 1 |  | 2.0313e-07 | 0.10684 | 0.98748
[5 empty] | MTRhrs: | 24
[5 empty] | m: | 0.041667
| RING |  |  | TOTAL FIBER FITS | MTBFhrs | FAILURE RATE | FAILURE FREE STATE (P0) | 1st FAILURE (P1) | UNAVAIL. (P2) | DOWNTIME (min/yr) | RING RESTORATIONS (/yr)
[6 empty] | l | m2 / ((l + m)2+l2) | 2lm / ((l + m)2+l2) | 2l2 / ((l + m)2+l2) | (P2)*525960 | 2*l*P0*365.25*24
| 1 |  |  | 59850 | 16708.4378 | 5.985e-05 | 0.99713 | 0.0028646 | 4.1147e-06 | 2.1641 | 1.0463
| 2 |  |  | 83790 | 11934.5984 | 8.379e-05 | 0.99599 | 0.0040058 | 8.0555e-06 | 4.2368 | 1.4631
3
4
5
TOTAL: |  |  |  | 143640 | 6961.8491 | 0.00014364 | 0.99999 |  | 1.217e-05 | 6.401 | 2.5094
TOTAL RING RESTORATIONS (/yr)
[9 empty] | TOTAL DOWNTIME (min/yr): | 82.2444 | 3.4969
[9 empty] | SOFTWARE/ PROCEDURAL DOWNTIME (min/yr): | 0
[9 empty] | CIRCUIT TOTAL DOWNTIME (min/yr): | 82.2444
[9 empty] | CIRCUIT AVAILABILITY: | 99.98%
Site B
DCS
CB
ADM
TT
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
DCS
DCS
CB
TT
RING 1
RING 2
Site A
Site J
Site C
Site D
Site H
Site E
Site L
Site F
Site G
Site I
Site K
Site M

## DH Multi Ring - Fiber
|  |  |  | MTRhrs: | 8
|  |  |  | m: | 0.125
PARALLEL EQUIPMENT (Ring Interface and End Equipment)
|  | SITE | TT | CHANNEL BANK | DCS | TOTAL EQUIPMENT PARALLEL FITS | l | UNAVAIL. | DOWNTIME (min/yr.)
| 1 | A (Ckt. 1) | 4000 | 3000 | 2000 | 2.56 | 2.56e-09 | 2.048e-08 | 0.010772
| 2 | A (Ckt. 2) | 4000 | 3000 | 0
| 3 | D (Ckt. 1) | 0 | 0 | 2000
| 4 | E (Ckt. 2) | 0 | 0 | 2000
| 5 | J (Ckt.1) | 4000 | 3000 | 2000
| 6 | J (Ckt. 2) | 4000 | 3000 | 0
0.010772
TOTAL:
|  |  |  | MTRhrs: | 8
|  |  |  | m: | 0.125
| RING |  | TOTAL EQUIP. FITS | MTBFhrs | FAILURE RATE | FAILURE FREE STATE (P0) | 1st FAILURE (P1) | UNAVAIL. (P2) | DOWNTIME (min/yr) | RING RESTORATIONS (/yr)
[5 empty] | l | m2 / ((l + m)2+l2) | 2lm / ((l + m)2+l2) | 2l2 / ((l + m)2+l2) | (P2)*525960 | 2*l*P0*365.25*24
| 1 |  | 28175.0001 | 35492.4578 | 2.8175e-05 | 0.99955 | 0.0004506 | 1.0156e-07 | 0.053419 | 0.49374
| 2 |  | 28175.0001 | 35492.4578 | 2.8175e-05 | 0.99955 | 0.0004506 | 1.0156e-07 | 0.053419 | 0.49374
3
4
5
TOTAL: |  |  | 56350.0001 | 17746.2289 | 5.635e-05 | 1 |  | 2.0313e-07 | 0.10684 | 0.98748
|  |  |  | MTRhrs: | 12
|  |  |  | m: | 0.083333
| RING |  | TOTAL FIBER FITS | MTBFhrs | FAILURE RATE | FAILURE FREE STATE (P0) | 1st FAILURE (P1) | UNAVAIL. (P2) | DOWNTIME (min/yr) | RING RESTORATIONS (/yr)
[5 empty] | l | m2 / ((l + m)2+l2) | 2lm / ((l + m)2+l2) | 2l2 / ((l + m)2+l2) | (P2)*525960 | 2*l*P0*365.25*24
| 1 |  | 59850 | 16708.4378 | 5.985e-05 | 0.99856 | 0.0014343 | 1.0301e-06 | 0.54181 | 1.0478
| 2 |  | 83790 | 11934.5984 | 8.379e-05 | 0.99799 | 0.0020069 | 2.0179e-06 | 1.0613 | 1.4661
3
4
5
TOTAL: |  |  | 143640 | 6961.8491 | 0.00014364 | 1 |  | 3.0481e-06 | 1.6032 | 2.5138
TOTAL RING RESTORATIONS (/yr)
[8 empty] | TOTAL DOWNTIME (min/yr): | 1.7208 | 3.5013
[8 empty] | SOFTWARE/ PROCEDURAL DOWNTIME (min/yr): | 0
[8 empty] | CIRCUIT TOTAL DOWNTIME (min/yr): | 1.7208
[8 empty] | CIRCUIT AVAILABILITY: | 100%
Site B
ADM
DCS
CB
TT
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
DCS
DCS
CB
TT
RING 1
RING 2
Site A
Site J
Site C
Site D
Site H
Site E
Site L
Site F
Site G
Site I
Site K
DCS
CB
TT
CB
TT

## FITS- Fiber Rings
|  |  |  | FIBER FITS (per MI or KM): | 342
|  |  |  | l: | 0.002924
| RING 1 - FIBER |  |  | RING 1 - EQUIPMENT
| SITE | FIBER DISTANCE TO NEXT (MI or KM) | TOTAL FIBER FITS | ADM FITS (1/2 NODE) | EDFA FITS | WAVE-SHIFTER FITS | SITE POWER FITS |  |  | TOTAL EQUIPMENT FITS
1 | A | 10 | 3420 | 4000 | 0 | 0 | 25 | 0 | 0 | 4025
2 | B | 15 | 5130 | 4000 | 5.13e-06 | 0 | 25 | 0 | 0 | 4025
3 | C | 20 | 6840 | 4000 | 6.84e-06 | 0 | 25 | 0 | 0 | 4025
4 | D | 25 | 8550 | 4000 | 8.55e-06 | 0 | 25 | 0 | 0 | 4025
5 | E | 30 | 10260 | 4000 | 1.026e-05 | 0 | 25 | 0 | 0 | 4025
6 | F | 35 | 11970 | 4000 | 1.197e-05 | 0 | 25 | 0 | 0 | 4025
7 | G | 40 | 13680 | 4000 | 1.368e-05 | 0 | 25 | 0 | 0 | 4025
|  |  | 59850 | [6 empty] | 28175.0001
| RING 2 - FIBER |  |  | RING 2 - EQUIPMENT
| SITE | FIBER DISTANCE TO NEXT (MI or KM) | TOTAL FIBER FITS | ADM FITS (1/2 NODE) | EDFA FITS | WAVE-SHIFTER FITS | SITE POWER FITS |  |  | TOTAL EQUIPMENT FITS
1 | D | 10 | 3420 | 4000 | 0 | 0 | 25 | 0 | 0 | 4025
2 | H | 20 | 6840 | 4000 | 6.84e-06 | 0 | 25 | 0 | 0 | 4025
3 | I | 30 | 10260 | 4000 | 1.026e-05 | 0 | 25 | 0 | 0 | 4025
4 | J | 40 | 13680 | 4000 | 1.368e-05 | 0 | 25 | 0 | 0 | 4025
5 | K | 50 | 17100 | 4000 | 1.71e-05 | 0 | 25 | 0 | 0 | 4025
6 | L | 60 | 20520 | 4000 | 2.052e-05 | 0 | 25 | 0 | 0 | 4025
7 | M | 35 | 11970 | 4000 | 1.197e-05 | 0 | 25 | 0 | 0 | 4025
|  |  | 83790 | [6 empty] | 28175.0001
Site B
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
RING 1
RING 2
Site A
Site J
Site C
Site D
Site H
Site E
Site L
Site F
Site G
Site I
Site K
Site M
Note: Telecom industry fiber failure rates are 342 FIT's per mile, or 212.5 FIT's per kilometer.

## DH Multi Ring - Fiber-MW
[5 empty] | MTRhrs: | 8
[5 empty] | m: | 0.125
PARALLEL EQUIPMENT (Ring Interface and End Equipment)
|  | SITE |  | TT | CHANNEL BANK | DCS | TOTAL EQUIPMENT PARALLEL FITS | l | UNAVAIL. | DOWNTIME (min/yr.)
| 1 | A (Ckt. 1) |  | 4000 | 3000 | 2000 | 2.24 | 2.24e-09 | 1.792e-08 | 0.0094252
| 2 | A (Ckt. 2) |  | 4000 | 3000 | 0
| 3 | D (Ckt. 1) |  | 0 | 0 | 2000
| 4 | E (Ckt. 2) |  | 0 | 0 | 0
| 5 | J (Ckt.1) |  | 4000 | 3000 | 2000
| 6 | J (Ckt. 2) |  | 4000 | 3000 | 0
[9 empty] | TOTAL: | 0.0094252
|  |  | RAYLEIGH FADING PATH |  |  |  | % Availability | ERRORED SECONDS
|  |  | J |  | K |  | 100% | 315.576
|  |  | K |  | L |  | 100% | 31.5576
|  |  | L |  | E |  | 100% | 315.576
[6 empty] | TOTAL ERRORED SEC. : |  | 662.7096
[6 empty] | TOTAL ERRORED MIN. (EM): |  | 11.0452
[6 empty] | STORM ERRORED MIN. (EM): |  | 5
[6 empty] | DOWNTIME (MIN.) : |  | 0.0201
Ring2: (P1FIBER+ P1EQUIP)*EM
[5 empty] | MTRhrs: | 8
[5 empty] | m: | 0.125
| RING |  |  | TOTAL EQUIP. FITS | MTBFhrs | FAILURE RATE | FAILURE FREE STATE (P0) | 1st FAILURE (P1) | UNAVAIL. (P2) | DOWNTIME (min/yr) | RING RESTORATIONS (/yr)
[6 empty] | l | m2 / ((l + m)2+l2) | 2lm / ((l + m)2+l2) | 2l2 / ((l + m)2+l2) | (P2)*525960 | 2*l*P0*365.25*24
| 1 |  |  | 28175.0001 | 35492.4578 | 2.8175e-05 | 0.99955 | 0.0004506 | 1.0156e-07 | 0.053419 | 0.49374
| 2 |  |  | 32175 | 31080.0311 | 3.2175e-05 | 0.99949 | 0.00051454 | 1.3244e-07 | 0.069659 | 0.5638
3
4
5
TOTAL: |  |  |  | 60350.0001 | 16570.0083 | 6.035e-05 | 1 |  | 2.3401e-07 | 0.12308 | 1.0575
[5 empty] | MTRhrs: | 12
[5 empty] | m: | 0.083333
| RING |  |  | TOTAL FIBER FITS | MTBFhrs | FAILURE RATE | FAILURE FREE STATE (P0) | 1st FAILURE (P1) | UNAVAIL. (P2) | DOWNTIME (min/yr) | RING RESTORATIONS (/yr)
[6 empty] | l | m2 / ((l + m)2+l2) | 2lm / ((l + m)2+l2) | 2l2 / ((l + m)2+l2) | (P2)*525960 | 2*l*P0*365.25*24
| 1 |  |  | 59850 | 16708.4378 | 5.985e-05 | 0.99856 | 0.0014343 | 1.0301e-06 | 0.54181 | 1.0478
| 2 |  |  | 30780 | 32488.629 | 3.078e-05 | 0.99926 | 0.00073817 | 2.7265e-07 | 0.1434 | 0.53924
3
4
5
TOTAL: |  |  |  | 90630 | 11033.874 | 9.063e-05 | 1 |  | 1.3028e-06 | 0.68522 | 1.587
TOTAL RING RESTORATIONS (/yr)
[9 empty] | TOTAL DOWNTIME (min/yr): | 0.81772 | 2.6446
[9 empty] | MW FADING DOWNTIME (min/yr): | 0.0201
[9 empty] | SOFTWARE/ PROCEDURAL DOWNTIME (min/yr): | 0
[9 empty] | CIRCUIT TOTAL DOWNTIME (min/yr): | 0.83782
[9 empty] | CIRCUIT AVAILABILITY: | 100%
Site B
ADM
DCS
CB
TT
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
DCS
RING 1
RING 2
Site A
Site J
Site C
Site D
Site H
Site E
Site L
Site F
Site G
Site I
Site K
DCS
CB
TT
ADM
DCS
CB
TT
CB
TT
MW
HS
MW
HS
MW
HS/SD
MW
HS/SD
MW
HS
MW
HS
Path L-E
Path K-L
Path J-K
Note: User must adjust formula to reference correct
ring P1 fiber and equipment failure probabilities.

## FITS- Fiber-MW Rings
|  |  |  | FIBER FITS (per MI or KM): | 342
|  |  |  | l: | 0.002924
| RING 1 - FIBER |  |  | RING 1 - EQUIPMENT
| SITE | FIBER DISTANCE TO NEXT (MI orKM) | TOTAL FIBER FITS | ADM FITS (1/2 NODE) | EDFA FITS | WAVE-SHIFTER FITS | SITE POWER FITS |  |  | TOTAL EQUIPMENT FITS
1 | A | 10 | 3420 | 4000 | 0 | 0 | 25 | 0 | 0 | 4025
2 | B | 15 | 5130 | 4000 | 5.13e-06 | 0 | 25 | 0 | 0 | 4025
3 | C | 20 | 6840 | 4000 | 6.84e-06 | 0 | 25 | 0 | 0 | 4025
4 | D | 25 | 8550 | 4000 | 8.55e-06 | 0 | 25 | 0 | 0 | 4025
5 | E | 30 | 10260 | 4000 | 1.026e-05 | 0 | 25 | 0 | 0 | 4025
6 | F | 35 | 11970 | 4000 | 1.197e-05 | 0 | 25 | 0 | 0 | 4025
7 | G | 40 | 13680 | 4000 | 1.368e-05 | 0 | 25 | 0 | 0 | 4025
|  |  | 59850 | [6 empty] | 28175.0001
| RING 2 - FIBER |  |  | RING 2 - EQUIPMENT
| SITE | FIBER DISTANCE TO NEXT (MI orKM) | TOTAL FIBER FITS | ADM FITS (1/2 NODE) | EDFA FITS | WAVE-SHIFTER FITS | SITE POWER FITS | MW |  | TOTAL EQUIPMENT FITS
1 | D | 10 | 3420 | 4000 | 0 | 0 | 25 | 0 | 0 | 4025
2 | H | 20 | 6840 | 4000 | 6.84e-06 | 0 | 25 | 0 | 0 | 4025
3 | I | 30 | 10260 | 4000 | 1.026e-05 | 0 | 25 | 0 | 0 | 4025
4 | J | 40 | 13680 | 4000 | 1.368e-05 | 0 | 25 | 2000 | 0 | 6025
5 | K | 0 | 0 | 0 | 0 | 0 | 25 | 4000 | 0 | 4025
6 | L | 0 | 0 | 0 | 0 | 0 | 25 | 4000 | 0 | 4025
7 | E | 0 | 0 | 4000 | 0 | 0 | 25 | 2000 | 0 | 6025
|  |  | 30780 | [6 empty] | 32175
Site B
ADM
DCS
CB
TT
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
ADM
DCS
RING 1
RING 2
Site A
Site J
Site C
Site D
Site H
Site E
Site L
Site F
Site G
Site I
Site K
DCS
CB
TT
ADM
DCS
CB
TT
CB
TT
MW
HS
MW
HS
MW
HS/SD
MW
HS/SD
MW
HS
MW
HS
Path L-E
Path K-L
Path J-K
Note: Telecom industry fiber failure rates are 342 FIT's per mile, or 212.5 FIT's per kilometer.