## Gens
Gen
Area Num of Gen | Area Name of Gen | Owner Number 1 | Owner Name 1 | Data Maintainer | Number of Bus | ID | ID | CASE Gen Min>Max | CASE Missing BA | CASE Pmax>GovMWCap | CASE Unapp Gen Model | EXCEED Gen Limit | NERC At Mvar Limit | NERC Limit Power Fact | NERC PSS No Ex | NERC RX Ratio | NERC Unreas H | NERC Unreas Sat | POWER Gen at 0.0 | POWER Gen on HV | POWER Miss Tag | POWER Miss Turbine Type | POWER Missing Model | POWER Missing PS | POWER Missing Sub R/X | POWER No Owner | Min MW | Max MW | Min Mvar | Max Mvar | BA Num of Gen | MWCap-MWMax | Gov_MWCap | Motor1 Exempt? | Machine | Stabilizer | Governor | Exciter | Status | Gen MW | Gen Mvar | Unit Type Code | MVA Base | Gen Power Factor Violation | Use Capability Curve | R (Internal Resistance) | X (Internal Reactance) | Inertia (Unit Base) | H (system base) | S1 | S12 | Saturation Ratio | Nom kV of Bus | BES Exempt? | GE Long ID | Unit Type | ID | Netting Exempt? | PSS Exempt?
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10425 | 02 | 02 | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | [7 empty] | -52.944 | 52.944 | -37.693 | 37.693 | 130 | -52.944 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 2.3725 | BA | 65 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.9 |  |  | BA (Energy Storage, Battery) | 02
10 | NEW MEXICO | 151 | Lighthouse Renewables Corp |  | 10564 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | [7 empty] | -20.3 | 20.3 | -12.8 | 12.8 | 130 | -20.3 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 1.2872 | BA | 24 | PF<-0.85 | NO | 0 | 0.833 | 0 |  |  |  | NAN | 0.38 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 129 | PN2 New Mexico |  | 10636 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -76.2 | 76.2 | -75.56 | 75.56 | 130 | -76.2 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 1.0875 | BA | 76.219 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 129 | PN2 New Mexico |  | 10641 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -76.2 | 76.2 | -75.56 | 75.56 | 130 | -76.2 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | -0.18409 | BA | 76.219 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10718 | 04 | 04 | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | [7 empty] | -52.944 | 52.944 | -37.693 | 37.693 | 130 | -52.944 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 2.3725 | BA | 65 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.9 |  |  | BA (Energy Storage, Battery) | 04
10 | NEW MEXICO | 129 | PN2 New Mexico |  | 10744 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -13.709 | 13.709 | -7.0163 | 7.0163 | 130 | -13.709 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 4.9689 | BA | 15.4 |  | NO | 9999 | 9999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 129 | PN2 New Mexico |  | 10750 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -15.667 | 15.667 | -8.0187 | 8.0187 | 130 | -15.667 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 5.3689 | BA | 17.6 |  | NO | 9999 | 9999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 129 | PN2 New Mexico |  | 10751 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -14.688 | 14.688 | -7.5175 | 7.5175 | 130 | -14.688 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 4.969 | BA | 16.5 |  | NO | 9999 | 9999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 451 | NextEra Energy |  | 10753 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -52.14 | 52.14 | -17.14 | 17.14 | 130 | -52.14 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 2.9824 | BA | 54.88 |  | NO | 0 | 100000 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 451 | NextEra Energy |  | 10756 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -107.58 | 107.58 | -35.19 | 35.19 | 130 | -107.58 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 2.9822 | BA | 113.19 |  | NO | 0 | 100000 | 0 |  |  |  | NAN | 0.645 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 451 | NextEra Energy |  | 10759 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -23.94 | 23.94 | -7.87 | 7.87 | 130 | -23.94 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 2.9822 | BA | 25.2 |  | NO | 0 | 100000 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 233 | JANPA |  | 10835 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | [7 empty] | -51.9 | 51.9 | -41.181 | 41.181 | 130 | -51.9 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 0.25817 | BA | 66.25 | PF<0.8 | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10837 | 2 | 2 | [11 empty] | Gen at 0.0 | [7 empty] | -150 | 202 | -116.295 | 116.295 | 130 | -202 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 22.4708 | BA | 266.8 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.48 |  | BESS-1 | BA (Energy Storage, Battery) | 2
10 | NEW MEXICO | 130 | PN1 New Mexico |  | 10839 | 4 | 4 | [11 empty] | Gen at 0.0 | [7 empty] | -150 | 202 | -116.295 | 116.295 | 130 | -202 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 22.4708 | BA | 266.8 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.48 |  | BESS-2 | BA (Energy Storage, Battery) | 4
10 | NEW MEXICO | 129 | PN2 New Mexico |  | 10976 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -60 | 60.5 | -50.12 | 114.38 | 130 | -60.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 179.2 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  |  | BA (Energy Storage, Battery) | 1
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11248 | PV | PV | [5 empty] | At Mvar Limit | [13 empty] | 0 | 150 | -49.3 | 49.3 | 125 | -150 |  |  | REGC_A |  |  | REEC_A | Closed | 149 | 49.3 | PV | 157.9 |  | NO | 0 | 10000000 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV
11 | EL PASO | 100 | Clearwater Power Company |  | 11362 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 52.8 | -15.84 | 15.84 | 125 | -52.8 | [6 empty] | Closed | 50 | -2.0387 | P3 | 52.8 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | 1
11 | EL PASO | 100 | Clearwater Power Company |  | 11363 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 52.8 | -15.84 | 15.84 | 125 | -52.8 | [6 empty] | Closed | 51 | -2.1293 | P3 | 52.8 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | 2
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11402 | PV | PV | [5 empty] | At Mvar Limit | [13 empty] | 0 | 10 | -1.4256 | 1.4256 | 125 | -10 |  |  | PVD1 |  |  |  | Closed | 9 | 1.4256 | PV | 10.1 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV |  | PSS Exempt
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11403 | PV | PV | [5 empty] | At Mvar Limit | [13 empty] | 0 | 10 | -1.4256 | 1.4256 | 125 | -10 |  |  | PVD1 |  |  |  | Closed | 9 | 1.4256 | PV | 10.1 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV |  | PSS Exempt
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11414 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 133.386 | -55.513 | 55.513 | 125 | -133.386 | [6 empty] | Closed | 132 | -55.513 | P3 | 144.48 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | P3 (Photovoltaic, Fixed) | 1
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11427 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 79.2904 | -44.0811 | 44.0811 | 125 | -79.2904 | [6 empty] | Closed | 78 | 18.9789 | PV | 90.72 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | Gen Type1 x 24 | PV (Photovoltaic) | 1
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11429 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 0 | 75.9867 | -42.2444 | 42.2444 | 125 | -75.9867 | [6 empty] | Closed | 75 | 18.9789 | PV | 86.94 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | Gen Type1 x 23 | PV (Photovoltaic) | 3
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11441 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10.2 | -4.75 | 4.75 | 125 | -10.2 | [6 empty] | Closed | 9 | -1.5888 | WT | 11.25 |  | NO | 9999 | 9999 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | 1
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11446 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 100.002 | -56.664 | 56.664 | 125 | -100.002 | [6 empty] | Closed | 99 | -19.0698 | P4 | 114.94 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.645 |  | SS100S_PV | P4 (Photovoltaic, Tracking) | PV
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11452 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 50.001 | -28.332 | 28.332 | 125 | -50.001 | [6 empty] | Closed | 49 | 27.2506 | P4 | 57.47 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.645 |  | SS50S_PV | P4 (Photovoltaic, Tracking) | PV
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11460 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 5 | -0.7125 | 0.7125 | 125 | -5 | [6 empty] | Closed | 4.5 | 0 | PV | 5.051 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11461 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 5 | -0.7125 | 0.7125 | 125 | -5 | [6 empty] | Closed | 4.5 | 0 | PV | 5.051 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11462 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 5 | -0.7125 | 0.7125 | 125 | -5 | [6 empty] | Closed | 4.5 | 0 | PV | 5.051 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11463 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 5 | -0.7125 | 0.7125 | 125 | -5 | [6 empty] | Closed | 4.5 | 0 | PV | 5.051 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11464 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 5 | -0.7125 | 0.7125 | 125 | -5 | [6 empty] | Closed | 4.5 | 0 | PV | 5.051 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV
11 | EL PASO | 125 | EPE El Paso Electric Company |  | 11465 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 5 | -0.7125 | 0.7125 | 125 | -5 | [6 empty] | Closed | 4.5 | 0 | PV | 5.051 |  | NO | 1 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | PV
10 | NEW MEXICO | 126 | LAC New Mexico |  | 13300 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12.6 | -8.3 | 8.3 | 130 | -2e-07 | 12.6 |  | GENTPJ |  | HYGOV | EXST1_GE | Closed | 8 | 1.4299 | HY | 12.6 | PF<-0.85 | NO | 0 | 0.2 | 3.8 | 0.4788 | 0.08 | 0.4 | 5 | 4.16 |  | COYOTE_J_4.16_ABIQUIU | HY (Hydro) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14812 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | 0.3428 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_W1 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14813 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | -1.7517 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_W2 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14814 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | -0.45185 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_W3 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14816 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | -5.5343 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_E1 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14817 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | 0.25639 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_E2 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 937 | Avangrid Renewables LLC Iberdrol |  | 14818 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21 | -8.9 | 3 | 2 | -21 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 10.7 | 1.4626 | W3 | 21 |  | NO | 0.005 | 0.212 | 0 |  |  |  | NAN | 0.6 |  | HASHKNIF_69_DRYLAKE_WIND_E3 | W3 (Wind Turbine, Type 3) | 1
14 | APS | 2 | Arizona Public Service |  | 14837 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -17.3 | 17.3 | -10.95 | 10.95 | 2 | -17.3 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 20.475 | PF<-0.85 | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.434 |  | Q300 Cotton Center BESS | BA (Energy Storage, Battery) | 1
14 | APS | 2 | Arizona Public Service |  | 14841 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -17 | 17 | -11.41 | 11.41 | 2 | -17 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 20.475 | PF<-0.85 | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.434 |  | Q305 Paloma BESS | BA (Energy Storage, Battery) | 1
14 | APS | 2 | Arizona Public Service |  | 14860 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 208.07 | -68.389 | 68.389 | 2 | -208.07 |  |  | REGC_A |  |  | REEC_A | Closed | 200 | 68.389 | PV | 219.02 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 34.5 |  | Q225 White Wing Ranch PV | PV (Photovoltaic) | 1
14 | APS | 995 | Yuma Cogeneration Associates |  | 14938 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 40 | -4 | 21 | 2 | 9 | 49 |  | GENTPF |  | GGOV1 | EXST4B | Open | 0 | 0 | CS | 49 |  | NO | 0 | 0.2 | 5.85 | 2.8665 | 0.1429 | 0.3913 | 2.7383 | 13.8 |  | YUMACO_13.8_CT1 | CS (Combined Cycle Single Shaft) | 1
14 | APS | 2 | Arizona Public Service |  | 14988 | 12 | 12 | [9 empty] | Unreas H | [9 empty] | 0 | 41 | -17 | 62 | 2 | 10.25 | 51.25 |  | GENROU | PSS2A | GGOV1 | EXAC8B | Open | 0 | 0 | JE | 71.17 | PF<0.8 | YES | 0.002 | 0.181 | 1.17 | 0.83269 | 0.112 | 0.461 | 4.1161 | 13.8 |  | SUNDAPS_ | JE (Jet Engine) | 12
14 | APS | 2 | Arizona Public Service |  | 14989 | 11 | 11 | [9 empty] | Unreas H | [9 empty] | 0 | 41 | -17 | 62 | 2 | 10.25 | 51.25 |  | GENROU | PSS2A | GGOV1 | EXAC8B | Open | 0 | 0 | JE | 71.17 | PF<0.8 | YES | 0.002 | 0.181 | 1.17 | 0.83269 | 0.112 | 0.461 | 4.1161 | 13.8 |  | SUNDAPS_ | JE (Jet Engine) | 11
15 | SRP | 80 | Salt River Project | SRP | 15845 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 20 | 0 | 0 | 80 | -20 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | QueenCreek_Solar_1 | PV (Photovoltaic) | 1
15 | SRP | 80 | Salt River Project | SRP | 15961 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 13 | -5.2 | 5.1 | 80 | 0.9 | 13.9 |  | GENTPJ | PSS2A | GPWSCC | EXST4B | Closed | 12 | 5.1 | HY | 13.9 |  | YES | 0.039 | 2.77 | 2.02 | 0.28078 | 0.074 | 0.175 | 2.3649 | 11 |  | STEWMNTN_11_U1_GRS | HY (Hydro) | 1
15 | SRP | 80 | Salt River Project | SRP | 15973 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 80 | -10 | [6 empty] | Closed | 5 | 0 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | CopperCrossing_PV_1 | PV (Photovoltaic) | 1
15 | SRP | 80 | Salt River Project | SRP | 15974 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 80 | -10 | [6 empty] | Closed | 5 | 0 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | CopperCrossing_PV2 | PV (Photovoltaic) | 1
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17000 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 30 | 0 | 0 | 4 | -30 |  |  | DER_A |  |  |  | Closed | 13.77 | 0 | BA | 30 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Apache_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17000 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 40.5 | 0 | 0 | 4 | -40.5 |  |  | DER_A |  |  |  | Closed | 26.73 | 0 | P3 | 40.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Apache_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17026 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 70.03 | -4.3769 | 30.6969 | 4 | 0.0010022 | 70.031 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 63 | -4.3769 | GT | 87.5 |  | YES | 0.003 | 0.27 | 8.02 | 7.0175 | 0.14 | 0.396 | 2.8286 | 13.8 |  | APACHE_13.8_GT-3 | GT (Gas Turbine) | 1 |  | PSS Exempt
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17300 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 30 | 0 | 0 | 4 | -30 |  |  | DER_A |  |  |  | Closed | 22.7 | 0 | BA | 30 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Longtin_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17300 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 31 | 0 | 0 | 4 | -31 |  |  | DER_A |  |  |  | Closed | 20.46 | 0 | P3 | 31 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 69 | BES Exempt | Longtin_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17602 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 15 | 0 | 0 | 4 | -15 |  |  | DER_A |  |  |  | Closed | 8.4 | 0 | BA | 15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 24.9 |  | Marana_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17602 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 4 | -10 |  |  | DER_A |  |  |  | Closed | 6.6 | 0 | P3 | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 24.9 |  | Marana_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17607 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 4 | -10 |  |  | DER_A |  |  |  | Closed | 10 | 0 | P3 | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 24.9 |  | Sahuraita_Aggregate_Battery | P3 (Photovoltaic, Fixed) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17620 | BT | BT | [17 empty] | Missing Sub R/X |  | 0 | 15 | 0 | 0 | 4 | -15 |  |  | DER_A |  |  |  | Closed | 8.4 | 0 | BA | 15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 115 | BES Exempt | ORACLE-AE_Aggregate_Battery | BA (Energy Storage, Battery) | BT
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 17620 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 4 | -10 |  |  | DER_A |  |  |  | Closed | 6.6 | 0 | P3 | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 115 | BES Exempt | ORACLE-AE_Aggregate_Solar | P3 (Photovoltaic, Fixed) | PV
18 | NEVADA | 18 | N3 Nevada |  | 18277 | ST | ST | [16 empty] | Missing PS |  |  | 27.2 | 29.1 | -10.1769 | 15.6359 | 24 | -29.1 |  |  | GENROU |  |  | ESAC1A | Closed | 27.7448 | 9.2125 | CA | 33 |  | YES | 0 | 0.269 | 5.187 | 1.7117 | 0.11 | 0.455 | 4.1364 | 13.8 |  | PABCO_13.2_GEN4 | CA (Combined Cycle Steam Part) | ST
18 | NEVADA | 18 | N3 Nevada |  | 18282 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 14 | 38 | -14.275 | 30.7 | 24 | 4.8e-07 | 38 |  | GENROU |  | GGOV1 | ESST1A_GE | Closed | 26.75 | 11.1803 | CT | 45.2 | PF<0.8 | YES | 0.005 | 0.17 | 5.17 | 2.3368 | 0.04 | 0.357 | 8.925 | 13.8 |  | SAGUARO2_13.8_SAGUARO_1 | CT (Combined Cycle Combustion Turbine Part) | 1 |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18283 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 14 | 38 | -14.275 | 30.7 | 24 | 4.8e-07 | 38 |  | GENROU |  | GGOV1 | ESST1A_GE | Closed | 26.75 | 11.4456 | CT | 45.2 | PF<0.8 | YES | 0.005 | 0.17 | 5.17 | 2.3368 | 0.04 | 0.357 | 8.925 | 13.8 |  | SAGUARO2_13.8_SAGUARO_2 | CT (Combined Cycle Combustion Turbine Part) | 2 |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18566 | PV | PV | [5 empty] | At Mvar Limit | [13 empty] | 0 | 149.1 | -72.06 | 72.06 | 24 | -149.1 |  |  | REGC_A |  |  | REEC_A | Closed | 145.3 | 72.06 | PV | 169.4 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | CMS5-G1_0.36_1 | PV (Photovoltaic) | PV |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18571 | PV | PV | [5 empty] | At Mvar Limit | [13 empty] | 0 | 103.5 | -48.67 | 48.67 | 24 | -103.5 |  |  | REGC_A |  |  | REEC_A | Closed | 90.2 | 48.67 | PV | 169.4 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | CMS5-G1_0.36_2 | PV (Photovoltaic) | PV |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18699 | B | B | [9 empty] | Unreas H | [9 empty] | 20.3 | 43.2 | -13.443 | 60.6075 | 24 | 2.96 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Closed | 25.5699 | 3.0811 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN3_2 | CT (Combined Cycle Combustion Turbine Part) | B
18 | NEVADA | 18 | N3 Nevada |  | 18700 | B | B | [9 empty] | Unreas H | [9 empty] | 18.9 | 45.1 | -13.353 | 60.3825 | 24 | 1.06 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Closed | 26.4699 | 3.5865 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN2_2 | CT (Combined Cycle Combustion Turbine Part) | B
18 | NEVADA | 18 | N3 Nevada |  | 18702 | A | A | [9 empty] | Unreas H | [9 empty] | 19.3 | 43 | -12.76 | 58.9 | 24 | 3.16 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Closed | 32.4 | 7.741 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN2_1 | CT (Combined Cycle Combustion Turbine Part) | A
18 | NEVADA | 18 | N3 Nevada |  | 18703 | A | A | [9 empty] | Unreas H | [9 empty] | 20.1 | 46 | -12.76 | 58.9 | 24 | 0.16 | 46.16 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Closed | 32.4 | 7.7588 | CT | 71.176 | PF<0.8 | YES | 0.005 | 0.18 | 1.19 | 0.84699 | 0.111 | 0.341 | 3.0721 | 13.8 |  | LVCOGEN_13.8_GEN3_1 | CT (Combined Cycle Combustion Turbine Part) | A
18 | NEVADA | 18 | N3 Nevada |  | 18781 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 210.7 | -83.8313 | 83.8313 | 24 | -210.7 |  |  | REGC_A |  |  | REEC_A | Closed | 204.9 | 12.928 | PV | 223.65 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | EGLESHDWG1_0.63_1 | PV (Photovoltaic) | 1
18 | NEVADA | 18 | N3 Nevada |  | 18782 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 95 | -55.8573 | 55.8573 | 24 | -95 |  |  | REGC_A |  |  | REEC_A | Closed | 84.1 | 12.9283 | PV | 100.8 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | EGLESHDWG2_0.63_2 | PV (Photovoltaic) | 1
14 | APS | 2 | Arizona Public Service |  | 148214 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 103.275 | -50.0184 | 50.0184 | 2 | -103.275 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 114.75 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.55 |  | Solar | PV (Photovoltaic) | 1
18 | NEVADA | 18 | N3 Nevada |  | 18874 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 3 | 30 | -9.9 | 9.9 | 24 | -30 |  |  | WT4G |  |  | WT4E | Closed | 6.4692 | -3.6527 | PV | 32 |  | NO | 1 | 10 | 0 |  |  |  | NAN | 0.4 |  | SILVST_34.5_PV1 | PV (Photovoltaic) | 1 |  | PSS Exempt
18 | NEVADA | 18 | N3 Nevada |  | 18884 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 30 | -33.12 | 33.12 | 24 | -30 |  |  | REGC_A |  |  | REEC_A | Closed | 22.4 | 0.72874 | PV | 33.12 | PF<0.8 | NO | 1 | 10 | 0 |  |  |  | NAN | 0.38 |  | SPECTRUM_0.38_GEN | PV (Photovoltaic) | 1 |  | PSS Exempt
19 | WAPA L.C. | 50 | US Bur Reclam |  | 19031 | A8 | A8 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 41 | -32 | 17 | 4 | 22 | 63 |  | GENTPJ | PSS2C | HYG3 | DC4C | Closed | 41 | 9.1992 | HY | 63.077 | PF<-0.85 | NO | 0.003 | 0.162 | 2.5 | 1.5769 | 0.1 | 0.52 | 5.2 | 16.5 |  | HOOVER_16.5_HVA8 | HY (Hydro) | A8
19 | WAPA L.C. | 50 | US Bur Reclam |  | 19031 | A9 | A9 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 41 | -29 | 17 | 4 | 30 | 71 |  | GENTPJ | PSS2C | HYG3 | DC4C | Closed | 41 | 9.1992 | HY | 70.256 | PF<-0.85 | NO | 0.003 | 0.175 | 3.6 | 2.5292 | 0.08 | 0.48 | 6 | 16.5 |  | HOOVER_16.5_HVA9 | HY (Hydro) | A9
19 | WAPA L.C. | 470 | Calpine Corp. |  | 19318 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 175 | -55 | 82 | 4 | 11 | 186 |  | GENROU | PSS2A | GGOV1 | ESST1A_GE | Closed | 175 | 82 | GT | 236 |  | NO | 0 | 0.21 | 4.767 | 11.2501 | 0.098 | 0.307 | 3.1327 | 18 |  | SOPOINT_16_UN_B | GT (Gas Turbine) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20006 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 160 | -50 | 70 | 111 | -2.38e-06 | 160 |  | GENROU | PSS2A | TGOV1 | EXST1_GE | Closed | 141.11 | 21.3019 | GT | 177.78 |  | NO | 0 | 0.199 | 3.69 | 6.5601 | 0.0522 | 0.1439 | 2.7567 | 15 |  | PJZ230_15_UNIT_5 | GT (Gas Turbine) | 5
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20007 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 160 | -50 | 70 | 111 | -2.38e-06 | 160 |  | GENROU | PSS2A | TGOV1 | EXST1_GE | Closed | 137.11 | 19.9648 | GT | 177.78 |  | NO | 0 | 0.199 | 3.69 | 6.5601 | 0.0522 | 0.1439 | 2.7567 | 15 |  | PJZ230_15_UNIT_6 | GT (Gas Turbine) | 6
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20141 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 30 | -10 | 12 | 111 | -1.19e-06 | 30 |  | GENROU |  | GGOV1 | EXDC1 | Closed | 28.24 | 2.2926 | BT | 35.3 |  | NO | 0.003 | 0.231 | 6.3 | 2.2239 | 0.28 | 0.886 | 3.1643 | 13.8 |  | CPU_13.8_UNIT_5 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 5 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20143 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Closed | 25 | 2.1819 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT10 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20144 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Closed | 25 | 2.1819 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT11 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20145 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Open | 0 | 0 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT12 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20146 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 27.27 | -10 | 12 | 111 | -1.17e-06 | 27.27 |  | GENROU |  | GGOV1 | EXAC1 | Open | 0 | 0 | BT | 30.33 |  | NO | 0 | 0.231 | 3.9593 | 1.2009 | 0.1875 | 0.65 | 3.4667 | 13.8 |  | CPC_13.8_UNIT13 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 4 |  | PSS Exempt
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20416 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 93 | 189 | -85 | 105 | 111 | 1.43e-06 | 189 |  | GENROU | PSS2B | GGOV1 | EXST4B | Closed | 173.0559 | 19.6025 | CT | 210 |  | NO | 0.002 | 0.12 | 5.421 | 11.3841 | 0.0705 | 0.6205 | 8.8014 | 18 |  | BJT230_18_GTG | CT (Combined Cycle Combustion Turbine Part) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20578 | SV | SV | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 0 | -250 | 350 | 111 | 0 | [6 empty] | Open | 0 | 0 | OT | 600 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 20 |  | MSC230_2 | OT (Other) | SV
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20598 | 1 | 1 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U1 | JE (Jet Engine) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20599 | 2 | 2 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U2 | JE (Jet Engine) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20600 | 3 | 3 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U3 | JE (Jet Engine) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20601 | 4 | 4 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U4 | JE (Jet Engine) | 4
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20602 | 5 | 5 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U5 | JE (Jet Engine) | 5
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20603 | 6 | 6 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U6 | JE (Jet Engine) | 6
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20604 | 7 | 7 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U7 | JE (Jet Engine) | 7
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20605 | 8 | 8 | [16 empty] | Missing PS |  |  | 20 | 29.4 | 0 | 9 | 111 | -29.4 | [6 empty] | Open | 0 | 0 | JE | 34.59 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | GOR-TG-U8 | JE (Jet Engine) | 8
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20611 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 15.38 | 1.6655 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B1-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20611 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 15.38 | 1.6655 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B1-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20611 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 15.38 | 1.6655 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B1-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20612 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 15.38 | 1.6655 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B2-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20612 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 15.38 | 1.6655 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B2-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20612 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 15.38 | 1.6655 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B2-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20613 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B3-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20613 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B3-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20613 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B3-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20614 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B4-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20614 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B4-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20614 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B4-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20615 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B5-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20615 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B5-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20615 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B5-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20616 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B6-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20616 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B6-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20616 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B6-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20617 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B7-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20617 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B7-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20617 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B7-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20618 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B8-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20618 | 2 | 2 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B8-U2 | IC (Internal Combustion) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20618 | 3 | 3 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 19.85 | -9.75 | 15.05 | 111 | -19.85 | [6 empty] | Closed | 14.79 | 1.5135 | IC | 20.2 | PF<0.8 | NO | 0 | 1.613 | 0 |  |  |  | NAN | 13.8 |  | MCI-B8-U3 | IC (Internal Combustion) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20660 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 0 | -12.5 | 25 | 111 | 0 |  |  | GENROU |  |  | EXAC1 | Closed | 0 | 1.1388 | SC | 37.5 | PF<0.8 | NO | 0 | 0.267 | 3.9593 | 1.4847 | 0.1875 | 0.65 | 3.4667 | 13.2 |  | FPP-01-CS | SC (Synchronous Condenser) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20670 | 2 | 2 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 0 | -12.5 | 25 | 111 | 0 |  |  | GENROU |  |  | EXAC1 | Open | 0 | 0 | SC | 37.5 | PF<0.8 | NO | 0 | 0.267 | 3.9593 | 1.4847 | 0.1875 | 0.65 | 3.4667 | 13.2 |  | FPP-02-CS | SC (Synchronous Condenser) | 2
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20680 | 3 | 3 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 0 | -12.5 | 25 | 111 | 0 |  |  | GENROU |  |  | EXAC1 | Open | 0 | 0 | SC | 37.5 | PF<0.8 | NO | 0 | 0.267 | 3.9593 | 1.4847 | 0.1875 | 0.65 | 3.4667 | 13.2 |  | FPP-03-CS | SC (Synchronous Condenser) | 3
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20914 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 57.6 | 0 | 27 | 111 | -57.6 | [6 empty] | Closed | 43.49 | 1.3105 | IC | 62.52 |  | NO | 0 | 0.301 | 0 |  |  |  | NAN | 13.8 |  | CIA-U1 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20915 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 48 | 0 | 22.5 | 111 | -48 | [6 empty] | Closed | 43.49 | 1.3105 | IC | 52.12 |  | NO | 0 | 0.362 | 0 |  |  |  | NAN | 13.8 |  | CIA-U2 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20916 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 57.6 | 0 | 27 | 111 | -57.6 | [6 empty] | Closed | 43.49 | 1.3105 | IC | 62.52 |  | NO | 0 | 0.301 | 0 |  |  |  | NAN | 13.8 |  | CIA-U3 | IC (Internal Combustion) | 1
20 | MEXICO-CFE | 111 | CFE - Mexico |  | 20917 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 48 | 0 | 22.5 | 111 | -48 | [6 empty] | Closed | 43.49 | 1.3105 | IC | 52.12 |  | NO | 0 | 0.362 | 0 |  |  |  | NAN | 13.8 |  | CIA-U4 | IC (Internal Combustion) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21012 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.375 | -2.6 | 2.6 | 16 | 7e-08 | 4.375 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 3.5649 | 0.65883 | ST | 4.375 |  | NO | 0 | 0.11 | 1.693 | 0.074069 | 0.05 | 1.18 | 23.6 | 13.8 |  | HEBER_6_HEBER1 | ST (Steam Turbine) | 12
21 | IID | 16 | Imperial Irrigation District |  | 21020 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 24 | 47 | -32 | 32 | 16 | 1.2e-07 | 47 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 40.7 | 4.6488 | CA | 54 | PF<-0.85 | NO | 0 | 0.14 | 5.5 | 2.97 | 0.075 | 0.22 | 2.9333 | 13.8 |  | ELCEN92_6_ELSTM.3 | CA (Combined Cycle Steam Part) | 1
21 | IID | 16 | Imperial Irrigation District |  | 21021 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 24 | 47 | -32 | 32 | 16 | 1.2e-07 | 47 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 40.7 | 4.5118 | CA | 54 | PF<-0.85 | NO | 0 | 0.14 | 5.5 | 2.97 | 0.075 | 0.22 | 2.9333 | 13.8 |  | ELCEN92_6_ELSTM.3 | CA (Combined Cycle Steam Part) | 1 |  | PSS Exempt
21 | IID | 211 | IID Independent Power Producer |  | 21026 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 20 | -2.82 | 2.82 | 16 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 16 | 2.82 | PV | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.42 |  | ELCEN92_6_SOL.GEN | PV (Photovoltaic) | 1 |  | PSS Exempt
21 | IID | 211 | IID Independent Power Producer |  | 21116 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -151.73 | 151.73 | -99.6 | 99.6 | 16 | -151.73 |  |  | REGC_A |  |  | REEC_C | Closed | 62.507 | 25.9639 | BA | 181.5 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21386 | 1 | 1 | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 70.875 | -34.25 | 34.25 | 16 | -70.875 |  |  | REGC_A |  |  |  | Closed | 70.875 | -8.6229 | UN | 78.75 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | SEVILLE_6_SEVILLE3 | UN (Unknown) | 1
21 | IID | 16 | Imperial Irrigation District |  | 21649 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 14 | 58 | -40 | 40 | 16 | -58 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 52 | -3.3314 | CA | 77.5 | PF<-0.85 | NO | 0 | 0.164 | 4.5 | 3.4875 | 0.101 | 0.585 | 5.7921 | 13.8 |  | ELCEN92_6_ELSTM.3 | CA (Combined Cycle Steam Part) | 1
21 | IID | 16 | Imperial Irrigation District |  | 21656 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 11.6 | -7.5 | 7.5 | 16 | -4.1e-07 | 11.6 |  | GENROU |  | HYGOV4 | ESST4B | Closed | 7 | 1.9974 | HY | 12.5 | PF<-0.85 | NO | 0 | 0.312 | 2.18 | 0.2725 | 0.124 | 0.398 | 3.2097 | 6.9 |  | DROP4_6_UNIT1 | HY (Hydro) | 1
21 | IID | 16 | Imperial Irrigation District |  | 21657 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 11.4 | -7.5 | 7.5 | 16 | 7.4e-07 | 11.4 |  | GENROU |  | HYGOV4 | ESST4B | Closed | 9 | 2.4862 | HY | 12 | PF<-0.85 | NO | 0 | 0.363 | 2.53 | 0.3036 | 0.0757 | 0.2226 | 2.9406 | 6.9 |  | DROP4_6_UNIT1 | HY (Hydro) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21666 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 24.2 | -7.44 | 8 | 16 | 0.48 | 24.68 |  | GENTPJ | PSS2A | GGOV1 |  | Closed | 24.2 | 1.9377 | BT | 25.47 |  | NO | 0 | 0.15 | 4 | 1.0188 | 0.05 | 0.4 | 8 | 13.8 |  | HEBER_6_HEBER1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21666 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 0 | 22.8 | -6.98 | 7.5 | 16 | 0.46 | 23.26 |  | GENTPJ | PSS2A | GGOV1 |  | Closed | 22.8 | 1.9377 | BT | 24 |  | NO | 0 | 0.15 | 4 | 0.96 | 0.05 | 0.4 | 8 | 13.8 |  | HEBER_6_HEBER1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
21 | IID | 211 | IID Independent Power Producer |  | 21706 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 58.32 | -17 | 21.7 | 16 | 2.21e-06 | 58.32 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 46 | 3.1939 | ST | 68.61 |  | NO | 0 | 0.267 | 6.6 | 4.5283 | 0.065 | 0.334 | 5.1385 | 13.8 |  | MIDWAY_6_SALTSEA.U5L | ST (Steam Turbine) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21753 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 52.2 | -25.23 | 25.23 | 16 | -52.2 |  |  | REGC_A |  |  | REEC_A | Closed | 52.2 | 1.2677 | PV | 58 |  | YES | 100000000 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | MIDWAY_6_CEDAR2 | PV (Photovoltaic) | 1
21 | IID | 390 | Pacific Gas and Electric |  | 21754 | 1 | 1 | [16 empty] | Missing PS |  |  | -52.2 | 52.2 | -25.23 | 25.23 | 16 | -52.2 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | ST | 58 |  | NO | 0 | 100000000 | 0 |  |  |  | NAN | 0.385 |  | MIDWAY_6_CEDAR2BS | ST (Steam Turbine) | 1
21 | IID | 211 | IID Independent Power Producer |  | 21962 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -21.1 | 21.1 | -13.36 | 13.36 | 16 | -21.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 26.082 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | NBRAWLEY_6_NBSOLR.BAT.G | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22082 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 25.8 | -4.53 | 0 | 999 | -25.8 |  |  | REGC_A |  |  | REEC_A | Closed | 12.384 | -4.53 | PV | 27.2 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.36 |  | BREGGO_6_SOLAR | PV (Photovoltaic) | 1 |  | PSS Exempt
22 | SANDIEGO | 136 | SDG&E |  | 22088 | 27 | 27 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | BLVRDE_6_BLVBT1_WDAT 127 - BESS | BA (Energy Storage, Battery) | 27
22 | SANDIEGO | 136 | SDG&E |  | 22136 | 28 | 28 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | CLRMNT_6_CLEBT1_WDAT 128 - BESS | BA (Energy Storage, Battery) | 28
22 | SANDIEGO | 136 | SDG&E |  | 22216 | 29 | 29 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ELLIOT_6_ELIBT1_WDAT 129 - BESS | BA (Energy Storage, Battery) | 29
22 | SANDIEGO | 136 | SDG&E |  | 22256 | 10 | 10 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ESCNDO_6_EB1BT1_WDAT 110 - BESS | BA (Energy Storage, Battery) | 10
22 | SANDIEGO | 136 | SDG&E |  | 22256 | 11 | 11 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ESCNDO_6_EB3BT3_WDAT 111 - BESS | BA (Energy Storage, Battery) | 11
22 | SANDIEGO | 136 | SDG&E |  | 22256 | 12 | 12 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | ESCNDO_6_EB2BT2_WDAT 112 - BESS | BA (Energy Storage, Battery) | 12
22 | SANDIEGO | 136 | SDG&E |  | 22372 | 25 | 25 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | KEARNY_6_NESBT1_WDAT 125 - BESS | BA (Energy Storage, Battery) | 25
22 | SANDIEGO | 136 | SDG&E |  | 22372 | 26 | 26 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | KEARNY_6_SESBT2_WDAT 126 - BESS | BA (Energy Storage, Battery) | 26
22 | SANDIEGO | 136 | SDG&E |  | 22440 | 22 | 22 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | MELRSE_6_MELBT1_WDAT 122 - BESS | BA (Energy Storage, Battery) | 22
22 | SANDIEGO | 136 | SDG&E |  | 22440 | 23 | 23 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | MELRSE_6_MELBT2_WDAT 123 - BESS | BA (Energy Storage, Battery) | 23
22 | SANDIEGO | 136 | SDG&E |  | 22486 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 48 | -23 | 72 | 999 | 1 | 49 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 71.72 | PF<0.8 | YES | 0.008 | 0.202 | 1.2 | 0.86064 | 0.158 | 0.89 | 5.6329 | 13.8 |  | MRGT_6_MMAREF | GT (Gas Turbine) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22487 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 48 | -20 | 71 | 999 | 1 | 49 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 71.72 | PF<0.8 | YES | 0.008 | 0.202 | 1.2 | 0.86064 | 0.158 | 0.89 | 5.6329 | 13.8 |  | MRGT_6_MEF2 | GT (Gas Turbine) | 1
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 22607 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 272 | -157.6667 | 183.5556 | 999 | -272 |  |  | GENROU | PSS2A |  | ESST4B | Closed | 200 | 37.3545 | CC | 323 |  | YES | 0.011 | 0.269 | 4.69 | 15.1487 | 0.21 | 1.15 | 5.4762 | 16 |  | OTMESA_2_STG3 | CC (Combined Cycle Generic) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22624 | 88 | 88 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | PALA_6_PGCBT1_WDAT 188 - BESS | BA (Energy Storage, Battery) | 88
22 | SANDIEGO | 136 | SDG&E |  | 22636 | 30 | 30 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 69 |  | PARDSE_6_PESBT1_WDAT 130 - BESS | BA (Energy Storage, Battery) | 30
22 | SANDIEGO | 148 | Customer Owned QF-in SDG&E Area |  | 22700 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 3.27 | -1.08 | 1.08 | 999 | -3.27 | [6 empty] | Open | 0 | 0 | GT | 26 |  | NO | 0.006 | 0.15 | 0 |  |  |  | NAN | 69 |  | SAMPSON_12.5_GT_UNIT_1_KELCO | GT (Gas Turbine) | 1
22 | SANDIEGO | 136 | SDG&E |  | 22734 | 31 | 31 | [12 empty] | Gen on HV | [6 empty] | -10 | 10 | -3.2868 | 3.2868 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 10 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 138 |  | SANTEE_1_SABBT1_WDAT 131 - BESS | BA (Energy Storage, Battery) | 31
22 | SANDIEGO | 207 | Tule Wind |  | 22949 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 131.1 | 0 | 61.78 | 999 | -131.1 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 26.22 | 0 | W3 | 145.667 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.69 |  | TULEWD_1_TULWD1 | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
22 | SANDIEGO | 137 | Sempra US Gas and Power |  | 22981 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 30 | 308 | -124.7363 | 227.2198 | 999 | -308 |  |  | GENROU | PSS2A |  | ESST4B | Closed | 257 | 41.9199 | CC | 365 |  | YES | 0.002 | 0.046 | 3.95 | 14.4175 | 0.037 | 0.103 | 2.7838 | 21 |  | TERMEX_2_STG | CC (Combined Cycle Generic) | 1
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 23162 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 50 | 111.3 | -59.3044 | 105.8261 | 999 | -5.06 | 106.24 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Closed | 93 | 4.138 | CS | 155.07 | PF<0.8 | YES | 0.007 | 0.165 | 1.4 | 2.171 | 0.106 | 0.362 | 3.4151 | 13.8 |  | PIOPIC_2_CTG1 | CS (Combined Cycle Single Shaft) | 1
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 23163 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 50 | 112.7 | -59.3044 | 105.8261 | 999 | -6.46 | 106.24 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Closed | 93 | 4.138 | CS | 155.07 | PF<0.8 | YES | 0.007 | 0.165 | 1.4 | 2.171 | 0.106 | 0.362 | 3.4151 | 13.8 |  | PIOPIC_2_CTG2 | CS (Combined Cycle Single Shaft) | 1
22 | SANDIEGO | 147 | Calpine/Otay Mesa Gen Co. |  | 23164 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 50 | 112 | -58.6087 | 101.6522 | 999 | -5.76 | 106.24 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Closed | 101 | 3.659 | CS | 155.07 | PF<0.8 | YES | 0.007 | 0.165 | 1.4 | 2.171 | 0.106 | 0.362 | 3.4151 | 13.8 |  | PIOPIC_2_CTG3 | CS (Combined Cycle Single Shaft) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23320 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 49 | -13 | 56 | 999 | -9.5e-07 | 49 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 72 | PF<0.8 | YES | 0.006 | 0.16 | 1.174 | 0.84528 | 0.121 | 0.36 | 2.9752 | 13.8 |  | ELCAJN_6_LM6K | GT (Gas Turbine) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23402 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 45 | 0 | 12.4 | 999 | -45 |  |  | REGC_A |  |  | REEC_A | Closed | 21.6 | 0 | PV | 48 |  | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.33 |  | CNTNLA_2_SOLAR2 | PV (Photovoltaic) | 2
22 | SANDIEGO | 195 | CED Westside Canal Battery Stora |  | 23421 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -137 | 137.1 | -110.675 | 110.675 | 999 | -137.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 176.2 | PF<0.8 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.69 |  | WESCAN_2_BDSBT1 | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 195 | CED Westside Canal Battery Stora |  | 23425 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -123 | 123 | -102.3194 | 102.3194 | 999 | -123 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 160.1 | PF<0.8 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.69 |  | WESCN2_2_BDSBT1 | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 209 | AES North America Development |  | 23519 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -27.7 | 31.7 | -21 | 21 | 999 | -31.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 41.16 | PF<-0.85 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.66 |  |  | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 195 | CED Westside Canal Battery Stora |  | 23584 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -103.7 | 103.7 | -70.8888 | 70.8888 | 999 | -103.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 125.8 | PF<-0.85 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.69 |  | WESCN2_2_BDSBT2 | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23604 | 1 | 1 | [16 empty] | Missing PS |  |  | -4.11 | -2.56 | -120 | 225 | 999 | 2.56 |  |  | GENROU |  |  | ESAC7B | Closed | -4.1 | 58.1337 | SC | 225 | PF<0.8 | NO | 0.002 | 0.13 | 2.12 | 4.77 | 0.08 | 0.3333 | 4.1663 | 17.5 |  | Synchron | SC (Synchronous Condenser) | 1
22 | SANDIEGO | 139 | Wellhead Electric Co. |  | 23685 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -50.74 | 50.74 | -40 | 40 | 999 | -50.74 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.2 | PF<0.8 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 74 | Southern California Edison |  | 23701 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | -3 | -3 | -120 | 225 | 999 | 3 |  |  | GENTPJ |  |  |  | Closed | -3 | -120 | SC | 225 | PF<0.8 | NO | 0 | 0.106 | 2.12 | 4.77 | 0.0168 | 0.2463 | 14.6607 | 17.5 |  | Synchronous condenser A | SC (Synchronous Condenser) | 1 |  | PSS Exempt
22 | SANDIEGO | 136 | SDG&E |  | 23871 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -50 | 51.4 | -49.215 | 49.215 | 999 | -51.4 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 71.2 | PF<0.8 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.66 |  |  | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23929 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -100 | 100.95 | -70 | 70 | 999 | -100.95 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 110 | PF<-0.85 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.48 |  | POME_6_POMBT1 | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23933 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -197.95 | 202.0625 | -141.0096 | 141.0096 | 999 | -202.0625 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 246.4 | PF<-0.85 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.48 |  | PERGRN_2_PRSBT1 | BA (Energy Storage, Battery) | 1
22 | SANDIEGO | 136 | SDG&E |  | 23959 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -297.2 | 302.815 | -198.1784 | 198.1784 | 999 | -302.815 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 361.9 | PF<-0.85 | NO | 0.036 | 0.909 | 0 |  |  |  | NAN | 0.48 |  | NITHWK_1_NHSBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24009 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | 0 | 42 | 999 | 54.4 | 94.4 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 94.4 | PF<0.8 | NO | 0 | 0.296 | 6.7638 | 6.385 | 0.149 | 0.61 | 4.094 | 13.8 |  | APPGEN_13.8_GT1 | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24010 | R2 | R2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | 0 | 42 | 999 | 54.4 | 94.4 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 94.4 | PF<0.8 | NO | 0 | 0.296 | 6.7638 | 6.385 | 0.149 | 0.61 | 4.094 | 13.8 |  | APPGEN_13.8_GT2 | OT (Other) | R2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24018 | R1 | R1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 35 | -8 | 17 | 999 | -35 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | OT | 100 |  | NO | 0 | 0.18 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  |  | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24063 | R1 | R1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 50 | 0 | 25 | 999 | 50 | 100 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 100 |  | NO | 0 | 0.14 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | WALNUT_6_HILLGEN | ST (Steam Turbine) | R1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24067 | HP | HP | [16 empty] | Missing PS |  |  | 0 | 107.5 | -22 | 65 | 999 | 107.5 | 215 |  | GENTPJ |  | IEEEG1_GE | EXDC1 | Open | 0 | 0 | XC | 128 |  | NO | 0 | 0.171 | 2.375 | 3.04 | 0.074 | 0.311 | 4.2027 | 13.8 |  | HNTGBH_13.8_GN2 | XC (Cross Compound Steam) | HP
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24067 | LP | LP | [16 empty] | Missing PS |  |  | 0 | 107.5 | -30 | 65 | 999 | -107.5 |  |  | GENTPJ |  |  | EXDC1 | Open | 0 | 0 | XC | 128 |  | NO | 0 | 0.25 | 6.227 | 7.9706 | 0.041 | 0.156 | 3.8049 | 13.8 |  |  | XC (Cross Compound Steam) | LP
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24094 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 21.6 | 0 | 20 | 999 | 24.4 | 46 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | GT | 45 | PF<0.8 | NO | 0.005 | 0.173 | 5 | 2.25 | 0.102 | 0.39 | 3.8235 | 13.8 |  | LAFRES_1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24107 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 750 | -20 | 202 | 999 | 0 | 750 |  | GENROU | PSS2A | GGOV1 | ESST4B | Open | 0 | 0 | ST | 896 |  | NO | 0.001 | 0.18 | 2.82 | 25.2672 | 0.208 | 0.384 | 1.8462 | 26 |  | W_ORMOND_26_GN1 | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24110 | D1 | D1 | [9 empty] | Unreas H | Unreas Sat | [5 empty] | Missing PS |  |  | 29.7 | 48.8 | 0 | 0 | 999 | 1.7 | 50.5 |  | GENTPJ |  | GGOV1 | ESAC2A | Open | 0 | 0 | JE | 57.412 |  | NO | 0.005 | 0.124 | 1.2 | 0.68894 | 0.22 | 0.733 | 3.3318 | 13.8 |  | SNCLRA_6_OXGEN | JE (Jet Engine) | D1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24118 | R1 | R1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 30 | 0 | 15 | 999 | 70 | 100 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | OT | 100 |  | NO | 0 | 0.18 | 3 | 3 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | SAUGUS_13.8_PTCHGN | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24139 | R1 | R1 | [16 empty] | Missing PS |  |  | 0 | 41.2 | -12.7903 | 19.81 | 999 | -41.2 | [6 empty] | Open | 0 | 0 | ST | 43.446 |  | YES | 0 | 0.115 | 0 |  |  |  | NAN | 12.47 |  | HINSON_6_SERRGN | ST (Steam Turbine) | R1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24159 | D1 | D1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 14.15 | -10.6 | 0.3 | 999 | -14.15 |  |  | GENTPJ | PSS2B |  | ESST4B | Open | 0 | 0 | JE | 31.5 | PF<-0.85 | NO | 0.004 | 0.2 | 2.48 | 0.7812 | 0.096 | 0.383 | 3.9896 | 12.47 |  | SNCLRA_2_UNIT1 | JE (Jet Engine) | D1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24170 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 56.3 | -15 | 30 | 999 | 13.7 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | HINSON_6_LBECH1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24170 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 56.5 | -15 | 30 | 999 | 13.5 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | HINSON_6_LBECH2 | GT (Gas Turbine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24171 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 56.5 | -15 | 30 | 999 | 13.5 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | HINSON_6_LBECH3 | GT (Gas Turbine) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24171 | 4 | 4 | [16 empty] | Missing PS |  |  | 0 | 56.5 | -15 | 30 | 999 | 13.5 | 70 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | GT | 70 |  | NO | 0 | 0.21 | 6 | 4.2 | 0.087 | 0.31 | 3.5632 | 13.8 |  | HINSON_6_LBECH4 | GT (Gas Turbine) | 4
24 | SOCALIF | 74 | Southern California Edison |  | 24234 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  |  | Gen at 0.0 | Gen on HV | [6 empty] | 0 | 0 | -100 | 50 | 999 | 0 |  |  | SVCWSC |  |  |  | Closed | 0 | -64.7319 | OT | 100 | PF<0.8 | NO | 0 | 0.2 | 0 |  |  |  | NAN | 230 |  | W_RECTOR_230_SVC | OT (Other) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24239 | C1 | C1 | [16 empty] | Missing PS |  |  | 0 | 44 | -4.5 | 25 | 999 | 6 | 50 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 40 | -3.9867 | CS | 50 |  | NO | 0 | 0.16 | 6.23 | 3.115 | 0.1 | 0.33 | 3.3 | 13.8 |  | VERNON_6_MALBRG | CS (Combined Cycle Single Shaft) | C1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24240 | C2 | C2 | [16 empty] | Missing PS |  |  | 0 | 44 | -4.5 | 25 | 999 | 6 | 50 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 40 | -4.0199 | CS | 50 |  | NO | 0 | 0.16 | 6.23 | 3.115 | 0.1 | 0.33 | 3.3 | 13.8 |  | VERNON_6_MALBRG | CS (Combined Cycle Single Shaft) | C2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24241 | S3 | S3 | [16 empty] | Missing PS |  |  | 0 | 51.6 | -5.3 | 30.6 | 999 | -51.6 |  |  | GENTPJ |  |  | ESAC7B | Closed | 45 | -4.4073 | CA | 58.8 |  | NO | 0 | 0.16 | 3.17 | 1.864 | 0.1 | 0.19 | 1.9 | 13.8 |  | VERNON_6_MALBRG | CA (Combined Cycle Steam Part) | S3
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24242 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 20 | 49.68 | -26 | 50 | 999 | 1.32 | 51 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 45 | -6.6179 | GT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.193 | 0.84913 | 0.15455 | 0.41435 | 2.681 | 13.8 |  | RVSIDE_6_RERCU1 | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24243 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 20 | 49.68 | -26 | 50 | 999 | 1.32 | 51 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 45 | -6.6179 | GT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.193 | 0.84913 | 0.15455 | 0.41435 | 2.681 | 13.8 |  | RVSIDE_6_RERCU2 | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24299 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 20 | 49.68 | -26 | 50 | 999 | -5.4e-07 | 49.68 |  | GENTPJ | PSS2A | GGOV1 | ESAC7B | Closed | 45 | -7.3179 | GT | 71.176 | PF<0.8 | NO | 0 | 0.198 | 1.193 | 0.84913 | 0.167 | 0.2952 | 1.7677 | 13.8 |  | RVSIDE_2_RERCU3 | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24300 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 20 | 49.68 | -26 | 50 | 999 | -5.4e-07 | 49.68 |  | GENTPJ | PSS2A | GGOV1 | ESAC7B | Closed | 45 | -7.3179 | GT | 71.176 | PF<0.8 | NO | 0 | 0.198 | 1.193 | 0.84913 | 0.167 | 0.2952 | 1.7677 | 13.8 |  | RVSIDE_2_RERCU4 | GT (Gas Turbine) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24317 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 93.5 | -3.75 | 25 | 999 | -2.4e-07 | 93.5 |  | GENQEC | PSS2A | HYGOV4 | EXST4B | Closed | 88 | -3.75 | HY | 95 |  | NO | 0.005 | 0.302 | 2.63 | 2.4985 |  |  | NAN | 13.8 |  | BIGCRK_2_EXESWD | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24318 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 93.5 | -8.4 | 10 | 999 | -2.4e-07 | 93.5 |  | GENQEC | PSS2A | HYGOV4 | EXST4B | Closed | 88 | -8.4 | HY | 95 |  | NO | 0.005 | 0.339 | 2.63 | 2.4985 |  |  | NAN | 13.8 |  | BIGCRK_2_EXESWD | HY (Hydro) | 2
24 | SOCALIF | 74 | Southern California Edison |  | 24323 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.5 | -0.9 | 4.3 | 999 | 3.3e-07 | 10.5 |  | GENTPJ |  | HYGOV4 | EXST1_GE | Open | 0 | 0 | HY | 12 |  | NO | 0 | 0.302 | 1.92 | 0.2304 | 0.247 | 0.549 | 2.2227 | 4.8 |  | BIGCRK_2_EXESWD | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24324 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 8 | 0 | 13 | 999 | 92 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | SANITR_6_UNITS | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24325 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 12 | 0 | 17 | 999 | 88 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Closed | 10 | 0 | IC | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | ELLIS_2_QF | IC (Internal Combustion) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24326 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20 | -14 | 28 | 999 | 80 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  |  | OT (Other) | S1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24329 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 21.6 | 0 | 20 | 999 | 78.4 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | ST | 100 | PF<0.8 | NO | 0.005 | 0.173 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_1 | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24330 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 17 | 0 | 20 | 999 | 83 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Closed | 15 | 1.1739 | CC | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_13.8_OUTFALL1 | CC (Combined Cycle Generic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24331 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 17 | 0 | 20 | 999 | 83 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Closed | 15 | 1.1739 | CC | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_13.8_OUTFALL2 | CC (Combined Cycle Generic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24332 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 13 | 0 | 20 | 999 | 87 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LAFRES_13.8_PALOGEN | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24337 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.1 | 0 | 20 | 999 | 89.9 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | HY | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | LACIEN_2_VENICE | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24341 | R1 | R1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20 | 0 | 17 | 999 | 80 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 13.8 |  | SANTGO_2_LNDFL1 | OT (Other) | R1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24361 | R3 | R3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | 0 | 42 | 999 | 54.4 | 94.4 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | OT | 94.4 | PF<0.8 | NO | 0 | 0.18 | 2.4 | 2.2656 | 0.05 | 0.3 | 6 | 13.8 |  | APPGEN_13.8_ST_3 | OT (Other) | R3 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24362 | G1 | G1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 29 | -14 | 28 | 999 | -29 | [6 empty] | Open | 0 | 0 | OT | 100 | PF<0.8 | NO | 0 | 0.28 | 0 |  |  |  | NAN | 13.8 |  | GOLETA_6_EXGEN | OT (Other) | G1
24 | SOCALIF | 74 | Southern California Edison |  | 24373 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 19.8 | -3.7 | 6.35 | 999 | 1.7 | 21.5 |  | GENTPJ |  | HYGOV4 | REXS | Closed | 18 | 5.0784 | HY | 21.5 |  | NO | 0 | 0.25 | 2.108 | 0.45322 | 0.048 | 0.1818 | 3.7875 | 11 |  | VESTAL_2_KERN | HY (Hydro) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24456 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 10 | -2.5 | 5 | 999 | 90 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | HY | 100 |  | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 66 |  | MONLTH_6_BOREL | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24460 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 14 | -2.8 | -2.8 | 999 | -6e-08 | 14 |  | WT1G |  | WT1T |  | Closed | 12 | -2.8 | W1 | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 66 |  | DTCHWD_2_BT3WND | W1 (Wind Turbine, Type 1) | 1
18 | NEVADA | 18 | N3 Nevada |  | 18875 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 3 | 28 | -9.9 | 9.9 | 24 | -28 |  |  | WT4G |  |  | WT4E | Closed | 6.0444 | -3.4099 | PV | 32 |  | NO | 1 | 10 | 0 |  |  |  | NAN | 0.4 |  | SILVST_34.5_PV2 | PV (Photovoltaic) | 2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24481 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10.5 | -4.5 | -4.5 | 999 | -10.5 |  |  | WT3G |  | WT3T | WT3E | Closed | 10 | -4.5 | W3 | 10.8 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12.47 |  | MIDWD_7_CORAMB,MIDWD_2_WIND2 | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24483 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 19.16 | -5 | -5 | 999 | -19.16 |  |  | WT3G |  | WT3T | WT3E | Closed | 10 | -5 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  | NZWIND_6_CALWND,NZWIND_2_WDSTR5 | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24484 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 13.2 | -3.7 | -3.7 | 999 | -13.2 |  |  | WT3G |  | WT3T | WT3E | Closed | 12 | -3.7 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  | NZWIND_6_WDSTR2 | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24695 | EQ | EQ | [17 empty] | Missing Sub R/X |  | 0 | 78 | -25.6461 | 25.6461 | 999 | -78 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 77 | 0 | W3 | 82.108 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 1 |  | BRODIE_2_WIND | W3 (Wind Turbine, Type 3) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24699 | EQ | EQ | [17 empty] | Missing Sub R/X |  | 0 | 24 | -7.891 | 7.891 | 999 | -24 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 13.1 | 0 | W3 | 25.264 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 1 |  | BRODIE_2_WIND | W3 (Wind Turbine, Type 3) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24485 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 12.8 | -3.7 | -3.7 | 999 | -12.8 |  |  | WT3G |  | WT3T | WT3E | Closed | 12 | -3.7 | W3 | 100 |  | NO | 0.007 | 0.123 | 0 |  |  |  | NAN | 12 |  | NZWIND_6_WDSTR4 | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24726 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 7.5 | -7.5 | 7.5 | 999 | 5 | 12.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 12.5 | PF<0.8 | NO | 0 | 0.18 | 4.733 | 0.59162 | 0.194 | 0.0928 | 0.47835 | 4.16 |  | CONTRL_1_QF | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24733 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 55 | -3 | 7 | 999 | 45 | 100 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 18 | -2.0045 | ST | 100 |  | NO | 0 | 0.195 | 1.92 | 1.92 | 0.194 | 0.194 | 1 | 13.8 |  | SEARLS_7_ARGUS | ST (Steam Turbine) | 1
24 | SOCALIF | 980 | Terra-Gen Dixie Valley LLC |  | 24747 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 59 | -24 | 30 | 999 | 2.62e-06 | 59 |  | GENROU | IEEEST | GGOV1 | EXST1_GE | Closed | 50 | 6.9002 | ST | 67.23 |  | NO | 0.003 | 0.23 | 7.6 | 5.1095 | 0.32 | 0.68 | 2.125 | 13.8 |  | CONTRL_1_OXBOW | ST (Steam Turbine) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24783 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.5 | -1.1 | 0.7 | 999 | 2.4e-07 | 6.5 |  | GENTPJ |  | HYGOV4 | EXST4B | Open | 0 | 0 | HY | 7.957 |  | NO | 0.003 | 0.256 | 1.885 | 0.14999 | 0.192 | 0.469 | 2.4427 | 2.4 |  | CONTRL_1_RUSHCK | HY (Hydro) | 2
24 | SOCALIF | 74 | Southern California Edison |  | 24784 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.5 | -0.5 | 1.125 | 999 | 0.1 | 1.6 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 1 | 0.70991 | HY | 1.875 | PF<0.8 | NO | 0 | 0.277 | 2.15 | 0.040313 | 0.0083 | 0.28 | 33.7349 | 2.4 |  | CONTRL_1_LUNDY | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 24784 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.5 | -0.5 | 1.125 | 999 | 0.1 | 1.6 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 1 | 0.70991 | HY | 1.875 | PF<0.8 | NO | 0 | 0.277 | 2.15 | 0.040313 | 0.0083 | 0.28 | 33.7349 | 2.4 |  | CONTRL_1_LUNDY | HY (Hydro) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24785 | PV | PV | [5 empty] | At Mvar Limit | [13 empty] | 0 | 2 | 2 | 7 | 999 | -2 |  |  | DER_A |  |  |  | Closed | 2 | 2 | PV | 2 | PF<0.8 | NO | 0 | 0.195 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | PV
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | G1 | G1 | [12 empty] | Gen on HV | [6 empty] | 0 | 8.7 | -2.9 | -2.9 | 999 | 2.5e-07 | 8.7 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  | GARNETCM_34.5_PWEST | WT (Wind Turbine) | G1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | G2 | G2 | [12 empty] | Gen on HV | [6 empty] | 0 | 3 | -1 | -1 | 999 | 7e-08 | 3 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  | GARNETCM_34.5_GN_WIND | WT (Wind Turbine) | G2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | PC | PC | [12 empty] | Gen on HV | [6 empty] | 0 | 2.1 | -0.7 | -0.7 | 999 | 3e-08 | 2.1 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  | PWEST_1_UNIT | WT (Wind Turbine) | PC
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | QF | QF | [6 empty] | Limit Power Fact | [5 empty] | Gen on HV | [6 empty] | 0 | 101.4 | -72.4 | -72.4 | 999 | -5.82e-06 | 101.4 |  | WT1G |  | WT1T |  | Closed | 90 | -72.4 | WT | 162 | PF<-0.85 | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  | GARNET_2_WIND4 | WT (Wind Turbine) | QF
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24815 | W2 | W2 | [6 empty] | Limit Power Fact | [5 empty] | Gen on HV | [6 empty] | 0 | 6.5 | -5.5 | -5.5 | 999 | 2.4e-07 | 6.5 |  | WT1G |  | WT1T |  | Open | 0 | 0 | WT | 100 | PF<0.8 | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  |  | WT (Wind Turbine) | W2
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24840 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | SPRGVL_2_EXETPV | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24840 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | SPRGVL_2_EXETPV | GT (Gas Turbine) | 2
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24841 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | RVSIDE_6_SPRING | GT (Gas Turbine) | 1
24 | SOCALIF | 2403 | City of Riverside Public Util |  | 24841 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 9.17 | -10.6875 | 9.975 | 999 | 1.83 | 11 |  | GENTPJ |  | GGOV1 | ESAC1A | Open | 0 | 0 | GT | 14.25 | PF<0.8 | NO | 0 | 0.16 | 5.37 | 0.76522 | 0.1583 | 0.3588 | 2.2666 | 13.8 |  | RVSIDE_6_SPRING | GT (Gas Turbine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24719 | R3 | R3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 108 | -41 | 58 | 999 | -108 |  |  | GENROU | PSS2A |  | TEXS | Open | 0 | 0 | CA | 133.333 |  | NO | 0 | 0.237 | 3 | 4 | 0.1442 | 0.613 | 4.251 | 13.8 |  |  | CA (Combined Cycle Steam Part) | R3 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24861 | 3 | 3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 105.7145 | -52.3068 | 52.3068 | 999 | -105.7145 |  |  | REGC_A |  |  | REEC_B | Closed | 90 | 18.0985 | PV | 120 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.55 |  | PRIMM_2_SOLAR1 | PV (Photovoltaic) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24862 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 24.275 | -8.7672 | 8.7672 | 999 | -24.275 |  |  | REGC_A |  |  | REEC_B | Closed | 14.6 | 7.4023 | PV | 26.3 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.36 |  | PRIMM_2_SOLAR1 | PV (Photovoltaic) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24878 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 40.7 | -15.7 | 28.7 | 999 | 0.5 | 41.2 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 40 | -2.408 | BT | 52.235 |  | NO | 0 | 0.154 | 1.596 | 0.83367 | 0.029 | 0.123 | 4.2414 | 12.47 |  | CONTRL_1_CASAD3 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24888 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.24 | -13.2 | 13.2 | 999 | -20.24 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 22 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24968 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 18 | -11.3 | 11.3 | 999 | -18 |  |  | REGC_A |  |  | REEC_A | Closed | 15.5 | -3.5667 | PV | 25.9 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.315 |  | DSRTSN_2_SOLAR2 | PV (Photovoltaic) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24974 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 41 | -44 | 44 | 999 | -41 |  |  | REGC_A |  |  | REEC_A | Closed | 30 | -2.6469 | PV | 44 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.55 |  | BLKCRK_2_GMCBT1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25038 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 50 | -56 | 56 | 999 | -50 |  |  | REGC_A |  |  | REEC_A | Closed | 45 | -3.3859 | PV | 56 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.55 |  | BLKCRK_2_SOLAR1 | PV (Photovoltaic) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25041 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 85 | -56.2 | 56.2 | 999 | -85 |  |  | REGC_A |  |  | REEC_A | Closed | 75 | -5.6546 | PV | 93.6 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.34 |  | BLKCRK_2_SOLAR1 | PV (Photovoltaic) | 4 |  | PSS Exempt
24 | SOCALIF | 2402 | City of Pasadena Water and Power |  | 25042 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 44.83 | -6.3 | 12.5 | 999 | 15.67 | 60.5 |  | GENROU |  | GGOV1 | EXAC8B | Open | 0 | 0 | GT | 71.176 |  | NO | 0.001 | 0.181 | 1.193 | 0.84913 | 0.12 | 0.37 | 3.0833 | 13.8 |  | GLNARM_7_UNIT 3 | GT (Gas Turbine) | 1
24 | SOCALIF | 2402 | City of Pasadena Water and Power |  | 25043 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 42.42 | -6.3 | 12.5 | 999 | 18.08 | 60.5 |  | GENROU |  | GGOV1 | EXAC8B | Open | 0 | 0 | GT | 71.176 |  | NO | 0.001 | 0.181 | 1.193 | 0.84913 | 0.12 | 0.37 | 3.0833 | 13.8 |  | GLNARM_7_UNIT 4 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25044 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 82 | -54.8 | 54.8 | 999 | -82 |  |  | REGC_A |  |  | REEC_A | Closed | 75 | -5.4999 | PV | 91.26 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.34 |  | BLKCRK_2_SOLAR1 | PV (Photovoltaic) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 24863 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 124.41 | -44.9319 | 44.9319 | 999 | -124.41 |  |  | REGC_A |  |  | REEC_B | Closed | 90 | 39.8431 | PV | 134.81 |  | NO | 10000000 | 10000000 | 0 |  |  |  | NAN | 0.36 |  | PRIMM_2_SOLAR1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25064 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20.9 | -2.05 | 2.05 | 999 | -20.9 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 100000 | 100000 | 0 |  |  |  | NAN | 0.385 |  | VESTAL_2_SOLAR1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25065 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 14.6 | -1.43 | 1.43 | 999 | -14.6 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 15.4 |  | NO | 100000 | 100000 | 0 |  |  |  | NAN | 0.385 |  | VESTAL_2_SOLAR2 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25079 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21.72 | -8.27 | 8.27 | 999 | -21.72 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 21.72 |  | NO | 0 | 0.61 | 0 |  |  |  | NAN | 0.645 |  | GLDFGR_6_SOLAR1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25086 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.7 | 9.7 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.8 |  | PLAINV_6_BSOLAR | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25089 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 22.39 | -9.76 | 9.76 | 999 | -22.39 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22.39 |  | NO | 0 | 0.982 | 0 |  |  |  | NAN | 0.42 |  | PLAINV_6_SOLARC | PV (Photovoltaic) | 1
24 | SOCALIF | 137 | Sempra US Gas and Power |  | 25119 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 93.1 | -44.56 | 33.56 | 999 | -93.1 |  |  | REGC_A |  |  | REEC_A | Closed | 56.2 | 33.56 | PV | 103.4 |  | NO | 0 | 99999 | 0 |  |  |  | NAN | 0.385 |  | COPMT4_2_SOLAR4 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25092 | EQ | EQ |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.215 | 9.215 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 20 |  | NO | 100000000 | 100000000 | 0 |  |  |  | NAN | 0.8 |  | MOJAVW_2_SOLAR | PV (Photovoltaic) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25196 | EQ | EQ | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.7 | -13.6 | 13.6 | 999 | -20.7 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 24.864 | PF<-0.85 | NO | 100000000 | 100000000 | 0 |  |  |  | NAN | 0.6 |  | SUNSPT_2_WNASR1 | PV (Photovoltaic) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25211 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.6835 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_2_CANYN1 | JE (Jet Engine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25212 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.7461 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_2_CANYN2 | JE (Jet Engine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25213 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.7461 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_2_CANYN3 | JE (Jet Engine) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25214 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 51.2 | -25.9 | 49 | 999 | 19.976 | 71.176 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 45 | -7.6835 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.17 | 1.193 | 0.84913 | 0.095 | 0.317 | 3.3368 | 13.8 |  | ANAHM_2_CANYN4 | JE (Jet Engine) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25215 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -125 | 130.35 | -80.9684 | 80.9684 | 999 | -130.35 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 153.45 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25216 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -125 | 130.35 | -80.9684 | 80.9684 | 999 | -130.35 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 153.45 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25217 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -100 | 103.687 | -64.4066 | 64.4066 | 999 | -103.687 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 122.063 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25218 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -100 | 103.687 | -64.4066 | 64.4066 | 999 | -103.687 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 122.063 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 4
24 | SOCALIF | 74 | Southern California Edison |  | 25219 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  | KERRGN_1_UNIT 1 | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 25220 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  | KERRGN_1_UNIT 1 | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 25221 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  | KERRGN_1_UNIT 1 | HY (Hydro) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 25222 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.2 | -0.75 | 1.24 | 999 | -6.2 |  |  | GENTPJ |  |  | EXST4B | Open | 0 | 0 | HY | 7.3 |  | NO | 0 | 0.338 | 1.645 | 0.12008 | 0.2 | 0.377 | 1.885 | 2.4 |  | KERRGN_1_UNIT 1 | HY (Hydro) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25257 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -50 | 50.571 | -39.81 | 39.81 | 999 | -50.571 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 53.01 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | ALMASL_2_AL6BT6 | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.276 | 0.823 | 2.9819 | 6.9 |  | EAGLMT_6.9_GN1 | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.302 | 0.886 | 2.9338 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.288 | 0.901 | 3.1285 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25411 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.272 | 0.853 | 3.136 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.284 | 0.868 | 3.0563 | 6.9 |  | EAGLMT_6.9_GN2 | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.41 | 1.13 | 2.7561 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.374 | 1.159 | 3.0989 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.359 | 1.157 | 3.2228 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25412 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.343 | 1.054 | 3.0729 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.32 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.17568 | 0.252 | 0.683 | 2.7103 | 6.9 |  |  | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.231 | 0.629 | 2.7229 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.228 | 0.65 | 2.8509 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25413 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.254 | 0.737 | 2.9016 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.257 | 0.655 | 2.5486 | 6.9 |  |  | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.54 | 0.18542 | 0.487 | 1.723 | 3.538 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.495 | 1.669 | 3.3717 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.495 | 1.669 | 3.3717 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25414 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.433 | 1.549 | 3.5774 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.32 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.17568 | 0.231 | 0.669 | 2.8961 | 6.9 |  |  | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.212 | 0.629 | 2.967 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.21 | 0.68 | 3.2381 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25415 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.212 | 2.4 | 0.1752 | 0.223 | 0.596 | 2.6726 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.004 | 0.16 | 2.4 | 0.1752 | 0.231 | 0.647 | 2.8009 | 6.9 |  |  | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.54 | 0.18542 | 0.482 | 2.393 | 4.9647 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.5 | 2.423 | 4.846 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -6.7 | 0.1 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.446 | 1.584 | 3.5516 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25416 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -6.7 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 7.3 | PF<0.8 | NO | 0.003 | 0.168 | 2.4 | 0.1752 | 0.5 | 1.783 | 3.566 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25417 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.007 | 0.15 | 2.01 | 0.07035 | 0.244 | 0.713 | 2.9221 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25417 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.007 | 0.15 | 2.01 | 0.07035 | 0.25 | 0.786 | 3.144 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25417 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.169 | 2.01 | 0.07035 | 0.262 | 0.806 | 3.0763 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.169 | 2.01 | 0.07035 | 0.247 | 0.844 | 3.417 | 6.9 |  | IRONMT_6.9_PUMP2 | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.161 | 2.01 | 0.07035 | 0.256 | 0.825 | 3.2227 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -3.2 | 0.1 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.153 | 1.9 | 0.0665 | 0.238 | 0.761 | 3.1975 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25418 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -3.2 | 0 | 0 | 0.2 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 3.5 | PF<0.8 | NO | 0.008 | 0.153 | 1.9 | 0.0665 | 0.196 | 0.711 | 3.6276 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.284 | 0.918 | 3.2324 | 6.9 |  | HINDS_6.9_PUMPS1 | MP (Motor/Pump) | 1
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.274 | 0.91 | 3.3212 | 6.9 |  |  | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.208 | 2.32 | 0.23548 | 0.279 | 0.786 | 2.8172 | 6.9 |  |  | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25419 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.28 | 0.844 | 3.0143 | 6.9 |  |  | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.003 | 0.194 | 2.16 | 0.21924 | 0.316 | 0.856 | 2.7089 | 6.9 |  | HINDS_6.9_PUMPS2 | MP (Motor/Pump) | 5
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.41 | 1.129 | 2.7537 | 6.9 |  |  | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.301 | 1.106 | 3.6744 | 6.9 |  |  | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Closed | -9.3 | 0.25 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.354 | 1.156 | 3.2655 | 6.9 |  |  | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25420 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | -9.3 | 0 | 0 | 0.5 | 999 | 0 |  |  | GENTPF |  |  |  | Open | 0 | 0 | MP | 10.15 | PF<0.8 | NO | 0.004 | 0.193 | 2.39 | 0.24258 | 0.41 | 1.183 | 2.8854 | 6.9 |  |  | MP (Motor/Pump) | 9
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25424 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 2
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25424 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 3
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25424 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 4
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25425 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 6
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25425 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 7
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25425 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 8
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25426 | 10 | 10 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 10
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25426 | 11 | 11 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.1 | 0.1 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 11
24 | SOCALIF | 135 | Metro. Water District S.Cal |  | 25426 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | -4.5 | 3.3 | 0 | 0.2 | 999 | -3.3 |  |  | GENTPJ |  |  | EXST1_GE | Open | 0 | 0 | MP | 10.15 |  | NO | 0.005 | 0.161 | 1.86 | 0.18879 | 0.41 | 1.183 | 2.8854 | 6.9 |  | DMDVLY_1_UNITS | MP (Motor/Pump) | 12
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25596 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -50 | 50 | -34.59 | 34.59 | 999 | -50 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 60.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | HIGHDS_2_H5SBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25633 | QF | QF | [12 empty] | Gen on HV | [6 empty] | 0 | 20 | -10 | -10 | 999 | 80 | 100 |  | GENROU | PSS2A | GGOV1 | REXS | Open | 0 | 0 | W4 | 100 |  | NO | 0 | 0.18 | 2.4 | 2.4 | 0.05 | 0.3 | 6 | 115 |  | CAPWD_1_QF | W4 (Wind Turbine, Type 4) | QF
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25169 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 12.63 | -5.488 | 5.488 | 999 | -12.63 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 13.032 |  | NO | 0 | 0.61 | 0 |  |  |  | NAN | 0.645 |  | GLDFGR_6_SOLAR2 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25634 | QF | QF |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 17.1 | -8.6 | -8.6 | 999 | -17.1 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | BUCKWD_1_QF | W3 (Wind Turbine, Type 3) | QF |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25636 | Q1 | Q1 | [12 empty] | Gen on HV | [6 empty] | 0 | 6.3 | -3.2 | -3.2 | 999 | -6.3 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Open | 0 | 0 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | RENWD_1_QF | W3 (Wind Turbine, Type 3) | Q1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25636 | Q2 | Q2 | [12 empty] | Gen on HV | [6 empty] | 0 | 6.6 | -3.3 | -3.3 | 999 | -6.6 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Open | 0 | 0 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | RENWD_1_QF | W3 (Wind Turbine, Type 3) | Q2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25634 | W5 | W5 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 3.7 | -1.2 | -1.2 | 999 | -3.7 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 4 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | BUCKWD_7_WINTCV | W3 (Wind Turbine, Type 3) | W5 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25640 | QF | QF | [12 empty] | Gen on HV | [6 empty] | 0 | 30 | -15 | -15 | 999 | 70 | 100 |  | WT1G |  | WT1T |  | Closed | 30 | -15 | W1 | 100 |  | NO | 0 | 0.177 | 0 |  |  |  | NAN | 115 |  | PANERO_2_MWPWD1 | W1 (Wind Turbine, Type 1) | QF
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25639 | QF | QF |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 27 | -13.5 | -13.5 | 999 | -27 |  |  | WT3G |  | WT3T | WT3E | Closed | 25 | -13.5 | W3 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | SEAWND_2_AMWWD1 | W3 (Wind Turbine, Type 3) | QF |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25645 | EU | EU |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 16.9 | -5.6 | -5.6 | 999 | -16.9 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 20 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | VENWD_1_WIND3 | W3 (Wind Turbine, Type 3) | EU |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25645 | Q1 | Q1 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 25.5 | -12.8 | -12.8 | 999 | -25.5 |  |  | WT3G |  | WT3T | WT3E | Closed | 25.5 | -12.8 | W3 | 35 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | VENWD_1_WIND3 | W3 (Wind Turbine, Type 3) | Q1 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25726 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -10 | 10.1 | -7 | 7 | 999 | -10.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 12.41 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.505 |  | GOLETA_2_VALBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25729 | EQ | EQ | [12 empty] | Gen on HV | [6 empty] | -35 | 35 | -11.5 | 11.5 | 999 | -35 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 50 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 66 |  | JOHANN_2_JOSBT1 | BA (Energy Storage, Battery) | EQ
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25767 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -64.72 | 64.72 | -51.162 | 51.162 | 999 | -64.72 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 82.5 | PF<0.8 | NO | 0 | 9999 | 0 |  |  |  | NAN | 34.5 |  | SISPRG_2_DS3BT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25769 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -63.156 | 63.156 | -46.41 | 46.41 | 999 | -63.156 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 78.375 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 34.5 |  | SISPRG_2_DS3BT2 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25771 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -13.156 | 13.156 | -9.958 | 9.958 | 999 | -13.156 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 16.5 | PF<0.8 | NO | 0 | 9999 | 0 |  |  |  | NAN | 34.5 |  | SISPRG_2_DS3BT3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25773 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -15.785 | 15.785 | -13.2749 | 13.2749 | 999 | -15.785 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 20.625 | PF<0.8 | NO | 0 | 9999 | 0 |  |  |  | NAN | 34.5 |  | SISPRG_2_DS3BT4 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25838 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 0.6 | 0 | 0 | 999 | -0.6 | [6 empty] | Closed | 0.6 | 0 | PV | 0.6 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 16 |  |  | PV (Photovoltaic) | PV
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25961 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -78.7 | 78.7 | -58.3 | 58.3 | 999 | -78.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 97.956 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25967 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -163.2 | 163.2 | -121 | 121 | 999 | -163.2 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 203.168 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
26 | LADWP | 81 | City of Los Angeles |  | 26027 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 50 | 230 | -50 | 122 | 81 | -230 |  |  | GENTPJ | PSS2B |  | ESDC4B | Open | 0 | 0 | CA | 270 |  | NO | 0.002 | 0.2 | 3.84 | 10.368 | 0.066 | 0.178 | 2.697 | 18 |  | VLY_18_GN6 | CA (Combined Cycle Steam Part) | 2
26 | LADWP | 122 | LA Contracts |  | 26028 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 0 | -189 | 375 | 81 | 0 |  |  | GENQEC |  |  | ST6C | Closed | 0 | -76.6873 | SC | 375 | PF<0.8 | NO | 0.007 | 0.15 | 1.92 | 7.2 |  |  | NAN | 19.5 |  |  | SC (Synchronous Condenser) | 1
26 | LADWP | 123 | Intermountain Power Agency |  | 26029 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 0 | -189 | 375 | 81 | 0 |  |  | GENQEC |  |  | ST6C | Open | 0 | 0 | SC | 375 | PF<0.8 | NO | 0.007 | 0.15 | 1.92 | 7.2 |  |  | NAN | 19.5 |  |  | SC (Synchronous Condenser) | 2
26 | LADWP | 123 | Intermountain Power Agency |  | 26030 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 0 | -189 | 375 | 81 | 0 |  |  | GENQEC |  |  | ST6C | Closed | 0 | -76.6873 | SC | 375 | PF<0.8 | NO | 0.007 | 0.15 | 1.92 | 7.2 |  |  | NAN | 19.5 |  |  | SC (Synchronous Condenser) | 3
26 | LADWP | 81 | City of Los Angeles |  | 26032 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 37.5 | -1 | 2 | 81 | 0 | 37.5 |  | GENTPJ | PSS2B | HYGOV4 | ESDC4B | Closed | 34.5 | 2 | HY | 37.5 |  | NO | 0.002 | 0.182 | 3.81 | 1.4287 | 0.158 | 0.512 | 3.2405 | 11.5 |  | TOLUCA_18_MAG_CT | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 81 | City of Los Angeles |  | 26033 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 37.5 | -1 | 2 | 81 | 0 | 37.5 |  | GENTPJ | PSS2B | HYGOV4 | ESDC4B | Closed | 34.5 | 2 | HY | 37.5 |  | NO | 0.002 | 0.182 | 3.81 | 1.4287 | 0.158 | 0.512 | 3.2405 | 11.5 |  | TOLUCA_18_MAG_ST | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 81 | City of Los Angeles |  | 26034 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 37.5 | -1 | 2 | 81 | 0 | 37.5 |  | GENTPJ | PSS2B | HYGOV4 | ESDC4B | Closed | 34.5 | 2 | HY | 37.5 |  | NO | 0.002 | 0.182 | 3.81 | 1.4287 | 0.158 | 0.512 | 3.2405 | 11.5 |  | NOT IN WSM | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 123 | Intermountain Power Agency |  | 26039 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 350 | 454 | -225 | 386 | 81 | 537 | 991 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST4B | Closed | 454 | 64.6792 | ST | 991 | PF<0.8 | NO | 0.003 | 0.27 | 2.89 | 28.6399 | 0.224 | 0.478 | 2.1339 | 26 |  | VLY_18_GN7 | ST (Steam Turbine) | 1
26 | LADWP | 123 | Intermountain Power Agency |  | 26040 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 350 | 454 | -225 | 386 | 81 | 537 | 991 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST4B | Closed | 454 | 64.551 | ST | 991 | PF<0.8 | NO | 0.003 | 0.27 | 2.875 | 28.4913 | 0.224 | 0.478 | 2.1339 | 26 |  | VLY_18_GN8 | ST (Steam Turbine) | 2
26 | LADWP | 81 | City of Los Angeles |  | 26166 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 47 | 0 | 0 | 81 | -47 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | HY | 53 |  | NO | 0.004 | 0.15 | 3.5 | 1.855 | 0.2534 | 0.703 | 2.7743 | 7.5 |  | PPLNT1_7.5_GN3 | HY (Hydro) | 1 |  | PSS Exempt
26 | LADWP | 81 | City of Los Angeles |  | 26290 | 14 | 14 | [16 empty] | Missing PS |  |  | -2 | 102 | -20 | 92 | 81 | -102 |  |  | GENQEC |  |  | ESAC7B | Closed | -2 | 33.7567 | JE | 127.282 | PF<0.8 | NO | 0.002 | 0.125 | 2.73 | 3.4748 |  |  | NAN | 13.8 |  | HARBOR_13.8_GN14 | JE (Jet Engine) | 14
26 | LADWP | 122 | LA Contracts |  | 26868 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 16.8 | 0 | 0 | 81 | -16.8 |  |  | REGC_A |  |  | REEC_A | Closed | 15 | 0 | PV | 16 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 1
26 | LADWP | 122 | LA Contracts |  | 26870 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 21 | 0 | 0 | 81 | -21 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | 0 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 2
26 | LADWP | 122 | LA Contracts |  | 26872 | 3 | 3 | [17 empty] | Missing Sub R/X |  | 0 | 28 | 0 | 0 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 28 | 0 | PV | 30.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | FTPECK_13.8_G01 | PV (Photovoltaic) | 3
26 | LADWP | 122 | LA Contracts |  | 26874 | 4 | 4 | [17 empty] | Missing Sub R/X |  | 0 | 28 | 0 | 0 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 23 | 0 | PV | 30.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | FTPECK_13.8_G02 | PV (Photovoltaic) | 4
26 | LADWP | 122 | LA Contracts |  | 26876 | 5 | 5 | [17 empty] | Missing Sub R/X |  | 0 | 21 | 0 | 0 | 81 | -21 |  |  | REGC_A |  |  | REEC_A | Closed | 19 | 0 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | FTPECK_13.8_G03 | PV (Photovoltaic) | 5
26 | LADWP | 122 | LA Contracts |  | 26878 | 6 | 6 | [17 empty] | Missing Sub R/X |  | 0 | 26.25 | 0 | 0 | 81 | -26.25 |  |  | REGC_A |  |  | REEC_A | Closed | 24 | 0 | PV | 25 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | TIBER_12.5_G1 | PV (Photovoltaic) | 6
26 | LADWP | 122 | LA Contracts |  | 26880 | 7 | 7 | [17 empty] | Missing Sub R/X |  | 0 | 28 | 0 | 0 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 23 | 0 | PV | 30.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | SANTAN_1 | PV (Photovoltaic) | 7
26 | LADWP | 122 | LA Contracts |  | 26882 | 8 | 8 | [17 empty] | Missing Sub R/X |  | 0 | 28 | 0 | 0 | 81 | -28 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | 0 | PV | 30.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | 8
26 | LADWP | 122 | LA Contracts |  | 26884 | A | A | [17 empty] | Missing Sub R/X |  | 0 | 24 | 0 | 0 | 81 | -24 |  |  | REGC_A |  |  | REEC_A | Closed | 16 | 0 | PV | 26.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | A
26 | LADWP | 122 | LA Contracts |  | 26886 | B | B | [17 empty] | Missing Sub R/X |  | 0 | 26 | 0 | 0 | 81 | -26 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | 0 | PV | 28.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  |  | PV (Photovoltaic) | B
26 | LADWP | 122 | LA Contracts |  | 26901 | B | B | [11 empty] | Gen at 0.0 | [5 empty] | Missing Sub R/X |  | -20 | 20 | -15 | 15 | 81 | -20 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 14.5 | PV | 25 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.57 |  |  | PV (Photovoltaic) | B
26 | LADWP | 122 | LA Contracts |  | 26980 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -92.4 | 81.472 | -92.4 | 92.4 | 81 | -81.472 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 17.3785 | BA | 92.4 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1 |  | PSS Exempt
26 | LADWP | 122 | LA Contracts |  | 26998 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -95.7 | 84.3813 | -95.7 | 95.7 | 81 | -84.3813 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 17.656 | BA | 95.7 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1 |  | PSS Exempt
26 | LADWP | 122 | LA Contracts |  | 27025 | 1 | 1 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.25 | 0 | 0 | 81 | -1.25 | [6 empty] | Closed | 1.25 | 0 | PV | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.39 |  |  | PV (Photovoltaic) | 1
26 | LADWP | 122 | LA Contracts |  | 27026 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.25 | 0 | 0 | 81 | -1.25 | [6 empty] | Closed | 1.25 | 0 | PV | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.39 |  |  | PV (Photovoltaic) | 2
26 | LADWP | 122 | LA Contracts |  | 27027 | 1 | 1 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.25 | 0 | 0 | 81 | -1.25 | [6 empty] | Closed | 1.25 | 0 | PV | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.39 |  |  | PV (Photovoltaic) | 1
26 | LADWP | 122 | LA Contracts |  | 27028 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.25 | 0 | 0 | 81 | -1.25 | [6 empty] | Closed | 1.25 | 0 | PV | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.39 |  |  | PV (Photovoltaic) | 2
26 | LADWP | 122 | LA Contracts |  | 27191 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -95.7 | 84.381 | -95.7 | 95.7 | 81 | -84.381 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 17.3784 | BA | 95.7 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1
26 | LADWP | 122 | LA Contracts |  | 27198 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | -92.4 | 81.4716 | -92.4 | 92.4 | 81 | -81.4716 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 17.6368 | BA | 92.4 | PF<0.8 | YES | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Storage | BA (Energy Storage, Battery) | 1
26 | LADWP | 121 | BURBANK |  | 27253 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 48 | -10 | 40 | 81 | -4 | 44 |  | GENROU | PSS2A | GGOV1 | ESST6B | Open | 0 | 0 | ST | 62.5 | PF<0.8 | NO | 0.002 | 0.24 | 3.68 | 2.3 | 0.1562 | 0.4882 | 3.1255 | 13.8 |  |  | ST (Steam Turbine) | 1
26 | LADWP | 119 | City of Glendale |  | 27342 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -7.6 | 10.3 | 81 | 25 | 25 |  | GENTPF |  | IEEEG1_GE | EXDC4 | Open | 0 | 0 | CC | 25 | PF<0.8 | NO | 0 | 1 | 2.97 | 0.7425 | 0.047 | 0.37 | 7.8723 | 13.8 |  |  | CC (Combined Cycle Generic) | 1 |  | PSS Exempt
26 | LADWP | 119 | City of Glendale |  | 27344 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 0 | -6.7 | 13.6 | 81 | 25 | 25 |  | GENTPF |  | IEEEG1_GE | REXS | Open | 0 | 0 | CC | 25 | PF<0.8 | NO | 0 | 1 | 3.52 | 0.88 | 0.091 | 0.461 | 5.0659 | 13.8 |  |  | CC (Combined Cycle Generic) | 2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29004 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 48 | -14 | 28 | 999 | 3.57 | 51.57 |  | GENROU |  | GGOV1 | REXS | Open | 0 | 0 | GT | 63 |  | NO | 0 | 0.227 | 1.72 | 1.0836 | 0.297 | 0.711 | 2.3939 | 13.8 |  | GOLETA_6_ELLWOD | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29005 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 25 | -6.3 | 12.5 | 999 | 7.1 | 32.1 |  | GENROU |  | GGOV1 | EXAC1 | Closed | 22 | 4.0683 | GT | 32.1 |  | NO | 0 | 0.2 | 2.3 | 0.7383 | 0.124 | 0.286 | 2.3065 | 13.8 |  | GLNARM_7_UNIT 1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29006 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 25 | -6.3 | 12.5 | 999 | 7.1 | 32.1 |  | GENROU |  | GGOV1 | EXAC1 | Closed | 22 | 4.0683 | GT | 32.1 |  | NO | 0 | 0.2 | 2.3 | 0.7383 | 0.124 | 0.286 | 2.3065 | 13.8 |  | GLNARM_7_UNIT 2 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29009 | D1 | D1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 27.5 | 41.39 | -26.5 | 32 | 999 | 0.21 | 41.6 |  | GENTPJ |  | GGOV1 | EXAC2 | Open | 0 | 0 | CT | 48.694 | PF<0.8 | NO | 0.009 | 0.097 | 5.47 | 2.6636 | 0.111 | 0.575 | 5.1802 | 13.8 |  | CHEVMN_2_UNITS | CT (Combined Cycle Combustion Turbine Part) | D1
24 | SOCALIF | 2402 | City of Pasadena Water and Power |  | 29013 | CT | CT | [16 empty] | Missing PS |  |  | 0 | 56 | -21 | 36.63 | 999 | 3.1 | 59.1 |  | GENROU |  | GGOV1 | ESAC7B | Open | 0 | 0 | CT | 69.529 |  | NO | 0.005 | 0.177 | 1.68 | 1.1681 | 0.11 | 0.49 | 4.4545 | 13.8 |  | GLNARM_2_UNIT 5 | CT (Combined Cycle Combustion Turbine Part) | CT
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29079 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -56.96 | 56 | -38.326 | 38.326 | 999 | -56 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 72 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | CENTPD_2_BMSX2 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29081 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -58.384 | 57.5 | -39.284 | 39.284 | 999 | -57.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 73.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | CENTPD_2_BMSX2 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29087 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -200 | 208.0694 | -158.165 | 158.165 | 999 | -208.0694 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 261.36 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.66 |  | CRIMSN_2_CRMBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29088 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -150 | 156.0521 | -118.6237 | 118.6237 | 999 | -156.0521 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 196.02 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.66 |  | CRIMSN_2_CRMBT2 | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29168 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -12.15 | 12.15 | -8.538 | 8.538 | 999 | -12.15 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 14.85 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.434 |  | RATSKE_2_RBSSB1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29170 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 61.255 | -24.969 | 24.969 | 999 | -61.255 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 66.15 |  | NO | 1000000 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | RATSKE_2_RBSSB1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29198 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 12.5 | -7.5 | 7.5 | 999 | 0 | 12.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 12.5 |  | NO | 0 | 0.105 | 4.733 | 0.59162 | 0.194 | 0.0928 | 0.47835 | 4.16 |  | CONTRL_1_QF | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29199 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 14 | -11.25 | 11.25 | 999 | 4.75 | 18.75 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 18.75 | PF<0.8 | NO | 0 | 0.105 | 4.733 | 0.88744 | 0.194 | 0.0928 | 0.47835 | 4.16 |  | CONTRL_1_QF | ST (Steam Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29201 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.93 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 96 | 38.9278 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | WALCRK_2_CTG1 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29202 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.32 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 96 | 38.9963 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | WALCRK_2_CTG2 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29203 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.53 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 96 | 38.863 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | WALCRK_2_CTG3 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29204 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 55.25 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | WALCRK_2_CTG4 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29205 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 51.48 | 102.7 | -81.688 | 81.688 | 999 | 2.3 | 105 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Open | 0 | 0 | GT | 155.07 | PF<0.8 | NO | 0 | 0.189 | 1.384 | 2.1462 |  |  | NAN | 13.8 |  | WALCRK_2_CTG5 | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 25645 | Q2 | Q2 |  |  |  | Unapproved Gen Model | [8 empty] | Gen on HV | [6 empty] | 0 | 19.3 | -9.7 | -9.7 | 999 | -19.3 |  |  | WT3G |  | WT3T | WT3E | Open | 0 | 0 | W3 | 25 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | VENWD_1_WIND3 | W3 (Wind Turbine, Type 3) | Q2 |  | PSS Exempt
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29222 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 14.52 | 0 | 0 | 999 | -14.52 |  |  | WT2G | WT2P | WT2T | WT2E | Open | 0 | 0 | W2 | 14.8 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | FLOWD_2_RT2WD2 | W2 (Wind Turbine, Type 2) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29224 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 0.972 | -0.27281 | -0.27281 | 999 | 0.0437 | 1.0157 |  | WT1G | WT1P | WT1T |  | Open | 0 | 0 | W1 | 1.0157 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.48 |  | FLOWD_2_RT2WD2 | W1 (Wind Turbine, Type 1) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29295 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | -105.2898 | 105.2898 | -53.6497 | 53.6497 | 999 | -105.2898 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 118.1704 |  | NO | 999999 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | SANBRN_2_ESBBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29296 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 133.4925 | -82.7312 | 82.7312 | 999 | -133.4925 |  |  | REGC_A |  |  | REEC_A | Closed | 130 | 11.8913 | PV | 157.05 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | EDWARD_2_E21SB | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29297 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 120.911 | -76.5197 | 76.5197 | 999 | -120.911 |  |  | REGC_A |  |  | REEC_A | Closed | 115 | 8.1183 | PV | 143.09 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | EDWARD_2_ES2BT3 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29338 | G1 | G1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 24 | -14 | 14 | 999 | 5.4e-07 | 24 |  | GENROU | PSS2B | GGOV1 | EXAC8B | Open | 0 | 0 | CT | 43.882 |  | NO | 0.003 | 0.27 | 1.2 | 0.52658 | 0.056 | 0.146 | 2.6071 | 12.47 |  | CORONS_6_CLRWTR | CT (Combined Cycle Combustion Turbine Part) | G1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29340 | S1 | S1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 8.5 | -1.5 | 3.5 | 999 | -8.5 |  |  | GENROU |  |  | EXAC8B | Open | 0 | 0 | CA | 10.594 |  | NO | 0.003 | 0.27 | 2.89 | 0.30617 | 0.077 | 0.18 | 2.3377 | 12.47 |  | CORONS_12.4_STG | CA (Combined Cycle Steam Part) | S1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29360 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -54 | 53.6 | -43.4 | 43.4 | 999 | -53.6 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 68.97 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | DSFLWR_2_W9CSB1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29363 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -37 | 36.3 | -30.1 | 30.1 | 999 | -36.3 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 47.19 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | DSFLWR_2_W9CSB2 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29366 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 40.837 | -16.646 | 16.646 | 999 | -40.837 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 44.1 |  | NO | 1000000 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | RATSKE_2_RBSSB2 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29367 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -16.2 | 16.2 | -11.384 | 11.384 | 999 | -16.2 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 19.8 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.434 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29385 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 52.9051 | -35.0605 | 35.0605 | 999 | -52.9051 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 63.468 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29226 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 11.9 | -1.9248 | -1.9248 | 999 | -11.9 |  |  | WT2G | WT2P | WT2T | WT2E | Open | 0 | 0 | W2 | 12.055 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.48 |  | FLOWD_2_RT2WD2 | W2 (Wind Turbine, Type 2) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29391 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 45.5 | -13 | 13 | 999 | -45.5 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 48.96 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.38 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29394 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -38.812 | 38.912 | -59.47 | 59.47 | 999 | -38.912 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | EDWARD_2_E21SB | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29395 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -38.78 | 38.78 | -54.18 | 54.18 | 999 | -38.78 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 62.56 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | EDWARD_2_ES2BT3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29396 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -13.179 | 13.179 | -12.04 | 12.04 | 999 | -13.179 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 13.902 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | EDWARD_2_E23SB1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29397 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -12.809 | 12.809 | -18.78 | 18.78 | 999 | -12.809 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 21.336 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | SANBRN_2_ES1BT3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29392 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | -10.2 | 10.2 | -4 | 4 | 999 | -10.2 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10.2 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.38 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29711 | 3 | 3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 88.22 | -40.36 | 40.36 | 999 | -88.22 |  |  | REGC_A |  |  | REEC_B | Closed | 52.9 | -2.1183 | PV | 97.02 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.52 |  | RTEDDY_2_SC1SR3,RTEDDY_2_SEBSR3 | PV (Photovoltaic) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29712 | 4 | 4 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 88.18 | -40.41 | 40.41 | 999 | -88.18 |  |  | REGC_A |  |  | REEC_B | Closed | 52.9 | -0.27261 | PV | 97.02 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.52 |  | RTEDDY_2_SPASR4,RTEDDY_2_SEBSR4 | PV (Photovoltaic) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29763 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -52 | 51.6 | -37 | 37 | 999 | -51.6 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 64.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29764 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -77.5 | 77.5 | -49 | 49 | 999 | -77.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 93.15 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29792 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -103.9 | 103.9 | -77.4 | 77.4 | 999 | -103.9 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 129.6 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | BIGSKY_2_ASLBT2 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29801 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.5 | -14.6 | 14.6 | 999 | -20.5 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 24.6 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29827 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -60.5 | 60.5 | -43 | 43 | 999 | -60.5 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 74.8 | PF<-0.85 | NO | 0.01 | 0.2 | 0 |  |  |  | NAN | 0.48 |  | GOLETA_2_GE2BT3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29849 | 1 | 1 | [6 empty] | Limit Power Fact |  | RX Ratio | [10 empty] | -10.773 | 10.773 | -15.65 | 15.65 | 999 | -10.773 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 17.778 | PF<0.8 | NO | 999999 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | SANBRN_2_ES2SB3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29850 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -40.1961 | 40.1961 | -59.47 | 59.47 | 999 | -40.1961 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | SANBRN_2_EESSB2 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29851 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -38.1694 | 38.1694 | -55.7402 | 55.7402 | 999 | -38.1694 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | EDWARD_2_E21SB1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29852 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -35.7466 | 35.7466 | -47.0451 | 47.0451 | 999 | -35.7466 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 59.09 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | EDWARD_2_ES2BT3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29853 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -11.8401 | 11.8401 | -17.7464 | 17.7464 | 999 | -11.8401 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 21.336 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | SANBRN_2_ES1BT3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29854 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -9.6001 | 9.6001 | -14.9631 | 14.9631 | 999 | -9.6001 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 17.778 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | SANBRN_2_ES2SB3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29855 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -40.1961 | 40.1961 | -54.2968 | 54.2968 | 999 | -40.1961 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 67.556 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29712 | 5 | 5 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20.05 | -12.27 | 12.27 | 999 | -20.05 |  |  | REGC_A |  |  | REEC_B | Closed | 12 | -0.27261 | PV | 23.52 |  | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.52 |  | RTEDDY_2_SRXSR4 | PV (Photovoltaic) | 5
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29914 | 1 | 1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | 0 | 10 | -11.19 | 11.19 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 11.19 | PF<0.8 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.42 |  | PLAINV_6_DSOLAR | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29917 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.7 | 9.7 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.8 |  | PLAINV_6_SOLAR3 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29952 | D1 | D1 | [16 empty] | Missing PS |  |  | 0 | 28 | -7 | 14 | 999 | -28 |  |  | GENROU |  |  | EXST4B | Closed | 26.2 | 5.7428 | CC | 35.8 |  | NO | 0 | 0.18 | 2.4 | 0.8592 | 0.05 | 0.3 | 6 | 13.8 |  | SNCLRA_2_UNIT | CC (Combined Cycle Generic) | D1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | SUNSHN_2_LNDFL | GT (Gas Turbine) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | SUNSHN_2_LNDFL | GT (Gas Turbine) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | SUNSHN_2_LNDFL | GT (Gas Turbine) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | SUNSHN_2_LNDFL | GT (Gas Turbine) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29954 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.7 | -1.5 | 3 | 999 | -4.7 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | GT | 5.75 |  | NO | 0 | 0.2 | 3 | 0.1725 | 0.194 | 0.0928 | 0.47835 | 13.8 |  | SUNSHN_2_LNDFL | GT (Gas Turbine) | 5
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29965 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -71.7155 | 66.4645 | -44.8833 | 44.8833 | 999 | -66.4645 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 80.2 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29966 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -48.5496 | 45.0248 | -33.5331 | 33.5331 | 999 | -45.0248 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 56.14 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 30464 | 1 | 1 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS | Missing Sub R/X |  | 0 | 54 | -22 | 32.3 | 999 | -54 |  |  | GENTPF |  |  | EXST1_GE | Closed | 28.6 | 32.3 | JE | 64.35 |  | NO | 0 | 1e-05 | 4.11 | 2.6448 | 0.126 | 0.357 | 2.8333 | 12.47 |  | WEBER_6_FORWRD | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31152 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12.5 | -12.4 | 17.2 | 999 | 0 | 12.5 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 11.72 | 1.7243 | ST | 25 | PF<0.8 | NO | 0 | 0.155 | 4.35 | 1.0875 | 0.091 | 0.325 | 3.5714 | 13.8 |  | PACLUM_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31152 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12.5 | -12.4 | 17.2 | 999 | 0 | 12.5 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 11.72 | 1.7243 | ST | 25 | PF<0.8 | NO | 0 | 0.155 | 4.35 | 1.0875 | 0.091 | 0.325 | 3.5714 | 13.8 |  | PACLUM_6_UNIT | ST (Steam Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31156 | MB | MB | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 12 | -4.31 | 4.31 | 999 | -12 | [6 empty] | Open | 0 | 0 | UN | 13.8 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.47 |  | BLULKE_6_BLUELK | UN (Unknown) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31158 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 25 | -8.3 | 12.5 | 999 | 2 | 27 |  | GENROU |  | GGOV1 | EXST1_GE | Open | 0 | 0 | ST | 52 |  | NO | 0 | 1 | 2.9474 | 1.5326 | 0.152 | 0.59 | 3.8816 | 12.47 |  | LAPAC_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.7 | 7.2087 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 5 | 5 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.7 | 7.2087 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 5
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 6 | 6 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.7 | 7.2087 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 6
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31180 | 7 | 7 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.738 | -12.34 | 12.34 | 999 | 0.302 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.7 | 7.2087 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_1_UNITS3 | IC (Internal Combustion) | 7
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31181 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -2.1982 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 1 | IC (Internal Combustion) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31181 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -2.1982 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 2 | IC (Internal Combustion) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31181 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -2.1982 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 3 | IC (Internal Combustion) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31182 | 10 | 10 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -2.2149 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 10 | IC (Internal Combustion) | 10
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31182 | 8 | 8 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -2.2149 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 8 | IC (Internal Combustion) | 8
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31182 | 9 | 9 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 16.662 | -12.445 | 12.445 | 999 | 0.378 | 17.04 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 16.662 | -2.2149 | IC | 20.8 | PF<-0.85 | NO | 0 | 0.206 | 1.608 | 0.33446 | 0.127 | 0.391 | 3.0787 | 13.8 |  | HUMBPP_6_UNITS unit 9 | IC (Internal Combustion) | 9
30 | PG AND E | 470 | Calpine Corp. |  | 31400 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 15.8 | 32.3 | -16.1 | 32.3 | 999 | -32.3 |  |  | GENTPJ | PSS2A |  | ESAC7B | Closed | 32.3 | 2.6441 | ST | 98 | PF<0.8 | NO | 0.004 | 0.276 | 4.3 | 4.214 | 0.104 | 0.588 | 5.6538 | 13.8 |  | SANTFG_7_UNITS | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31401 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 13.5 | 33.7 | -13.5 | 32 | 999 | -33.7 |  |  | GENTPJ | PSS2A |  | ESAC7B | Closed | 32.3 | 2.6441 | ST | 98 | PF<0.8 | NO | 0.004 | 0.276 | 4.3 | 4.214 | 0.104 | 0.588 | 5.6538 | 13.8 |  | SANTFG_7_UNITS | ST (Steam Turbine) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 31402 | R1 | R1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -3.3 | 5 | 999 | 2 | 12 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 12 |  | NO | 0 | 1 | 5.3268 | 0.63922 | 0.267 | 0.763 | 2.8577 | 13.8 |  | BEARCN_2_UNITS | OT (Other) | R1
30 | PG AND E | 470 | Calpine Corp. |  | 31402 | R2 | R2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -3.3 | 5 | 999 | 2 | 12 |  | GENTPF |  | GGOV1 | EXAC1 | Open | 0 | 0 | OT | 12 |  | NO | 0 | 1 | 5.3268 | 0.63922 | 0.267 | 0.763 | 2.8577 | 13.8 |  | BEARCN_2_UNITS | OT (Other) | R2
30 | PG AND E | 470 | Calpine Corp. |  | 31414 | 1 | 1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 27 | 48 | -10 | 40 | 999 | -48 |  |  | GENROU | PSS2B |  |  | Closed | 48 | -6.1093 | ST | 132 | PF<0.8 | NO | 0.001 | 0.234 | 3.83 | 5.0556 | 0.075 | 0.293 | 3.9067 | 13.8 |  | GEYS12_7_UNIT12 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31416 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 27.6 | 55.7 | -34.6 | 32.8 | 999 | -55.7 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 55.7 | 2.6725 | ST | 155.3 | PF<-0.85 | NO | 0.004 | 0.189 | 4.7 | 7.2991 | 0.072 | 0.22 | 3.0556 | 13.8 |  | GEYS13_7_UNIT13 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31418 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 109 | -47.8 | 90 | 999 | -109 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 70 | 17.2645 | BT | 137.8 | PF<0.8 | NO | 0 | 1 | 4.8 | 6.6144 | 0.113 | 0.304 | 2.6903 | 13.8 |  | GEYS14_7_UNIT14 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31420 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 29.3 | 48.2 | -33.46 | 68.89 | 999 | -48.2 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 48.2 | -9.8805 | ST | 137.8 | PF<0.8 | NO | 0.002 | 0.258 | 3.75 | 5.1675 | 0.06 | 0.2 | 3.3333 | 13.8 |  | GEYS16_7_UNIT16 | ST (Steam Turbine) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 31421 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 55 | -15.886 | 26.64 | 999 | 166.4 | 221.4 |  | GENTPF | IEEEST | GGOV1 | REXS | Open | 0 | 0 | BT | 221.4 |  | NO | 0 | 1e-05 | 5.52 | 12.2213 | 0.216 | 0.74 | 3.4259 | 13.8 |  | GEYS17_2_BOTRCK | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31422 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 27.7 | 64 | -22 | 49.5 | 999 | -64 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 64 | -12.9613 | ST | 137.8 | PF<0.8 | NO | 0.002 | 0.258 | 3.75 | 5.1675 | 0.06 | 0.2 | 3.3333 | 13.8 |  | GEYS17_7_UNIT17 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31424 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 21.6 | 62.8 | -24 | 58 | 999 | -62.8 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 62.8 | 6.4312 | ST | 137.8 | PF<0.8 | NO | 0 | 0.227 | 3.85 | 5.3053 | 0.095 | 0.308 | 3.2421 | 13.8 |  | GEYS18_7_UNIT18 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31426 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 26.2 | 45.8 | -29 | 83 | 999 | -45.8 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 45.8 | 4.9663 | ST | 137.8 | PF<0.8 | NO | 0.002 | 0.258 | 3.75 | 5.1675 | 0.06 | 0.2 | 3.3333 | 13.8 |  | GEYS20_7_UNIT20 | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31435 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 3.95 | 11.35 | -3.7 | 6.7 | 999 | -11.35 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 11.35 | 0.20814 | ST | 13.89 |  | NO | 0 | 0.08 | 5 | 0.6945 | 0.193 | 0.47 | 2.4352 | 13.8 |  | ADLIN_1_UNITS | ST (Steam Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 31437 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 3.91 | 9 | -4.4 | 7.7 | 999 | -9 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 9 | 0.15371 | ST | 13.89 | PF<0.8 | NO | 0 | 0.08 | 5 | 0.6945 | 0.157 | 0.376 | 2.3949 | 13.8 |  | ADLIN_1_UNITS | ST (Steam Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31763 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 2.2 | -0.33 | 1.66 | 999 | -2.2 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.3 | 1.5039 | IT | 3 | PF<0.8 | NO | 0 | 1e-05 | 3.6963 | 0.11089 | 0.126 | 0.357 | 2.8333 | 4.16 |  | ESQUON_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31763 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 2.2 | -0.33 | 1.66 | 999 | -2.2 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.3 | 1.5039 | IT | 3 | PF<0.8 | NO | 0 | 1e-05 | 3.6963 | 0.11089 | 0.126 | 0.357 | 2.8333 | 4.16 |  | ESQUON_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31764 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 32.5 | -10 | 16 | 999 | -1.5 | 31 |  | GENTPJ |  | HYG3 | ESST1A_GE | Closed | 10.57 | -0.22021 | HY | 34.3 |  | NO | 0 | 1 | 1.72 | 0.58996 | 0.1 | 0.2 | 2 | 13.8 |  | MALCHQ_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31786 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 55 | -40 | 40 | 999 | -55 |  |  | GENTPJ | PSS2A | H6E | ESST4B | Closed | 54.25 | -6.2947 | HY | 70 | PF<-0.85 | NO | 0 | 0.19 | 4.8 | 3.36 | 0.096 | 0.277 | 2.8854 | 13.8 |  | RCKCRK_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31788 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 55 | -40.16 | 40.16 | 999 | -55 |  |  | GENTPJ | PSS2A | H6E | ESST4B | Closed | 54.25 | -1.9733 | HY | 70 | PF<-0.85 | NO | 0 | 0.19 | 4.8 | 3.36 | 0.096 | 0.277 | 2.8854 | 13.8 |  | RCKCRK_7_UNIT 2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 906 | Burney Forest Products |  | 31798 | 1 | 1 | [16 empty] | Missing PS |  |  | 8 | 31.75 | -5.49 | 13.07 | 999 | 0.01 | 31.76 |  | GENTPJ |  | GGOV1 | EXST1_GE | Closed | 31.66 | 1.2465 | ST | 34.23 |  | NO | 0 | 0.209 | 2.7353 | 0.93629 | 0.126 | 0.357 | 2.8333 | 13.2 |  | BURNYF_2_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31800 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 42 | -14 | 21 | 999 | 2 | 44 |  | GENTPF |  | GGOV1 | EXST1_GE | Open | 0 | 0 | JE | 46.6 |  | NO | 0 | 1 | 2.7039 | 1.26 | 0.124 | 0.55 | 4.4355 | 12.47 |  | SMPAND_7_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31806 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 39.14 | -14 | 14 | 999 | 0.86 | 40 |  | GENQEC |  | HYGOV | DC1C | Closed | 39.1 | 2.1401 | HY | 41.6 |  | NO | 0.004 | 0.208 | 3.36 | 1.3978 |  |  | NAN | 11.5 |  | PIT5_7_PL3X4 | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31806 | 4 | 4 | [16 empty] | Missing PS |  |  | 0 | 43.3 | -15.6 | 15.6 | 999 | 6.7 | 50 |  | GENQEC |  | HYGOV | DC1C | Closed | 43.3 | 2.1401 | HY | 46 |  | NO | 0.004 | 0.23 | 3.36 | 1.5456 |  |  | NAN | 11.5 |  | PIT5_7_PL3X4 | HY (Hydro) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31808 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 25 | -13.29 | 13.29 | 999 | 2.7 | 27.7 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 25 | 5.2223 | HY | 30.5 |  | NO | 0.002 | 0.307 | 3.084 | 0.94062 | 0.202 | 0.529 | 2.6188 | 11.5 |  | CARBOU_7_PL2X3 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31808 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 25 | -12.16 | 12.16 | 999 | 2.7 | 27.7 |  | GENTPJ | PSS2A | HYGOV4 | ESST4B | Closed | 25 | 5.2223 | HY | 27.7 |  | NO | 0.002 | 0.307 | 3.1 | 0.8587 | 0.202 | 0.529 | 2.6188 | 11.5 |  | CARBOU_7_PL2X3 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31810 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 25 | -8 | 7.6 | 999 | 2.45 | 27.45 |  | GENTPJ |  | HYGOV | EXST1_GE | Closed | 25 | 7.6 | HY | 26.5 |  | NO | 0.002 | 0.266 | 3.084 | 0.81726 | 0.2017 | 0.5287 | 2.6212 | 11.5 |  | CARBOU_7_UNIT1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31812 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 35 | -24.19 | 24.19 | 999 | -0.31 | 34.69 |  | GENTPJ |  | HYGOV | EXDC4 | Closed | 35 | -0.87169 | HY | 43 | PF<-0.85 | NO | 0 | 0.184 | 3.29 | 1.4147 | 0.1156 | 0.4926 | 4.2612 | 11.5 |  | CRESTA_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31820 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 30 | -21.78 | 21.78 | 999 | 2.7 | 32.7 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 29 | 2.3492 | HY | 36.3 | PF<-0.85 | NO | 0 | 0.2 | 2.426 | 0.88064 | 0.0847 | 0.2636 | 3.1122 | 11 |  | BUCKCK_7_PL1X2 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31820 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 30 | -21.78 | 21.78 | 999 | 2.7 | 32.7 |  | GENTPJ | PSS2B | HYG3 | ESST4B | Closed | 30 | 2.3492 | HY | 36.3 | PF<-0.85 | NO | 0 | 0.2 | 2.426 | 0.88064 | 0.0847 | 0.2636 | 3.1122 | 11 |  | BUCKCK_7_PL1X2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31826 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7 | -2.9 | 3.8 | 999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.12 | 3.8 | HY | 7 |  | NO | 0 | 1 | 4.64 | 0.3248 | 0.152 | 0.59 | 3.8816 | 4.16 |  | SOUTH_2_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31828 | MB | MB | [16 empty] | Missing PS |  |  | 0 | 1.6 | 0 | 0 | 999 | -1.6 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | KILARC_2_UNIT 1 | HY (Hydro) | MB
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31830 | MB | MB | [16 empty] | Missing PS |  |  | 0 | 2.4 | -0.4 | 0.6 | 999 | -2.4 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 2.4 |  | HMLTBR_6_UNITS | HY (Hydro) | MB
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31840 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 6.1 | -0.95 | 1.4 | 999 | -6.1 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.5 | 1.4 | HY | 6 |  | NO | 0 | 1 | 4.64 | 0.2784 | 0.152 | 0.59 | 3.8816 | 9.11 |  | BLCKBT_2_STONEY | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31846 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7 | -2.3 | 3.5 | 999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.27 | 3.5 | HY | 5 |  | NO | 0 | 1 | 4.64 | 0.232 | 0.152 | 0.59 | 3.8816 | 13.8 |  | COVERD_2_HCKHY1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31846 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -1.7 | 2.5 | 999 | -5 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.58 | 2.5 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 13.8 |  | COVERD_2_MCKHY1 | HY (Hydro) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31847 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 2.6 | -0.8 | 1.3 | 999 | -2.6 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.6 | 1.3 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 13.8 |  | COVERD_2_QFUNTS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31855 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 3 | -1 | 1.5 | 999 | -3 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 0.35 | -1 | HY | 3 |  | NO | 0 | 1 | 4.64 | 0.1392 | 0.152 | 0.59 | 3.8816 | 9.11 |  | TKOPWR_6_HYDRO | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31870 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 11.6 | -3.8 | 5.8 | 999 | -11.6 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 10 | -3.8 | HY | 12 |  | NO | 0 | 1 | 4.64 | 0.5568 | 0.152 | 0.59 | 3.8816 | 9.11 |  | FORKBU_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31870 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 1.7 | -0.6 | 0.9 | 999 | -1.7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 1.7 | -0.6 | HY | 2 |  | NO | 0 | 1 | 4.64 | 0.0928 | 0.152 | 0.59 | 3.8816 | 9.11 |  | FORKBU_6_UNIT | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31888 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 8.12 | -6 | 6 | 999 | 2.38 | 10.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 8.02 | 6 | GT | 9 | PF<-0.85 | NO | 0 | 0.206 | 4.3022 | 0.3872 | 0.14 | 0.574 | 4.1 | 4.16 |  | OROVIL_6_UNIT | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 31895 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 5.625 | -1.95 | 2.72 | 999 | 0.625 | 6.25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 5.32 | 2.72 | ST | 6.25 |  | NO | 0 | 1e-05 | 1 | 0.0625 | 0.227 | 0.779 | 3.4317 | 13.8 |  | COLPIN_6_COLLNS | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 31908 | MB | MB | [16 empty] | Missing PS |  |  | 0 | 8 | -2.5 | 4.5 | 999 | -8 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 4.16 |  | INSKIP_2_UNIT | HY (Hydro) | MB
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 29921 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -6.8415 | 6.8415 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | PLAINV_6_NLRSR1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240542 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10.58 | -4.5 | 4.5 | 999 | -10.58 |  |  | REGC_A |  |  | REEC_B | Closed | 10.5 | -2.2922 | PV | 11.5 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 339 | Hatchet Ridge Wind LLC |  | 31914 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 24 | -12 | 8.28 | 999 | -24 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 8.66 | -0.93724 | W4 | 26.67 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 1
30 | PG AND E | 339 | Hatchet Ridge Wind LLC |  | 31914 | 2 | 2 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 24 | -12 | 8.28 | 999 | -24 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 8.66 | -0.93724 | W4 | 26.67 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 2
30 | PG AND E | 339 | Hatchet Ridge Wind LLC |  | 31914 | 3 | 3 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 24 | -12 | 8.28 | 999 | -24 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 8.66 | -0.93724 | W4 | 26.67 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32154 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 29.07 | -5.3 | 14.07 | 999 | -0.42 | 28.65 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 27.81 | -2.4271 | ST | 32.3 |  | NO | 0 | 0.17 | 3.6 | 1.1628 | 0.08 | 0.25 | 3.125 | 13.8 |  | WADHAM_6_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32156 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 28 | -11 | 13 | 999 | 0.0099999 | 28.01 |  | GENTPJ |  | IEEEG1_GE | ESAC1A | Closed | 27.74 | 5.0489 | ST | 37 |  | NO | 0.001 | 0.148 | 4.97 | 1.8389 | 0.08 | 0.36 | 4.5 | 13.8 |  | BIOMAS_1_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32172 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 160.2 | -56.85 | 56.85 | 999 | -160.2 |  |  | WT2G |  | WT2T | WT2E | Closed | 150 | -22.2284 | W2 | 169.99 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BRDSLD_2_HIWIND | W2 (Wind Turbine, Type 2) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32172 | 2 | 2 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 1.79 | -0.575 | 0.575 | 999 | -1.79 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 1.79 | -0.575 | W3 | 1.88 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 32173 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 20 | 48 | -7.9 | 21.5 | 999 | 3.25 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 48 | 2.9994 | JE | 71.176 |  | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.103 | 0.359 | 3.4854 | 13.8 |  | LMBEPK_2_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32174 | 3 | 3 | [9 empty] | Unreas H | [9 empty] | 20.5 | 48.7 | -11.6 | 27.83 | 999 | 2.55 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 48.7 | 3.0855 | JE | 71.176 |  | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.13 | 0.384 | 2.9538 | 13.8 |  |  | JE (Jet Engine) | 3
30 | PG AND E | 470 | Calpine Corp. |  | 32175 | 2 | 2 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [9 empty] | 20 | 46 | -11.2918 | 27 | 999 | 5.25 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 46 | -11.2918 | JE | 71.176 |  | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.093 | 0.349 | 3.7527 | 13.8 |  |  | JE (Jet Engine) | 2
30 | PG AND E | 339 | Hatchet Ridge Wind LLC |  | 31914 | 4 | 4 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 19.2 | -9.6 | 6.62 | 999 | -19.2 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 7.16 | -0.93724 | W4 | 21.33 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32181 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 150 | -72.65 | 49.3 | 999 | -150 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 150 | 49.3 | W3 | 167 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  | BRDSLD_2_SHILO1 | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32185 | 1 | 1 | [9 empty] | Unreas H | [7 empty] | Missing Sub R/X |  | 0 | 60.5 | -22.2 | 37.5 | 999 | -9.25 | 51.25 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 48.5 | 13.1985 | JE | 71.176 |  | NO | 0 | 1e-05 | 1.17 | 0.83276 | 0.1 | 0.285 | 2.85 | 13.8 |  | WOLFSK_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32188 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 36.8 | -14.26 | 14.26 | 999 | -36.8 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 14 | 14.26 | W4 | 39.47 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | WNDSTR_2_WIND | W4 (Wind Turbine, Type 4) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32450 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 170.5 | -45 | 57 | 999 | 4.5 | 175 |  | GENTPJ | PSS2B | HYG3 | ESDC4B | Closed | 120 | 38.4949 | HY | 175 |  | NO | 0 | 1e-05 | 2.87 | 5.0225 | 0.15 | 0.35 | 2.3333 | 13.8 |  | COLGAT_7_UNIT 1 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32451 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 50 | -16.4 | 31 | 999 | 0 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Closed | 48.79 | -8.34 | JE | 71.2 |  | NO | 0 | 0.247 | 1.17 | 0.83304 | 0.112 | 0.461 | 4.1161 | 13.8 |  | BOGUE_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 3001 | Placer County Water Agency |  | 32456 | 1 | 1 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 63 | -25.6 | 25.6 | 999 | 5 | 68 |  | GENTPJ | PSS2B | HYG3 |  | Closed | 63 | 15.0013 | HY | 68 |  | NO | 0.004 | 0.243 | 2.867 | 1.9496 | 0.17 | 0.29 | 1.7059 | 13.8 |  | MDFKRL_2_PROJCT | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 3001 | Placer County Water Agency |  | 32456 | 2 | 2 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 64 | -23 | 23 | 999 | 4 | 68 |  | GENTPJ | PSS2B | HYG3 |  | Closed | 64 | 15.0013 | HY | 68 |  | NO | 0.004 | 0.243 | 2.867 | 1.9496 | 0.17 | 0.29 | 1.7059 | 13.8 |  | MDFKRL_2_PROJCT | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32464 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 22.13 | -16.32 | 16.32 | 999 | -22.13 |  |  | GENTPJ |  | H6E | ESDC4B | Closed | 21.42 | 1.5691 | HY | 27.5 | PF<-0.85 | NO | 0 | 0.172 | 2.78 | 0.7645 | 0.0726 | 0.313 | 4.3113 | 11 |  | DUTCH1_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32472 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7 | -2.9 | 3.5 | 999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.92 | 3.5 | HY | 19 |  | NO | 0 | 1 | 4.64 | 0.8816 | 0.152 | 0.59 | 3.8816 | 9.11 |  | SPAULD_6_UNIT12 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32472 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 4.4 | -1 | 1.9 | 999 | -4.4 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 2.46 | 1.9 | HY | 19 |  | NO | 0 | 1 | 4.64 | 0.8816 | 0.152 | 0.59 | 3.8816 | 9.11 |  | SPAULD_6_UNIT12 | HY (Hydro) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32472 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5.8 | -2 | 4 | 999 | -5.8 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.23 | 4 | HY | 19 |  | NO | 0 | 1 | 4.64 | 0.8816 | 0.152 | 0.59 | 3.8816 | 9.11 |  | SPAULD_6_UNIT 3 | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32476 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 12.2 | -5.78 | 5.78 | 999 | -12.2 |  |  | GENTPJ |  |  | ESST4B | Closed | 12.2 | 5.78 | HY | 13.5 |  | NO | 0 | 0.384 | 2.52 | 0.3402 | 0.1 | 0.36 | 3.6 | 6.6 |  | ROLLIN_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32478 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.4 | -10.07 | 10.07 | 999 | -10.4 |  |  | GENTPJ |  | H6E |  | Closed | 5.52 | -0.36684 | HY | 17 | PF<0.8 | NO | 0 | 0.29 | 3.5 | 0.595 | 0.11 | 0.242 | 2.2 | 6.6 |  | HALSEY_6_UNIT | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32484 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 6 | -2 | 1.9 | 999 | -6 |  |  | GENTPF |  |  | EXDC1 | Closed | 3.28 | 1.9 | HY | 7 |  | NO | 0 | 1 | 2.2713 | 0.15899 | 0.1904 | 0.548 | 2.8782 | 9.11 |  | OXBOW_6_DRUM | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32489 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -2.42 | 2.42 | 999 | 2.222 | 7.222 |  | GENTPJ |  | GGOV1 | EXST1_GE | Closed | 5 | -2.42 | HY | 7.222 |  | NO | 0 | 0.314 | 1.266 | 0.091431 | 0.152 | 0.59 | 3.8816 | 4.16 |  | HAYPRS_6_HAYHD2 upper haypress | HY (Hydro) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32490 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 15 | 30.2 | -16.1 | 23.5 | 999 | 9.8 | 40 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Open | 0 | 0 | JE | 41.111 | PF<0.8 | NO | 0 | 0.18 | 1.8 | 0.74 | 0.08 | 0.264 | 3.3 | 13.8 |  | GRNLF1_1_PL1X2 ctg1 1a | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32491 | 2 | 2 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact | [12 empty] | 15 | 30 | -16.1 | 23.5 | 999 | 10 | 40 |  | GENTPJ | PSS2B | GGOV3 | ESAC7B | Closed | 30.2 | 0.71223 | JE | 41.111 | PF<0.8 | NO | 0 | 0.18 | 1.8 | 0.74 | 0.08 | 0.264 | 3.3 | 13.8 |  | GRNLF1_1_PL1X2 ctg2 1b | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32492 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 49.5 | -14 | 22 | 999 | -3.5 | 46 |  | GENROU |  | GGOV1 | ESAC1A | Closed | 49.5 | -2.2441 | JE | 49.5 |  | NO | 0 | 1 | 2.15 | 1.0643 | 0.13 | 0.4 | 3.0769 | 13.8 |  | GRNLF2_1_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32494 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 20.4 | 49.9 | -18 | 24.16 | 999 | -1.29e-06 | 49.9 |  | GENTPJ |  | GGOV1 | ESAC1A | Closed | 49 | -1.0905 | JE | 55.448 |  | NO | 0 | 0.155 | 2 | 1.109 | 0.2 | 0.6 | 3 | 13.8 |  | YUBACT_1_SUNSWT | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 32496 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 20.4 | 49.04 | -16.95 | 51.5 | 999 | 2.21 | 51.25 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 48.58 | -4.8654 | JE | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.17 | 0.83276 | 0.18 | 0.371 | 2.0611 | 13.8 |  | YUBACT_6_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 963 | Rio Bravo Rocklin |  | 32500 | 1 | 1 | [16 empty] | Missing PS |  |  | 16 | 27.65 | -10 | 17.35 | 999 | 0.35 | 28 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 26.62 | 4.8163 | ST | 32.94 |  | NO | 0 | 0.17 | 4.2 | 1.3835 | 0.092 | 0.275 | 2.9891 | 12.47 |  | ULTRCK_2_UNIT | ST (Steam Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32512 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 20.1 | -6 | 9 | 999 | -20.1 |  |  | GENTPF |  |  | EXDC1 | Closed | 8.16 | 9 | HY | 25 |  | NO | 0 | 1 | 2.612 | 0.653 | 0.169 | 0.556 | 3.2899 | 12.47 |  | WISE_1_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32513 | 1 | 1 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 10 | -3.3 | 7.5 | 999 | -10 |  |  | GENTPJ |  |  |  | Closed | 7.37 | 4.1586 | HY | 12.5 | PF<0.8 | NO | 0 | 1e-05 | 4.64 | 0.58 | 0.152 | 0.59 | 3.8816 | 21.6 |  | ELDORO_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 32514 | 1 | 1 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 10 | -3.3 | 7.5 | 999 | -10 |  |  | GENTPJ |  |  |  | Closed | 7.78 | 4.1756 | HY | 12.5 | PF<0.8 | NO | 0 | 1e-05 | 4.64 | 0.58 | 0.152 | 0.59 | 3.8816 | 21.6 |  | ELDORO_7_UNIT 2 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32700 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 5 | 0 | 0 | 999 | -5 |  |  | GENTPF |  |  | EXAC1 | Closed | 3.44 | 0 | HY | 5 |  | NO | 0 | 1 | 2.6998 | 0.13499 | 0.5 | 1.22 | 2.44 | 9.11 |  | MONTPH_7_UNITS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32700 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 5 | 0 | 0 | 999 | -5 |  |  | GENTPF |  |  | EXAC1 | Closed | 3.44 | 0 | HY | 5 |  | NO | 0 | 1 | 2.6998 | 0.13499 | 0.5 | 1.22 | 2.44 | 9.11 |  | MONTPH_7_UNITS | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32700 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.5 | 0 | 0 | 999 | -1.5 |  |  | GENTPF |  |  | EXAC1 | Closed | 1.04 | 0 | HY | 1 |  | NO | 0 | 1 | 3.54 | 0.0354 | 0.5 | 1.22 | 2.44 | 9.11 |  | MONTPH_7_UNITS | HY (Hydro) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32741 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 17.1 | 23.04 | -9 | 16.9 | 999 | 5.76 | 28.8 |  | GENROU |  | GGOV1 | ESAC8B_GE | Closed | 17.1 | 16.9 | CT | 28.8 |  | NO | 0 | 0.175 | 2 | 0.576 | 0.04 | 0.18 | 4.5 | 12.47 |  | GRZZLY_1_BERKLY | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32741 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0.3 | 5.5 | -3 | 4.1 | 999 | -5.5 |  |  | GENROU |  |  | ESAC1A | Closed | 3.81 | 4.1 | CA | 6.88 |  | NO | 0 | 0.199 | 1.15 | 0.07912 | 0.08 | 0.23 | 2.875 | 12.47 |  |  | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32741 | RN | RN | [17 empty] | Missing Sub R/X |  | 0 | 0.396 | 0 | 0 | 999 | -0.396 |  |  | DER_A |  |  |  | Closed | 0.396 | 0 | PV | 0.326 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1230-RD 1314-RD 1340-RD | PV (Photovoltaic) | RN
30 | PG AND E | 437 | Dynegy Inc. |  | 32901 | 1 | 1 | [16 empty] | Missing PS |  |  | 14.8 | 54 | -23.2 | 26.15 | 999 | -2.15e-06 | 54 |  | GENROU |  | GGOV1 | REXS | Open | 0 | 0 | JE | 74.5 |  | NO | 0 | 0.134 | 2.17 | 1.6167 | 0.17 | 0.568 | 3.3412 | 13.8 |  | OAK C_7_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32910 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 16.7 | -13 | 19.7 | 999 | 2 | 18.7 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 11.76 | 19.7 | GT | 16 | PF<0.8 | NO | 0 | 1 | 4.2706 | 0.6833 | 0.126 | 0.357 | 2.8333 | 12 |  | UNOCAL_1_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32910 | 2 | 2 | [5 empty] | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 16.6 | -13 | 19.7 | 999 | 2 | 18.6 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 11.69 | 19.7 | GT | 16 | PF<0.8 | NO | 0 | 1 | 4.2706 | 0.6833 | 0.126 | 0.357 | 2.8333 | 12 |  | UNOCAL_1_UNITS | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32910 | 3 | 3 | [5 empty] | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 16.6 | -12.9 | 19.6 | 999 | 2 | 18.6 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 11.69 | 19.6 | GT | 16 | PF<0.8 | NO | 0 | 1 | 4.2706 | 0.6833 | 0.126 | 0.357 | 2.8333 | 12 |  | UNOCAL_1_UNITS | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32920 | RT | RT | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 27.4 | -8.55 | 13 | 999 | -27.4 | [6 empty] | Open | 0 | 0 | UN | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | UNCHEM_1_UNIT | UN (Unknown) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32921 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 20 | 54 | -15 | 32.49 | 999 | 2 | 56 |  | GENTPF |  | GGOV1 | EXDC1 | Closed | 54 | 23.4073 | GT | 51 |  | NO | 0 | 1 | 5.098 | 2.6 | 0.1929 | 0.711 | 3.6858 | 13.8 |  | STOILS_1_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32922 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 20 | 54 | -15 | 32.49 | 999 | 2 | 56 |  | GENTPF |  | GGOV1 | EXDC1 | Closed | 54 | 23.3418 | GT | 51 |  | NO | 0 | 1 | 5.098 | 2.6 | 0.1929 | 0.711 | 3.6858 | 13.8 |  | STOILS_1_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32923 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 20 | 25 | -15 | 7.809 | 999 | 1 | 26 |  | GENTPF |  | GGOV1 | EXDC1 | Closed | 25 | -1.7267 | GT | 25 |  | NO | 0 | 1 | 5.098 | 1.2745 | 0.1929 | 0.711 | 3.6858 | 13.8 |  | STOILS_1_UNITS | GT (Gas Turbine) | 3
30 | PG AND E | 339 | Hatchet Ridge Wind LLC |  | 31914 | 5 | 5 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 12 | -6 | 4.41 | 999 | -12 |  |  | GEWTG |  | WNDTGE | EXWTGE | Closed | 4.52 | -0.93724 | W4 | 13.33 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | HATRDG_2_WIND | W4 (Wind Turbine, Type 4) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33103 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 999 | -10 | [6 empty] | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21.6 |  | 1787-RD | PV (Photovoltaic) | RE
30 | PG AND E | 470 | Calpine Corp. |  | 33108 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 122.8 | 179.6 | -64.8 | 84.4 | 999 | 6.4 | 186 |  | GENTPJ | PSS2B | GGOV3 | ESST6B | Open | 0 | 0 | CT | 250 |  | NO | 0 | 1e-05 | 5.92 | 14.8 | 0.068 | 0.182 | 2.6765 | 18 |  | DELTA_2_PL1X4 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33109 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 122.9 | 166.9 | -66.9 | 70.1 | 999 | 19.1 | 186 |  | (GENTPJ) | (PSS2B) | (GGOV3) | (ESST6B) | Closed | 166.9 | 30.5714 | CT | 250 |  | NO | 0 | 1e-05 | 0 |  | 0.067 | 0.204 | 3.0448 | 18 |  | DELTA_2_PL1X4 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33110 | 1 | 1 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 122.6 | 166.9 | -60.7 | 89.6 | 999 | 19.1 | 186 |  | (GENTPJ) | (PSS2B) | (GGOV3) | (ESST6B) | Closed | 166.9 | 30.6191 | CT | 250 |  | NO | 0 | 1e-05 | 0 |  | 0.068 | 0.182 | 2.6765 | 18 |  | DELTA_2_PL1X4 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 33111 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 85 | 169 | -66 | 117 | 999 | 0.59999 | 169.6 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 200 | 31.0245 | GT | 234 |  | NO | 0 | 0.534 | 4.76 | 11.1384 | 0.075 | 0.269 | 3.5867 | 18 |  | LMEC_1_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33119 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 196 | -65 | 98 | 999 | -22 | 174 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Open | 0 | 0 | GT | 239 |  | NO | 0 | 0.201 | 4.7 | 11.233 | 0.068 | 0.58 | 8.5294 | 18 |  | GATWAY_2_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33120 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 196 | -65 | 98 | 999 | -22 | 174 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Open | 0 | 0 | GT | 239 |  | NO | 0 | 0.201 | 4.7 | 11.233 | 0.068 | 0.58 | 8.5294 | 18 |  | GATWAY_2_PL1X3 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33141 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 23.5 | -6.5 | 15 | 999 | 2 | 25.5 |  | GENTPF | WSCCST | GGOV1 | EXST1_GE | Closed | 23.5 | 8.4419 | GT | 23 |  | NO | 0 | 1 | 3.0143 | 0.69329 | 0.0833 | 0.146 | 1.7527 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33142 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 43.6 | -13 | 30 | 999 | 2 | 45.6 |  | GENTPF | WSCCST | GGOV1 | EXST1_GE | Closed | 43.6 | 11.8231 | GT | 43 |  | NO | 0 | 1 | 6.6463 | 2.8579 | 0.0615 | 0.154 | 2.5041 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33143 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 43.6 | -13 | 30 | 999 | 2 | 45.6 |  | GENTPF | WSCCST | GGOV1 | EXST1_GE | Closed | 43.6 | 11.2319 | GT | 43 |  | NO | 0 | 1 | 6.6463 | 2.8579 | 0.0615 | 0.154 | 2.5041 | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33151 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 46 | -18.4 | 27.6 | 999 | 2 | 48 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 34.77 | 11.279 | GT | 50 |  | NO | 0 | 0.326 | 4.0998 | 2.0499 | 0.124 | 0.55 | 4.4355 | 12.47 |  | TIDWTR_2_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33151 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 46 | -18.4 | 27.6 | 999 | 2 | 48 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 34.77 | 11.279 | GT | 50 |  | NO | 0 | 0.326 | 4.0998 | 2.0499 | 0.124 | 0.55 | 4.4355 | 12.47 |  | TIDWTR_2_UNITS | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33151 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 35 | -14 | 21 | 999 | 2 | 37 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 26.46 | 11.279 | GT | 40 |  | NO | 0 | 0.428 | 4.1 | 1.64 | 0.124 | 0.55 | 4.4355 | 12.47 |  | TIDWTR_2_UNITS | GT (Gas Turbine) | 3
30 | PG AND E | 470 | Calpine Corp. |  | 33178 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 46 | -15 | 39 | 999 | 4 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Closed | 46 | 2.8574 | JE | 67.5 | PF<0.8 | NO | 0 | 0.19 | 1.21 | 0.81675 | 0.086 | 0.369 | 4.2907 | 13.8 |  | RVRVEW_1_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33250 | 1 | 1 | [14 empty] | Miss Turbine Type | Missing Model |  | Missing Sub R/X |  | 0 | 13.4 | 0 | 0 | 999 | -13.4 | [6 empty] | Closed | 9.38 | 0 | UN | 13.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2192-WD | UN (Unknown) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33460 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 0 | -15 | 40 | 999 | 0 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0 | -15 | SC | 48 | PF<0.8 | NO | 0 | 1 | 1.5583 | 0.74798 | 0.167 | 0.33 | 1.976 | 13.2 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 1.58 | 0.80464 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 1.58 | 0.80464 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 3 | 3 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 1.58 | 0.80464 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 4 | 4 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 1.58 | 0.80464 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 5 | 5 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 1.58 | 0.80464 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 6 | 6 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 1.58 | 0.80464 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 6
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33469 | 7 | 7 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 1.9 | -0.92 | 1.43 | 999 | 0.474 | 2.374 |  | GENROU |  | GGOV1 | REXS | Closed | 1.58 | 0.80464 | IT | 2.374 | PF<0.8 | NO | 0 | 1e-05 | 0.87 | 0.020654 | 0.25 | 0.9 | 3.6 | 4.16 |  | OXMTN_6_LNDFIL | IT (Internal Combustion Turbo Charged) | 7
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33800 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 8.6 | -4.16 | 7.41 | 999 | -8.6 |  |  | GENTPJ |  |  | REXS | Closed | 6.3 | 5.8544 | HY | 14.5 | PF<0.8 | NO | 0 | 1 | 2.233 | 0.32379 | 0.2183 | 0.4419 | 2.0243 | 11 |  | SALTSP_7_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33804 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 0 | -15 | 40 | 999 | 0 |  |  | GENTPF |  |  | EXST1_GE | Open | 0 | 0 | SC | 48 | PF<0.8 | NO | 0 | 1 | 1.5583 | 0.74798 | 0.167 | 0.33 | 1.976 | 13.8 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
30 | PG AND E | 930 | GWF Energy LLC |  | 33805 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 96.14 | -18 | 59.6 | 999 | -1.14 | 95 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 96.1 | 13.7331 | CT | 113.1 |  | NO | 0 | 1e-05 | 6.1 | 6.8991 | 0.073 | 0.395 | 5.411 | 13.8 |  | SCHLTE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 930 | GWF Energy LLC |  | 33807 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 96.14 | -18 | 59.6 | 999 | -1.14 | 95 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 96.1 | 13.7331 | CT | 113.1 |  | NO | 0 | 1e-05 | 6.1 | 6.8991 | 0.073 | 0.395 | 5.411 | 13.8 |  | SCHLTE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 930 | GWF Energy LLC |  | 33811 | 1 | 1 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 103.7 | -58 | 103.7 | 999 | -103.7 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 203.7 | 28.3122 | CA | 196.88 | PF<0.8 | NO | 0 | 1e-05 | 2.3 | 4.5282 | 0.17 | 0.35 | 2.0588 | 18 |  | SCHLTE_1_PL1X3 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33813 | 1 | 1 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Closed | 50 | 2.163 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | KELSO_2_UNITS | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33815 | 2 | 2 | [6 empty] | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Closed | 49.9 | 2.1813 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | KELSO_2_UNITS | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33817 | 3 | 3 | [6 empty] | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Closed | 49.9 | 2.1575 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | KELSO_2_UNITS | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33819 | 4 | 4 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact |  |  | Unreas H | [9 empty] | 26 | 49.9 | -24 | 37.5 | 999 | 0.71 | 50.61 |  | GENTPJ | PSS2A | GGOV1 | EXAC1 | Closed | 50 | 2.1644 | GT | 76.9 | PF<0.8 | NO | 0 | 0.195 | 1.193 | 0.91742 | 0.1207 | 0.5362 | 4.4424 | 13.8 |  | KELSO_2_UNITS | GT (Gas Turbine) | 4
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33820 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 14.081 | -7.59 | 7.59 | 999 | -0.081 | 14 |  | GENTPJ |  | HYGOV | EXDC2A | Closed | 12.74 | 0.8394 | HY | 16 |  | NO | 0 | 0.28 | 3.173 | 0.50768 | 0.3187 | 0.9591 | 3.0094 | 11.5 |  | WESTPT_2_UNIT | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 33822 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 30.7125 | -11.93 | 11.93 | 999 | -1.7125 | 29 |  | GENTPJ |  | HYG3 | ESDC1A | Closed | 21.84 | 2.4124 | HY | 32.5 |  | NO | 0 | 1 | 4.1 | 1.3325 | 0.201 | 0.473 | 2.3532 | 11 |  | TIGRCK_7_UNITS unit 2 | HY (Hydro) | 2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33842 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 18.2 | -9.4 | -9.4 | 999 | -18.2 |  |  | WT2G |  | WT2T | WT2E | Closed | 18.2 | -9.4 | W2 | 23.25 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | FLOWD2_2_FPLWND | W2 (Wind Turbine, Type 2) | 1 |  | PSS Exempt
30 | PG AND E | 3005 | East Bay Municipal Utility Distr |  | 33848 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 9.4 | -1.425 | 3 | 999 | -9.4 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 8.99 | -1.425 | HY | 9 |  | NO | 0 | 1 | 4.64 | 0.4176 | 0.152 | 0.59 | 3.8816 | 7.2 |  | PARDEB_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33868 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 46 | -22.28 | 22.28 | 999 | -46 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 46 | 8.0193 | W3 | 51.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWND2_1_WIND3 | W3 (Wind Turbine, Type 3) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33873 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 85.92 | -41.62 | 41.62 | 999 | -85.92 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 85.92 | 14.8929 | W3 | 95.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWND2_1_WIND1 USWND2_1_WIND2 | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34050 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 10 | 21.236 | -120 | 15 | 999 | 6.764 | 28 |  | GENTPJ |  | GGOV1 | REXS | Closed | 20.66 | 3.9076 | ST | 30.19 | PF<-0.85 | NO | 0 | 0.122 | 3.2 | 0.96608 | 0.2 | 0.6 | 3 | 12.47 |  | ULTPCH_1_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 187 | Sierra Pacific Industries |  | 34055 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 1 | 10.9 | -3.5 | 6.8 | 999 | 1.96 | 12.86 |  | GENTPJ |  | IEEEG1_GE | ESAC7B | Closed | 10.9 | 1.8189 | ST | 12.86 |  | NO | 0 | 0.207 | 2.42 | 0.31121 | 0.235 | 0.763 | 3.2468 | 13.8 |  | SPIFBD_1_PL1X2 | ST (Steam Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34058 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 72.5 | -15 | 17.8 | 999 | 7.5 | 80 |  | GENTPJ | PSS2B | PIDGOV | ESST4B | Closed | 72.07 | -1.613 | HY | 80 |  | NO | 0 | 0.2 | 2.7 | 2.16 | 0.148 | 0.988 | 6.6757 | 13.8 |  | DONNLS_7_UNIT | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 984 | Tri-Dam Project of Oakdale/SJID |  | 34074 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11 | -3.77 | 5.48 | 999 | -11 |  |  | GENTPJ |  |  | ESST4B | Closed | 11 | -0.12389 | HY | 13 |  | NO | 0 | 0.236 | 2.8364 | 0.36873 | 0.0152 | 1.462 | 96.1842 | 6.9 |  | BEARDS_7_UNIT1 hydro | HY (Hydro) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34076 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 8.8 | -6 | 6 | 999 | -8.8 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 8.2 | 4.2793 | HY | 13 | PF<-0.85 | NO | 0 | 1 | 4.64 | 0.6032 | 0.152 | 0.59 | 3.8816 | 6.9 |  | TULLCK_7_UNITS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34076 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0.74 | 6.48 | -3 | 3 | 999 | -6.48 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 6.06 | 3 | HY | 7.2 |  | NO | 0 | 1 | 4.64 | 0.33408 | 0.152 | 0.59 | 3.8816 | 6.9 |  | TULLCK_7_UNITS | HY (Hydro) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34078 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7 | -2.8 | 3.515 | 999 | -7 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 5.18 | 3.515 | HY | 7 |  | NO | 0 | 1 | 4.64 | 0.3248 | 0.152 | 0.59 | 3.8816 | 6 |  | SPRGAP_1_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 139 | Wellhead Electric Co. |  | 34142 | 1 | 1 | [16 empty] | Missing PS |  |  | 35.3 | 50.1 | -17.29 | 23.63 | 999 | 1.3 | 51.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 49.97 | -4.9841 | JE | 63 |  | NO | 0 | 0.18 | 1.91 | 1.2033 | 0.103 | 0.445 | 4.3204 | 13.8 |  | PNOCHE_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34213 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 2.8 | -0.7 | 1.33 | 999 | -2.8 |  |  | GENTPF |  |  | EXST1_GE | Closed | 0.06 | 1.33 | JE | 2.8 |  | NO | 0 | 1 | 4.1117 | 0.11513 | 0.126 | 0.357 | 2.8333 | 12.47 |  | BULLRD_7_SAGNES | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34253 | QF | QF | [5 empty] | At Mvar Limit | [13 empty] | 0 | 2.8 | -0.7 | 1.33 | 999 | -2.8 |  |  | GENTPF |  |  | EXST1_GE | Closed | 1.34 | 1.33 | HY | 2.8 |  | NO | 0 | 1 | 4.1117 | 0.11513 | 0.126 | 0.357 | 2.8333 | 12.47 |  | BORDEN_2_QF | HY (Hydro) | QF
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34265 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 6.1 | -0.2 | 0.2 | 999 | -6.1 |  |  | REGC_A |  |  | REEC_A | Closed | 0.61 | 0 | PV | 6.54 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.3 |  | AVENAL_6_AVPARK 0029-WD SPV | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34301 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [6 empty] | Missing PS |  |  | 15 | 49.6 | -5.6 | 6.24 | 999 | 0.464 | 50.064 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 48.8 | 6.24 | IC | 62.08 |  | NO | 0 | 0.22 | 1 | 0.6208 | 0.08 | 0.3 | 3.75 | 13.8 |  | CHWCHL_1_UNIT | IC (Internal Combustion) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34308 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 154.7 | -10.1 | 10.1 | 999 | -154.7 |  |  | GENQEC | PSS2C | H6E | ST1C | Closed | 99.52 | 10.1 | HY | 155 |  | NO | 0 | 0.19 | 5.1 | 7.905 |  |  | NAN | 13.8 |  | KERKH2_7_UNIT 1 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 32179 | 1 | 1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 78.2 | -30.3 | 30.3 | 999 | -78.2 |  |  | WT4G |  |  | WT4E | Closed | 78.2 | 30.3 | W4 | 78.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BRDSLD_2_MTZUM2 | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34315 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 19.55 | -5.39 | 5.39 | 999 | -19.55 |  |  | REGC_A |  |  | REEC_A | Closed | 1.955 | 5.39 | PV | 20.28 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | ADMEST_6_SOLAR Q0632 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 33102 | 1 | 1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 19.2 | 0.1 | 4.3 | 999 | -19.2 |  |  | WT4G |  |  | WT4E | Closed | 13.44 | 0.1 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 3008 | Panoche Energy Center LLC |  | 34326 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 47 | 108.19 | -67.58 | 81.68 | 999 | -6e-08 | 108.19 |  | GENQEC | PSS2B | GGOV1 | ESAC7B | Closed | 104.25 | -32.367 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 |  |  | NAN | 13.8 |  | PNCHEG_2_PL1X4 | GT (Gas Turbine) | 1
30 | PG AND E | 3008 | Panoche Energy Center LLC |  | 34327 | 2 | 2 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact | [12 empty] | 50 | 104.2 | -67.58 | 81.68 | 999 | 3.99 | 108.19 |  | GENQEC | PSS2B | GGOV1 | ESAC7B | Closed | 108.19 | 9.5433 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 |  |  | NAN | 13.8 |  | PNCHEG_2_PL1X4 ctg2 | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34329 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 22 | 69.9 | -19.7 | 43.26 | 999 | 12.335 | 82.235 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 80 | -6.6964 | JE | 82.235 |  | NO | 0 | 0.227 | 2.67 | 2.1957 | 0.07 | 0.49 | 7 | 13.8 |  | PNCHPP_1_PL1X2 | JE (Jet Engine) | 2
30 | PG AND E | 3008 | Panoche Energy Center LLC |  | 34336 | 3 | 3 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact | [12 empty] | 50 | 104.2 | -67.58 | 81.68 | 999 | 3.99 | 108.19 |  | GENQEC | PSS2B | GGOV1 | ESAC7B | Closed | 108.19 | 9.5433 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 |  |  | NAN | 13.8 |  | PNCHEG_2_PL1X4 ctg3 | GT (Gas Turbine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34314 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.17 | 9.17 | 999 | -20 |  |  | WT4G |  |  | WT4E | Open | 0 | 0 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34340 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 106.9 | -47.2 | 47.2 | 999 | -106.9 |  |  | REGC_A |  |  | REEC_A | Closed | 74.83 | 47.2 | PV | 118 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  | TRNQLT_2_SOLAR spv1 Q0643X | PV (Photovoltaic) | 1
30 | PG AND E | 3008 | Panoche Energy Center LLC |  | 34341 | 4 | 4 |  |  |  |  | Exceed Gen Limit |  | Limit Power Fact | [12 empty] | 50 | 104.2 | -67.58 | 81.68 | 999 | 3.99 | 108.19 |  | GENQEC | PSS2B | GGOV1 | ESAC7B | Closed | 108.19 | 10.8165 | GT | 155.07 | PF<0.8 | NO | 0 | 0.177 | 2.31 | 3.5821 |  |  | NAN | 13.8 |  | PNCHEG_2_PL1X4 ctg4 | GT (Gas Turbine) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34342 | RT | RT | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 13 | 0 | 0 | 999 | -13 | [6 empty] | Open | 0 | 0 | UN | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | INTTRB_6_UNIT | UN (Unknown) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34316 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 11 | 0 | 0 | 999 | -11 |  |  | GENTPJ | PFQRG |  | ESAC1A | Closed | 11 | 0 | HY | 25.2 |  | NO | 0 | 1 | 1.58 | 0.39816 | 0.2 | 0.6 | 3 | 9.11 |  | ONLLPP_6_UNITS | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34339 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 5 | -0.7 | -0.7 | 999 | -5 |  |  | GEWTG |  |  | EXWTGE | Closed | 3 | -0.7 | PV | 5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.5 |  | MENBIO_6_RENEW1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34349 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0078-WD CANTUA_1_SOLAR spv1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34349 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0078-WD CANTUA_1_SOLAR spv2 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 9 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0067-WD SCHNDR_1_WSTSDE spv1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 5 | 0 | 0 | 999 | -5 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0067-WD SCHNDR_1_WSTSDE spv2 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 3 | 3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0066-WD SCHNDR_1_FIVPTS spv1 | PV (Photovoltaic) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34353 | 4 | 4 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 5 | 0 | 0 | 999 | -5 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0066-WD SCHNDR_1_FIVPTS spv2 | PV (Photovoltaic) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34461 | 8 | 8 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 12 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0136-WD GUERNS_6_SOLAR spv1 | PV (Photovoltaic) | 8
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34539 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 54.8 | -18 | 30.4 | 999 | -5.8 | 49 |  | GENROU |  | GGOV1 | EXAC2 | Open | 0 | 0 | JE | 71.2 |  | NO | 0 | 1e-05 | 1.176 | 0.83731 | 0.05 | 0.4 | 8 | 13.8 |  | HENRTA_6_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34541 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS | Missing Sub R/X |  | 0 | 54.8 | -18 | 30.4 | 999 | -5.8 | 49 |  | GENROU |  | GGOV1 | EXAC2 | Closed | 50.52 | -2.258 | JE | 71.2 |  | NO | 0 | 1e-05 | 1.176 | 0.83731 | 0.05 | 0.4 | 8 | 13.8 |  | HENRTA_6_UNITA2 | JE (Jet Engine) | 1
30 | PG AND E | 139 | Wellhead Electric Co. |  | 34553 | RT | RT | [16 empty] | Missing PS |  |  | 0 | 49 | -25.3 | 25.3 | 999 | -49 | [6 empty] | Open | 0 | 0 | OT | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 13.8 |  |  | OT (Other) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34463 | 5 | 5 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 12 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0136-WD GUERNS_6_SOLAR spv2 | PV (Photovoltaic) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34467 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0065-WD GIFFEN_6_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34557 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0074-WD HURON_6_SOLAR spv1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34557 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0074-WD HURON_6_SOLAR spv2 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34603 | ST | ST | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 2.9 | -2 | 2.2 | 999 | 7.1 | 10 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 2.9 | 2.2 | GT | 10 | PF<0.8 | NO | 0 | 1e-05 | 2.7559 | 0.27559 | 0.124 | 0.55 | 4.4355 | 12.47 |  |  | GT (Gas Turbine) | ST
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34608 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 14 | 18.59 | -8.4 | 11.523 | 999 | 3.285 | 21.875 |  | GENTPJ |  | GGOV1 | ESST4B | Closed | 18.59 | -1.014 | JE | 21.875 |  | NO | 0 | 0.176 | 2.28 | 0.49875 | 0.31 | 0.72 | 2.3226 | 13.8 |  | AGRICO_6_PL3N5 unit 3 | JE (Jet Engine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34608 | 4 | 4 |  |  |  |  | Exceed Gen Limit | [14 empty] | 25.4 | 51.9 | -25 | 37.494 | 999 | 6.2e-07 | 51.9 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 51.9 | -1.014 | JE | 71.176 |  | NO | 0 | 0.189 | 1.4 | 0.99646 | 0.12 | 0.33 | 2.75 | 13.8 |  | AGRICO_7_UNIT unit 4 | JE (Jet Engine) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34608 | MB | MB | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  |  |  | 0 | 7.8 | -1 | 7 | 999 | -7.8 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | UN | 12.5 | PF<0.8 | NO | 0 | 1e-05 | 5.06 | 0.6325 | 0.164 | 0.497 | 3.0305 | 13.8 |  | AGRICO_7_UNIT unit 2 | UN (Unknown) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34563 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0079-WD STROUD_6_SOLAR spv1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34563 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0079-WD STROUD_6_SOLAR spv2 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34613 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0075-WD GATES_2_SOLAR spv1 | PV (Photovoltaic) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34616 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 52.04 | -14.12 | 14.12 | 999 | -52.04 |  |  | GENTPJ | PSS2B | H6E | ESST4B | Closed | 52.04 | 14.12 | HY | 54 |  | NO | 0 | 0.172 | 2.88 | 1.5552 | 0.051 | 0.33 | 6.4706 | 13.8 |  | KINGRV_7_UNIT1 hydro | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34613 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0075-WD GATES_2_SOLAR spv2 | PV (Photovoltaic) | 2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 34633 | MB | MB | [16 empty] | Missing PS |  |  | 0 | 4.2 | -1 | 1 | 999 | -4.2 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 9.11 |  | CRNEVL_6_SJQN 3 | HY (Hydro) | MB
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34613 | 3 | 3 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0120-WD GATES_2_WSOLAR | PV (Photovoltaic) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34617 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 102 | -46.7 | 46.7 | 999 | -102 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 112.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | HENRTS_1_SOLAR Q0581 | PV (Photovoltaic) | 1
30 | PG AND E | 960 | Rio Bravo Fresno |  | 34640 | 1 | 1 | [16 empty] | Missing PS |  |  | 16 | 27.5 | -10 | 17.5 | 999 | -6e-07 | 27.5 |  | GENTPJ |  | GGOV1 | ESAC7B | Closed | 26.38 | 11.731 | ST | 32.94 |  | NO | 0 | 0.18 | 3.3 | 1.087 | 0.17 | 0.59 | 3.4706 | 12.47 |  | ULTPFR_1_UNIT 1 | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34644 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 22.5 | -9.426 | 9.426 | 999 | -22.5 |  |  | REGC_A |  |  | REEC_D | Closed | 15.75 | -9.1956 | PV | 22.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | GIFENS_6_BUGSL1 Q0679 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34646 | 1 | 1 | [6 empty] | Limit Power Fact |  |  | Unreas H | [9 empty] | 5 | 40 | -14.9 | 35 | 999 | 10 | 50 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 40 | 12.4272 | CT | 71.176 | PF<0.8 | NO | 0.001 | 0.181 | 1.3 | 0.92529 | 0.11 | 0.37 | 3.3636 | 13.8 |  | SGREGY_6_SANGER | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34646 | 2 | 2 | [5 empty] | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 10.5 | -5.27 | 9.87 | 999 | 2 | 12.5 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 9.62 | 9.87 | CA | 15.625 | PF<0.8 | NO | 0.002 | 0.157 | 4.4 | 0.6875 | 0.105 | 0.409 | 3.8952 | 13.8 |  |  | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34636 | 4 | 4 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 2 | -1.29 | 0 | 999 | -2 |  |  | MOTOR1 |  |  |  | Open | 0 | 0 | HY | 2.381 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 6.6 |  | FRIANT_6_UNITS | HY (Hydro) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34651 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 3.26 | 0 | 0 | 999 | -3.26 | [6 empty] | Closed | 2.282 | 0 | PV | 3.26 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1523-RD spv and existing spv | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34652 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 16.5 | -5.4 | 7.885 | 999 | 1 | 17.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 7.59 | 7.885 | JE | 17 |  | NO | 0 | 1 | 4.1071 | 0.69821 | 0.124 | 0.55 | 4.4355 | 9.11 |  | CHEVCO_6_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34652 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 8.5 | -2 | 3.8 | 999 | 2 | 10.5 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 1.12 | 3.8 | JE | 9 |  | NO | 0 | 1 | 4.1072 | 0.36965 | 0.124 | 0.55 | 4.4355 | 9.11 |  | CHEVCO_6_UNIT 2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34639 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 18 | -5.01 | 9.69 | 999 | -18 |  |  | WT4G |  |  | WT4E | Open | 0 | 0 | PV | 22.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | JAYNE_6_WLSLR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34654 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -10 | 10 | 0 | 0 | 999 | -10 |  |  | REGC_A |  |  | REEC_C | Closed | 10 | 0 | BA | 11.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1296-WD HENRTA_6_HDEBT1 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34666 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20 | -6 | 6 | 999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | 5.4461 | PV | 23.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | KANSAS_6_SOLAR spv Q0637 SGIP | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34668 | 1 | 1 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 999 | -10 | [6 empty] | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2392-WD | PV (Photovoltaic) | 1
30 | PG AND E | 939 | Kings River Conservation Distric |  | 34671 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [7 empty] | Missing Sub R/X |  | 0 | 56 | -17 | 25 | 999 | 4.5 | 60.5 |  | GENQEC | PSS2C | GGOV1 | AC7C | Closed | 48.81 | 25 | JE | 71.18 |  | NO | 0 | 1e-05 | 0.97 | 0.69045 |  |  | NAN | 13.8 |  | MALAGA_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 939 | Kings River Conservation Distric |  | 34672 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | [7 empty] | Missing Sub R/X |  | 0 | 56 | -17 | 25 | 999 | 4.5 | 60.5 |  | GENQEC | PSS2C | GGOV1 | AC7C | Closed | 48.31 | 25 | JE | 71.18 |  | NO | 0 | 1e-05 | 0.97 | 0.69045 |  |  | NAN | 13.8 |  | MALAGA_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34649 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 14 | -7.061 | 7.061 | 999 | -14 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 17.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | Q0965 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34653 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20.2 | -8.72 | 8.72 | 999 | -20.2 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | Q0526 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34673 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20.2 | -8.72 | 8.72 | 999 | -20.2 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | Q0532 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34685 | 2 | 2 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | -77.5 | 77.5 | -33 | 33 | 999 | -77.5 |  |  | REGC_A |  |  | REEC_C | Closed | 31 | 33 | BA | 87.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q0643W | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34677 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 19.8 | -6.1 | 6.1 | 999 | -19.8 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 19.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.405 |  | WAUKNA_1_SOLAR2 Q0558 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34680 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -5.01 | 9.69 | 999 | -20 |  |  | WT4G |  |  | WT4E | Open | 0 | 0 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | KANSAS_6_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34688 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 126.82 | -48.17 | 48.17 | 999 | -126.82 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | P4 | 132.51 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q0272 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34689 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | 0 | 0 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0055-WD OROLOM_1_SOLAR2 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34778 | QF | QF | [5 empty] | At Mvar Limit | [13 empty] | 0 | 17.5 | -6.5 | 9.215 | 999 | -17.5 |  |  | GENTPF |  |  | EXST1_GE | Closed | 2.83 | 9.215 | ST | 17.5 |  | NO | 0 | 1 | 4.1117 | 0.71955 | 0.126 | 0.357 | 2.8333 | 21 |  | FELLOW_7_QFUNTS | ST (Steam Turbine) | QF
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34783 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 12 | -3.6 | 5.5 | 999 | 2 | 14 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 2.29 | -3.6 | GT | 11 |  | NO | 0 | 1 | 4.2819 | 0.47101 | 0.14 | 0.574 | 4.1 | 9.11 |  | TXMCKT_6_UNIT | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34783 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 12 | -3 | 5 | 999 | -12 |  |  | GENTPF |  |  | EXST1_GE | Closed | 2.29 | -3 | GT | 11 |  | NO | 0 | 1 | 4.2819 | 0.47101 | 0.14 | 0.574 | 4.1 | 9.11 |  | TXMCKT_6_UNIT | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34789 | 1 | 1 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 1.6 | 0 | 0 | 999 | -1.6 | [6 empty] | Closed | 1.6 | 0 | GT | 6.68 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34791 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 5.6 | 0 | 0 | 999 | -5.6 | [6 empty] | Closed | 5.6 | 0 | GT | 6.68 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | GT (Gas Turbine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34690 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | 0 | 0 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0094-WD CORCAN_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 34692 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 12 | 0 | 0 | 999 | -12 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 12 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0095-WD CORCAN_1_SOLAR2 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35000 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -2.85 | 2.85 | 999 | -20 |  |  | GEWTG |  |  | EWTGFC | Open | 0 | 0 | PV | 50 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | ATWELL_1_SOLAR | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35022 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20.57 | -6.86 | 6.86 | 999 | -20.57 |  |  | REGC_A |  |  | REEC_A | Closed | 20.57 | 5.9839 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | MARCPW_6_SOLAR1 spv Q0620 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35013 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -6.57 | 9.69 | 999 | -20 |  |  | GEWTG |  |  | EWTGFC | Open | 0 | 0 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | OLIVEP_1_SOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35019 | 1 | 1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 15 | 61.4 | -44.86 | 44.86 | 999 | -61.4 |  |  | WT4G |  |  | WT4E | Closed | 42.98 | -0.3935 | PV | 75 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  | LAMONT_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35029 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 20.9 | 48 | -18 | 29 | 999 | 1.07e-06 | 48 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 48 | 1.2367 | JE | 68.75 |  | NO | 0 | 0.22 | 1.3 | 0.89375 | 0.12 | 0.5 | 4.1667 | 13.8 |  | BDGRCK_1_UNITS | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35027 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 8 | 24.4 | -9.5 | 9.5 | 999 | 2 | 26.4 |  | GENTPJ | PFQRG | GGOV1 | ESAC8B_GE | Closed | 24.4 | 0.49023 | JE | 26.8 |  | NO | 0.001 | 0.156 | 2 | 0.536 | 0.11 | 0.38 | 3.4545 | 13.8 |  | SIERRA_1_UNITS | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35034 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20 | -8.18 | 8.18 | 999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | -2.8764 | PV | 21.78 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.405 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 35037 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 33 | 35.58 | -9.5 | 25.2 | 999 | 12.22 | 47.8 |  | GENTPJ |  | GGOV1 | ESST4B | Closed | 35.58 | 1.2264 | JE | 47.8 |  | NO | 0 | 0.222 | 5.6 | 2.6768 | 0.07 | 0.14 | 2 | 12.47 |  | UNVRSY_1_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35038 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 48 | -15.8 | 24 | 999 | 2 | 50 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 48 | 1.5533 | JE | 49 |  | NO | 0 | 1 | 3.7029 | 1.8144 | 0.126 | 0.357 | 2.8333 | 9.11 |  | CHALK_1_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35040 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 22 | -11 | 14 | 999 | 3 | 25 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Closed | 13.73 | 8.1264 | JE | 34.92 |  | NO | 0 | 0.116 | 2.3788 | 0.83068 | 0.1224 | 0.4172 | 3.4085 | 13.8 |  | KERNRG_1_UNITS | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35042 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20.357 | -6.87 | 6.87 | 999 | -20.357 |  |  | REGC_A |  |  | REEC_A | Closed | 2.035 | -5.2424 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  | PMPJCK_1_SOLAR2 Q0900 SPV | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35046 | 1 | 1 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 27 | -8 | 9.5 | 999 | 2 | 29 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 3.71 | 9.5 | JE | 38 |  | NO | 0 | 1 | 3.7366 | 1.4199 | 0.126 | 0.357 | 2.8333 | 9.11 |  | VEDDER_1_SEKERN | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35047 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 15 | -9.206 | 9.206 | 999 | -15 |  |  | REGC_A |  |  | REEC_D | Closed | 15 | -5.4447 | P4 | 17.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | WLDWD_1_SOLAR2 Q0901 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35048 | RT | RT | [14 empty] | Miss Turbine Type |  | Missing PS |  |  | 0 | 7.5 | -2.375 | 3.8 | 999 | -7.5 | [6 empty] | Open | 0 | 0 | UN | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.47 |  | FRITO_1_LAY | UN (Unknown) | RT
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35052 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 11.6 | -3 | 4.75 | 999 | 2.4 | 14 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 1.63 | 4.75 | GT | 11 |  | NO | 0 | 1 | 3.7273 | 0.41 | 0.126 | 0.357 | 2.8333 | 9.11 |  | CHEVCD_6_UNIT | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35054 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 16.66 | -7.596 | 7.596 | 999 | -16.66 |  |  | REGC_A |  |  | REEC_A | Closed | 16.66 | 7.596 | PV | 18.31 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | LAMONT_1_SOLAR5 spv Q0744 c4 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35056 | 4 | 4 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 0 | 3.3 | -1.4 | 1.8 | 999 | 0.572 | 3.872 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Closed | 3.3 | 1.8 | JE | 3.973 |  | NO | 0 | 0.129 | 0.686 | 0.027255 | 1.161 | 1.566 | 1.3488 | 4.16 |  |  | JE (Jet Engine) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35056 | 5 | 5 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 3.2 | -1.4 | 1.8 | 999 | 0.672 | 3.872 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 3.973 |  | NO | 0 | 0.129 | 0.686 | 0.027255 | 1.161 | 1.566 | 1.3488 | 4.16 |  |  | JE (Jet Engine) | 5
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35056 | 6 | 6 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 3 | -1.4 | 1.8 | 999 | 0.872 | 3.872 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 3.973 |  | NO | 0 | 0.129 | 0.686 | 0.027255 | 1.161 | 1.566 | 1.3488 | 4.16 |  |  | JE (Jet Engine) | 6
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35058 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 48 | -15.9 | 24 | 999 | 2 | 50 |  | GENROU |  | GGOV1 | EXST1_GE | Closed | 48 | 3.0723 | JE | 53 |  | NO | 0 | 1 | 2.9474 | 1.5621 | 0.152 | 0.59 | 3.8816 | 9.11 |  | LIVOAK_1_UNIT 1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35059 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 26.656 | -12.154 | 12.154 | 999 | -26.656 |  |  | REGC_A |  |  | REEC_A | Closed | 26.656 | 11.2238 | PV | 29.296 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | LAMONT_1_SOLAR4 spv Q0744 c4 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35060 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 45.4 | -15 | 22.7 | 999 | 2 | 47.4 |  | GENROU |  | GGOV1 | EXST1_GE | Closed | 45.4 | -2.7833 | GT | 53 |  | NO | 0 | 1 | 2.9474 | 1.5621 | 0.152 | 0.59 | 3.8816 | 9.11 |  | MKTRCK_1_UNIT 1 | GT (Gas Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35062 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 44 | -14.5 | 22 | 999 | 2 | 46 |  | GENROU |  | GGOV1 | EXST1_GE | Closed | 9.14 | 17.3808 | JE | 48 |  | NO | 0 | 1 | 2.9474 | 1.4148 | 0.152 | 0.59 | 3.8816 | 13.8 |  | DISCOV_1_CHEVRN | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35065 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20 | 0 | 0 | 999 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 14 | 0 | PV | 23.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21.6 |  | 0096-WD 7STDRD_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35066 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 32.6 | 48 | -18 | 29 | 999 | 1.07e-06 | 48 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 48 | 9.0019 | JE | 68.75 |  | NO | 0 | 0.142 | 1.3 | 0.89375 | 0.15 | 0.35 | 2.3333 | 13.8 |  | BEARMT_1_UNIT | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35027 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 8 | 24.4 | -9.5 | 9.5 | 999 | 2 | 26.4 |  | GENTPJ | PFQRG | GGOV1 | ESAC8B_GE | Closed | 24.4 | 0.49023 | JE | 26.8 |  | NO | 0.001 | 0.156 | 2 | 0.536 | 0.11 | 0.38 | 3.4545 | 13.8 |  | SIERRA_1_UNITS | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35033 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20.46 | -8.084 | 8.084 | 999 | -20.46 |  |  | REGC_A |  |  | REEC_B | Closed | 14.322 | -2.466 | PV | 20.46 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | LHILLS_6_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35087 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 14.994 | -6.836 | 6.836 | 999 | -14.994 |  |  | REGC_A |  |  | REEC_A | Closed | 14.994 | 6.836 | PV | 16.479 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | LAMONT_1_SOLAR3 spv Q0744 c4 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35082 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -5.01 | 9.69 | 999 | -20 |  |  | WT4G |  |  | WT4E | Closed | 14 | -1.2724 | PV | 23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.44 |  | ARVINN_6_ORION1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35091 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 20.5 | -6.9 | 6.9 | 999 | -20.5 |  |  | REGC_A |  |  | REEC_A | Closed | 14.35 | 3.2473 | PV | 21.84 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | OLDRV1_6_SOLAR Q0517 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35084 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 12 | 0 | 0 | 999 | -12 |  |  | WT4G |  |  | WT4E | Closed | 8.4 | 0 | PV | 15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0032-WD GOOSLK_1_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35095 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 15.47 | -3.5593 | 3.5593 | 999 | -15.47 |  |  | REGC_A |  |  | REEC_A | Closed | 10.829 | 0.34695 | PV | 17.22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.406 |  | MRLSDS_6_SOLAR Q0775 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35098 | 1 | 1 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 20.05 | -12.7 | 12.7 | 999 | -20.05 |  |  | REGC_A |  |  | REEC_A | Closed | 14.035 | -12.1978 | PV | 23.75 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | Q0557 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35302 | RN | RN | [15 empty] | Missing Model |  | Missing Sub R/X |  | -2 | 2.45 | 0 | 0 | 999 | -2.45 | [6 empty] | Closed | 0.98 | 0 | OT | 2.45 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 0937-RD 1301-RD | OT (Other) | RN
30 | PG AND E | 462 | West Coast Energy |  | 35304 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 113.4 | 180.5 | -59.5 | 80.8 | 999 | 21.5 | 202 |  | GENTPJ | PSS2B | GGOV3 |  | Closed | 180.5 | 31.752 | CT | 226 |  | NO | 0.003 | 0.201 | 5.46 | 12.3396 | 0.127 | 0.368 | 2.8976 | 15 |  | RUSCTY_2_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 462 | West Coast Energy |  | 35305 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 110 | 179.2 | -56.1 | 90.4 | 999 | 22.8 | 202 |  | GENTPJ | PSS2B | GGOV3 |  | Closed | 179.2 | 31.6097 | CT | 226 |  | NO | 0.003 | 0.201 | 5.46 | 12.3396 | 0.127 | 0.368 | 2.8976 | 15 |  | RUSCTY_2_UNITS | CT (Combined Cycle Combustion Turbine Part) | 2
30 | PG AND E | 462 | West Coast Energy |  | 35306 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 65 | 250.3 | -83.8 | 123.5 | 999 | -250.3 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 250.3 | 43.2093 | CA | 312.375 |  | NO | 0.003 | 0.21 | 3.49 | 10.9019 | 0.0572 | 0.4604 | 8.049 | 18 |  | RUSCTY_2_UNITS | CA (Combined Cycle Steam Part) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35307 | RN | RN | [15 empty] | Missing Model |  | Missing Sub R/X |  | -2.4 | 2.4 | 0 | 0 | 999 | -2.4 | [6 empty] | Closed | 0.96 | 0 | OT | 2.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1075-RD | OT (Other) | RN
30 | PG AND E | 470 | Calpine Corp. |  | 35851 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 19.9 | 48 | -16 | 25.4 | 999 | 2 | 50 |  | GENROU | IEEEST | GGOV1 | EXAC8B | Closed | 49 | -1.0021 | JE | 71.176 |  | NO | 0.002 | 0.181 | 1.176 | 0.83703 | 0.146 | 0.437 | 2.9932 | 13.8 |  | GILRPP_1_PL1X2 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35853 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 48.1 | -14 | 17.4 | 999 | 1.9 | 50 |  | GENROU | IEEEST | GGOV1 |  | Closed | 48.1 | 11.1383 | JE | 71.176 |  | NO | 0.002 | 0.181 | 1.17 | 0.83276 | 0.069 | 0.526 | 7.6232 | 13.8 |  | GILRPP_1_PL3X4 | JE (Jet Engine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35854 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 30.08 | 47 | -11.82 | 40.29 | 999 | 4.25 | 51.25 |  | GENTPJ | PSS2B | GGOV3 | ESAC8B_GE | Closed | 47 | 12.8253 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35855 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 30.05 | 43.3 | -12.07 | 44.81 | 999 | 7.95 | 51.25 |  | GENTPJ | PSS2B | GGOV3 | ESAC8B_GE | Open | 0 | 0 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35856 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 29.99 | 47.5 | -11.13 | 42.96 | 999 | 3.75 | 51.25 |  | GENTPJ | PSS2B | GGOV3 | ESAC8B_GE | Closed | 47.5 | 14.6907 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35857 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 30.15 | 46.1 | -11.8 | 44.2 | 999 | 5.15 | 51.25 |  | GENTPJ | PSS2B | GGOV3 | ESAC8B_GE | Closed | 46.1 | 14.6543 | CT | 71.176 | PF<0.8 | NO | 0.002 | 0.181 | 1.174 | 0.83561 | 0.112 | 0.461 | 4.1161 | 13.8 |  | LECEF_1_UNITS | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35858 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 7.7 | 113 | -49.2 | 49.9 | 999 | -113 |  |  | GENTPJ | PSS2B |  |  | Closed | 113 | 22.07 | CA | 148.318 |  | NO | 0.003 | 0.14 | 5.41 | 8.024 | 0.112 | 0.231 | 2.0625 | 13.8 |  | LECEF_1_UNITS | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35859 | RN | RN | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 50 | -35.72 | 35.72 | 999 | -50 | [6 empty] | Open | 0 | 0 | GT | 61.45 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 2249-RD | GT (Gas Turbine) | RN
30 | PG AND E | 470 | Calpine Corp. |  | 35860 | 2 | 2 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [6 empty] | Missing Sub R/X |  | 5.4 | 6.9 | -3.55 | 3.2 | 999 | -6.9 |  |  | GENROU |  |  | ESAC1A | Closed | 6.9 | 3.2 | CA | 9.5 |  | NO | 0 | 1e-05 | 2.5 | 0.2375 | 0.24 | 0.675 | 2.8125 | 13.8 |  | CALPIN_1_AGNEW | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35861 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact |  |  | Unreas H | [9 empty] | 0 | 8.4 | -6.3 | 6.3 | 999 | 1.1e-07 | 8.4 |  | GENROU |  | GGOV1 | REXS | Closed | 6.5 | 6.3 | GT | 10.5 | PF<0.8 | NO | 0 | 0.218 | 0.7097 | 0.074519 | 0.05 | 0.3 | 6 | 4.16 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 35871 | 2 | 2 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [5 empty] | Missing PS |  |  | 27.8 | 27.8 | -10.8 | 23.4 | 999 | -27.8 |  |  | GENROU |  |  | REXS | Closed | 27.8 | -1.7851 | CA | 42.4 | PF<0.8 | NO | 0 | 0.17 | 3.7 | 1.5688 | 0.059 | 0.169 | 2.8644 | 13.8 |  | GILROY_1_UNIT | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 470 | Calpine Corp. |  | 36202 | 2 | 2 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 19.6 | 38.5 | -14.2 | 17.2 | 999 | -38.5 |  |  | GENTPJ |  |  | REXS | Closed | 37.2 | 0.54663 | CA | 42.4 |  | NO | 0 | 0.138 | 4 | 1.696 | 0.29 | 0.598 | 2.0621 | 13.8 |  | BASICE_2_UNITS | CA (Combined Cycle Steam Part) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36204 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 3.2 | -0.3 | 0.7 | 999 | -3.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 3 | 0.2 | W3 | 3.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36204 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 3.2 | -0.3 | 0.7 | 999 | -3.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 3 | 0.2 | W3 | 3.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12 |  |  | W3 (Wind Turbine, Type 3) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36207 | 1 | 1 | [9 empty] | Unreas H | [7 empty] | Missing Sub R/X |  | 0 | 60.5 | -22.2 | 37.5 | 999 | -10.5 | 50 |  | GENTPJ | IEEEST | GGOV1 | ESAC8B_GE | Closed | 44.6 | 11.5856 | JE | 71.176 |  | NO | 0 | 1e-05 | 1.17 | 0.83276 | 0.163 | 0.403 | 2.4724 | 13.8 |  | KNGCTY_6_UNITA1 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36212 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 19.3 | -6.68 | 6.68 | 999 | -19.3 |  |  | REGC_A |  |  | REEC_A | Closed | 13.51 | 6.68 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | FRNTBW_6_SOLAR1 Q0705 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36220 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 19.91 | -7.98 | 7.98 | 999 | -19.91 |  |  | REGC_A |  |  | REEC_D | Closed | 1.991 | -3.4297 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.38 |  | Q0972 SPV c6 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36222 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 166.28 | -45 | 90 | 999 | 5.22 | 171.5 |  | GENTPJ | PSS2A | GGOV1 | ESST4B | Closed | 166.28 | 25.7736 | CT | 207.8 |  | NO | 0 | 0.18 | 5.36 | 11.1381 | 0.077 | 0.267 | 3.4675 | 18 |  | MOSSLD_2_PSP1 CTG2 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36223 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 192.2 | -70 | 90 | 999 | -192.2 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 192.2 | 37.2142 | CA | 233 |  | NO | 0 | 0.196 | 4.78 | 11.1374 | 0.061 | 0.572 | 9.377 | 18 |  | MOSSLD_2_PSP1 STG1 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36226 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 192.14 | -70 | 90 | 999 | -192.14 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 192.14 | 33.095 | CA | 233 |  | NO | 0 | 0.196 | 4.78 | 11.1374 | 0.061 | 0.572 | 9.377 | 18 |  | MOSSLD_2_PSP2 STG2 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36232 | RE | RE | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | 0 | 0 | 999 | -10 | [6 empty] | Closed | 7 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21.6 |  | 1862-RD | PV (Photovoltaic) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36430 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 229.5 | -95.12 | 95.12 | 999 | -229.5 |  |  | REGC_A |  |  | REEC_A | Closed | 160.65 | 12.6598 | PV | 275.04 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.324 |  | TOPAZ_2_SOLAR unit A1 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36432 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 26.44 | -10.96 | 10.96 | 999 | -26.44 |  |  | REGC_A |  |  | REEC_A | Closed | 18.508 | 10.96 | PV | 34.32 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit A2 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36434 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 38.45 | -15.94 | 15.94 | 999 | -38.45 |  |  | REGC_A |  |  | REEC_A | Closed | 26.915 | 9.7112 | PV | 46.08 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.324 |  | TOPAZ_2_SOLAR unit B1 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36436 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 73.3 | -30.4 | 30.4 | 999 | -73.3 |  |  | REGC_A |  |  | REEC_A | Closed | 51.31 | 9.711 | PV | 95.16 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit B2 | PV (Photovoltaic) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36439 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 195 | -76.6 | 76.6 | 999 | -195 |  |  | REGC_A |  |  | REEC_A | Closed | 136.5 | -1.5272 | PV | 209.76 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.342 |  | CAVLSR_2_RSOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36440 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 6.5 | -2.55 | 2.55 | 999 | -6.5 |  |  | REGC_A |  |  | REEC_A | Closed | 4.55 | -1.5273 | PV | 7 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.27 |  | CAVLSR_2_RSOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 36441 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 38.2 | -15 | 15 | 999 | -38.2 |  |  | REGC_A |  |  | REEC_A | Closed | 26.74 | -1.5273 | PV | 41.04 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.342 |  | CAVLSR_2_BSOLAR | PV (Photovoltaic) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 36863 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 23 | 50 | -9.3 | 40 | 999 | 5 | 55 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 49.6 | -0.7811 | CT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.38 | 0.98223 | 0.081 | 0.271 | 3.3457 | 13.8 |  | DUANE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 36864 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 23 | 50 | -9.3 | 40 | 999 | 5 | 55 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 47.6 | -1.0399 | CT | 71.176 | PF<0.8 | NO | 0 | 0.181 | 1.38 | 0.98223 | 0.081 | 0.271 | 3.3457 | 13.8 |  | DUANE_1_PL1X3 | CT (Combined Cycle Combustion Turbine Part) | 1
30 | PG AND E | 394 | Silicon Valley Power |  | 36865 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 8 | 47.79 | -15 | 36 | 999 | -47.79 |  |  | GENTPJ | PSS2A |  | ESAC7B | Closed | 45.8 | -1.0729 | CA | 63.059 | PF<0.8 | NO | 0 | 0.12 | 6.01 | 3.7898 | 0.079 | 0.265 | 3.3544 | 13.8 |  | DUANE_1_PL1X3 | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 3003 | Lassen Municipality Utility Dist |  | 36912 | 2 | 2 | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 7.5 | -2.46 | 2.46 | 999 | -7.5 |  |  | REGC_A |  |  | REEC_A | Closed | 7.497 | 1.5374 | UN | 7.9 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | UN (Unknown) | 2
30 | PG AND E | 3003 | Lassen Municipality Utility Dist |  | 36938 | 1 | 1 | [5 empty] | At Mvar Limit | [10 empty] | Missing PS |  |  | 0 | 30 | -6 | 6 | 999 | 2 | 32 |  | GENTPF |  | GGOV1 | EXST1_GE | Closed | 26.4 | 6 | ST | 30 |  | NO | 0 | 1 | 2.7447 | 0.82341 | 0.126 | 0.357 | 2.8333 | 9.11 |  |  | ST (Steam Turbine) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37150 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 160 | -16 | 16 | 888 | -160 |  |  | REGC_A |  |  | REEC_A | Closed | 112 | 16 | PV | 171.8261 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37302 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 77 | -13 | 12 | 888 | 1.91e-06 | 77 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 15 | -12.0044 | HY | 77 |  | NO | 0.002 | 0.284 | 2.7 | 2.079 | 0.13 | 0.23 | 1.7692 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37305 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 76.5 | -11 | 10 | 888 | 1.43e-06 | 76.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 66 | -11 | HY | 76.5 |  | NO | 0.004 | 0.216 | 2.304 | 1.7626 | 0.24 | 0.5 | 2.0833 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37306 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 76.5 | -10 | 20 | 888 | 1.43e-06 | 76.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 66 | -10 | HY | 76.5 |  | NO | 0.004 | 0.216 | 2.304 | 1.7626 | 0.24 | 0.5 | 2.0833 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37307 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 10.5 | -0.6 | 2.3 | 888 | -10.5 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 10 | -0.6 | HY | 10.5 |  | NO | 0.003 | 0.25 | 3.24 | 0.3402 | 0.17 | 0.25 | 1.4706 | 4.16 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37308 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 78 | -8.5 | 24.9 | 888 | 5.5 | 83.5 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 25 | -7.3202 | HY | 78 |  | NO | 0.003 | 0.284 | 3.4 | 2.652 | 0.22 | 0.42 | 1.9091 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37313 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 50 | -14.2 | 37.5 | 888 | 10.5 | 60.5 |  | GENQEC | PSS2C | GGOV1 | AC7C | Closed | 47 | 20.2654 | JE | 71.18 |  | NO | 0 | 0.181 | 1.37 | 0.97517 |  |  | NAN | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37314 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 26.8 | -3.1 | 4.1 | 888 | 2.9 | 29.7 |  | GENTPJ |  | HYG3 | ESST1A_GE | Closed | 20 | -0.90518 | HY | 29.7 |  | NO | 0.003 | 0.25 | 1.692 | 0.50252 | 0.24 | 0.49 | 2.0417 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37315 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 48 | -4.8 | 31.6 | 888 | -8 | 40 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 40 | 9.7829 | CT | 60 |  | NO | 0 | 0.13 | 2.42 | 1.452 | 0.04 | 0.15 | 3.75 | 13.8 |  |  | CT (Combined Cycle Combustion Turbine Part) | 1 |  | PSS Exempt
30 | PG AND E | 363 | Sacramento Utility District |  | 37316 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 42.5 | -3.7 | 31.6 | 888 | -2.5 | 40 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 40 | 10.3762 | JE | 52.5 |  | NO | 0 | 0.13 | 2.42 | 1.2705 | 0.04 | 0.15 | 3.75 | 13.8 |  |  | JE (Jet Engine) | 1 |  | PSS Exempt
30 | PG AND E | 363 | Sacramento Utility District |  | 37317 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 46.7 | -5.7 | 12.2 | 888 | -7.6e-07 | 46.7 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 44 | 6.3213 | HY | 46.7 |  | NO | 0.002 | 0.227 | 1.869 | 0.87282 | 0.25 | 0.55 | 2.2 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 363 | Sacramento Utility District |  | 37318 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 116 | -28 | 51 | 888 | 24 | 140 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 108 | 28.0987 | HY | 140 |  | NO | 0.002 | 0.22 | 2.151 | 3.0114 | 0.17 | 0.31 | 1.8235 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 363 | Sacramento Utility District |  | 37319 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 134.3 | -20 | 48 | 888 | 5.7 | 140 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 108 | 28.2328 | HY | 140 |  | NO | 0.002 | 0.22 | 2.151 | 3.0114 | 0.17 | 0.31 | 1.8235 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 395 | OWNER395 |  | 37320 | 1 | 1 | [18 empty] | No Owner | 0 | 26 | -10 | 15 | 888 | 3 | 29 |  | GENTPF |  | GGOV1 | EXAC1 | Closed | 25 | -1.0279 | JE | 27 |  | NO | 0.011 | 0.196 | 2.778 | 0.75006 | 0.14 | 0.43 | 3.0714 | 12.5 |  |  | JE (Jet Engine) | 1 |  | PSS Exempt
30 | PG AND E | 363 | Sacramento Utility District |  | 37321 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 207 | -50 | 90 | 888 | -207 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 230 | 28.0339 | CA | 228 |  | NO | 0 | 0.201 | 6.58 | 15.0024 | 0.073 | 0.25 | 3.4247 | 16.5 |  |  | CA (Combined Cycle Steam Part) | 1
30 | PG AND E | 470 | Calpine Corp. |  | 37523 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 175 | -20 | 108.5 | 888 | -175 |  |  | GENTPJ | PSS2B |  | ESST6B | Closed | 100 | -11.9449 | CC | 250 |  | NO | 0 | 0.201 | 3.95 | 9.875 | 0.063 | 0.16 | 2.5397 | 18 |  | SUTTER_2_PL1X3 | CC (Combined Cycle Generic) | 3
30 | PG AND E | 313 | City of Redding |  | 37530 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 5 | -3 | 3 | 888 | -5 | [6 empty] | Open | 0 | 0 | HY | 100 |  | NO | 0.006 | 0.224 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37549 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 69 | -30 | 22 | 888 | 1 | 70 |  | GENTPJ | PSS2A | HYGOVR | ST6C | Closed | 39.1 | 22 | HY | 71.9 |  | NO | 0.003 | 0.34 | 3.69 | 2.6531 | 0.1335 | 0.46 | 3.4457 | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37561 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 166.7 | -60 | 60 | 888 | 23.3 | 190 |  | GENQEC | PSS2C | HYGOVR | ST4C | Closed | 65.7 | 12.4353 | HY | 166.67 |  | NO | 0.503 | 0.25 | 3.8 | 6.3335 |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
30 | PG AND E | 50 | US Bur Reclam |  | 37562 | 2 | 2 | [8 empty] | RX Ratio | [10 empty] | 0 | 166.7 | -60 | 60 | 888 | 23.3 | 190 |  | GENQEC | PSS2C | HYGOVR | ST4C | Closed | 150 | 12.6473 | HY | 166.67 |  | NO | 0.503 | 0.25 | 3.8 | 6.3335 |  |  | NAN | 13.8 |  |  | HY (Hydro) | 2
30 | PG AND E | 50 | US Bur Reclam |  | 37577 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 142 | -50 | 50 | 888 | 2 | 144 |  | GENTPJ | PSS2B | HYGOVR | ESST6B | Closed | 120 | -0.35899 | HY | 142 |  | NO | 0.003 | 0.27 | 2.77 | 3.9334 | 0.2 | 0.69 | 3.45 | 13.8 |  |  | HY (Hydro) | 3
30 | PG AND E | 50 | US Bur Reclam |  | 37578 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 142 | -50 | 50 | 888 | 2 | 144 |  | GENTPJ | PSS2B | HYGOVR | ESST6B | Closed | 125 | 0.12549 | HY | 142 |  | NO | 0.003 | 0.27 | 2.77 | 3.9334 | 0.2 | 0.69 | 3.45 | 13.8 |  |  | HY (Hydro) | 4
30 | PG AND E | 313 | City of Redding |  | 37942 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 13 | 23 | -11.5 | 10.9 | 888 | 2.4 | 25.4 |  | GENROU | PSS2B | TGOV1 | ESAC8B_GE | Closed | 15.03 | 3.5053 | JE | 31.04 |  | NO | 0 | 1e-05 | 6.2 | 1.9245 | 0.166 | 0.625 | 3.7651 | 13.8 |  | REDGPW_13.8_CT3 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37944 | 1 | 1 | [16 empty] | Missing PS | Missing Sub R/X |  | 11 | 27 | -0.9 | 14.9 | 888 | 1.5 | 28.5 |  | GENROU |  | TGOV1 | ESAC5A | Closed | 22 | 4.0101 | JE | 31.5 |  | NO | 0 | 1e-05 | 5.7 | 1.7955 | 0.098 | 0.3124 | 3.1878 | 13.8 |  | REDGPW_13.8_ST1 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37958 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 22 | 39 | -3.8 | 18.2 | 888 | 4.5 | 43.5 |  | GENROU | PSS2B | TGOV1 | ESAC1A | Closed | 36.9 | 6.9217 | JE | 50 |  | NO | 0 | 1e-05 | 8 | 4 | 0.0965 | 0.233 | 2.4145 | 13.8 |  | REDGPW_13.8_CT4 | JE (Jet Engine) | 1
30 | PG AND E | 313 | City of Redding |  | 37963 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 22 | 40 | -7.8 | 18 | 888 | 4.8 | 44.8 |  | GENROU | PSS2B | TGOV1 | ESAC1A | Closed | 36.9 | 6.9102 | JE | 50 |  | NO | 0 | 1e-05 | 6 | 3 | 0.0965 | 0.233 | 2.4145 | 13.8 |  | REDGPW_13.8_CT5 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38020 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 2.5 | -0.61 | 1.22 | 999 | 0.28 | 2.78 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 1.8 | 0.305 | HY | 2.78 |  | NO | 0 | 1e-05 | 3 | 0.0834 | 0.15 | 0.45 | 3 | 115 |  |  | HY (Hydro) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35089 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 20 | -9.59 | 9.59 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Closed | 14 | -3.4768 | PV | 22.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | SKERN_6_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 361 | City of Roseville |  | 38071 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 50 | -10 | 20 | 888 | 15 | 65 |  | GENROU | PSS2A | GGOV1 | EXST4B | Closed | 47.5 | 7.6282 | JE | 65 |  | NO | 0 | 1e-05 | 6.5 | 4.225 | 0.05 | 0.3 | 6 | 13.8 |  | FDYMNT_13.8_CT1 | JE (Jet Engine) | 1
30 | PG AND E | 361 | City of Roseville |  | 38079 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 50 | -10 | 20 | 888 | 15 | 65 |  | GENROU | PSS2A | GGOV1 | EXST4B | Closed | 47.5 | 7.6282 | JE | 65 |  | NO | 0 | 1e-05 | 6.5 | 4.225 | 0.05 | 0.3 | 6 | 13.8 |  | FDYMNT_13.8_CT2 | JE (Jet Engine) | 2
30 | PG AND E | 361 | City of Roseville |  | 38080 | 3 | 3 | [17 empty] | Missing Sub R/X |  | 0 | 70 | -29.4 | 35 | 888 | -70 |  |  | GENROU | PSS2A |  | EXST4B | Closed | 70 | 12.304 | JE | 65 |  | NO | 0 | 1e-05 | 4.5 | 2.925 | 0.05 | 0.3 | 6 | 13.8 |  | FDYMNT_13.8_STG | JE (Jet Engine) | 3
30 | PG AND E | 361 | City of Roseville |  | 38091 | 4 | 4 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  | Missing Sub R/X |  | 0 | 37 | -18.5 | 33 | 888 | -7 | 30 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 22.5 | 5.4606 | UN | 30 | PF<0.8 | NO | 0 | 1e-05 | 2.05 | 0.615 | 0.134 | 0.39 | 2.9104 | 13.8 |  |  | UN (Unknown) | 4
30 | PG AND E | 361 | City of Roseville |  | 38091 | 5 | 5 | [6 empty] | Limit Power Fact | [7 empty] | Miss Turbine Type |  |  | Missing Sub R/X |  | 0 | 37 | -18.5 | 33 | 888 | -7 | 30 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 22.5 | 5.4606 | UN | 30 | PF<0.8 | NO | 0 | 1e-05 | 2.05 | 0.615 | 0.134 | 0.39 | 2.9104 | 13.8 |  |  | UN (Unknown) | 5
30 | PG AND E | 392 | Northern California Power Agency |  | 38106 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 33.5 | -14.7 | 38.5 | 999 | -33.5 |  |  | GENROU | PSS2B |  | ESAC7B | Closed | 23.4 | 2.73 | ST | 64 | PF<0.8 | NO | 0 | 0.165 | 5.8 | 3.712 | 0.192 | 0.604 | 3.1458 | 13.8 |  | NCPA_7_GP1UN1 | ST (Steam Turbine) | 1
30 | PG AND E | 392 | Northern California Power Agency |  | 38108 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 30.5 | -14 | 39.5 | 999 | -30.5 |  |  | GENROU | PSS2B |  | ESAC7B | Closed | 21.4 | 2.6036 | ST | 64 | PF<0.8 | NO | 0 | 0.165 | 5.8 | 3.712 | 0.192 | 0.604 | 3.1458 | 13.8 |  | NCPA_7_GP1UN2 | ST (Steam Turbine) | 1
30 | PG AND E | 361 | City of Roseville |  | 38116 | 1 | 1 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 37 | -18.5 | 33 | 888 | -12.3 | 24.7 |  | GENROU |  | GGOV1 | EXST4B | Closed | 22.5 | 14.5227 | JE | 28.4 | PF<0.8 | NO | 0 | 1e-05 | 8.77 | 2.4907 | 0.101 | 0.277 | 2.7426 | 13.8 |  | ROSVIL_13.8_GT1 | JE (Jet Engine) | 1
30 | PG AND E | 361 | City of Roseville |  | 38117 | 1 | 1 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 37 | -18.5 | 33 | 888 | -12.3 | 24.7 |  | GENROU |  | GGOV1 | EXST4B | Closed | 22.5 | 14.5227 | JE | 28.4 | PF<0.8 | NO | 0 | 1e-05 | 8.77 | 2.4907 | 0.101 | 0.277 | 2.7426 | 13.8 |  | ROSVIL_13.8_GT2 | JE (Jet Engine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38134 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 0.4 | 0 | 0 | 999 | -2e-08 | 0.4 |  | GENTPJ |  | HYG3 |  | Closed | 0.17 | 0 | HY | 0.4 |  | NO | 0 | 1e-05 | 3 | 0.012 | 0.15 | 0.45 | 3 | 69 |  |  | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38150 | 1 | 1 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 3.35 | -1.2 | 2.45 | 999 | -3.35 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.34 | -0.42406 | IT | 4.06 |  | NO | 0 | 1e-05 | 1.47 | 0.059682 | 0.01 | 0.001 | 0.1 | 4.16 |  |  | IT (Internal Combustion Turbo Charged) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38150 | 2 | 2 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 3.35 | -1.2 | 2.45 | 999 | -3.35 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.34 | -0.42406 | IT | 4.06 |  | NO | 0 | 1e-05 | 1.47 | 0.059682 | 0.01 | 0.001 | 0.1 | 4.16 |  |  | IT (Internal Combustion Turbo Charged) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 35092 | 4 | 4 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20.377 | -4.173 | 4.173 | 999 | -20.377 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | Q0744 | PV (Photovoltaic) | 4
30 | PG AND E | 1 | No owner defined |  | 38330 | 1 | 1 | [6 empty] | Limit Power Fact |  |  | Unreas H | Unreas Sat |  |  |  | Miss Turbine Type |  | Missing PS |  | No Owner | 0 | 49.2 | -24.6 | 36.9 | 888 | -49.2 |  |  | GENTPJ |  |  | ESAC8B_GE | Open | 0 | 0 | UN | 61.5 | PF<0.8 | NO | 0 | 1e-05 | 1.267 | 0.7792 | 0.07 | 0.18 | 2.5714 | 0.48 |  |  | UN (Unknown) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38351 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 20 | 48 | -20 | 56.5 | 888 | 3 | 51 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 71.176 | PF<0.8 | YES | 0 | 1e-05 | 1.258 | 0.89539 | 0.295 | 0.792 | 2.6847 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38353 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [6 empty] | Missing Sub R/X |  | 20 | 46 | -20 | 50.5 | 888 | 5 | 51 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 35 | 1.9442 | JE | 71.176 | PF<0.8 | YES | 0 | 1e-05 | 1.258 | 0.89539 | 0.295 | 0.792 | 2.6847 | 13.8 |  |  | JE (Jet Engine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38356 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 30 | 45 | -20 | 22 | 888 | 11.7 | 56.7 |  | GENROU |  | GGOV1 | ESAC1A | Closed | 43 | -4.7321 | GT | 56.7 |  | YES | 0 | 0.472 | 1.285 | 0.72859 | 0.223 | 0.41 | 1.8386 | 13.8 |  |  | GT (Gas Turbine) | 1 |  | PSS Exempt
30 | PG AND E | 334 | Modesto Irrigation District |  | 38357 | 1 | 1 | [9 empty] | Unreas H | [7 empty] | Missing Sub R/X |  | 25 | 48 | -26.1667 | 28.1667 | 888 | 2 | 50 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 48 | -3.2669 | GT | 71.176 |  | YES | 0 | 1e-05 | 1.17 | 0.83276 | 0.1207 | 0.4943 | 4.0953 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38357 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 25 | -38.0408 | 33.7535 | 888 | -25 |  |  | GENTPJ | PSS2A |  | ESAC8B_GE | Closed | 8 | -3.2669 | GT | 44.388 | PF<0.8 | YES | 0 | 1e-05 | 3.9 | 1.7311 | 0.075 | 0.267 | 3.56 | 13.8 |  |  | GT (Gas Turbine) | 2
30 | PG AND E | 334 | Modesto Irrigation District |  | 38370 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.365 | 6.165 | 888 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.33 | -3.365 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38371 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.365 | 6.165 | 888 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.33 | -3.365 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38372 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.365 | 6.165 | 888 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.33 | -3.365 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38373 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.365 | 6.165 | 888 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.33 | -3.365 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38374 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.365 | 6.165 | 888 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.33 | -3.365 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38375 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5 | 8.2 | -3.365 | 6.165 | 888 | 2.349 | 10.549 |  | GENTPJ | PSS2B | GGOV1 | ESAC8B_GE | Closed | 6.33 | -3.365 | GT | 10.549 | PF<0.8 | YES | 0 | 1e-05 | 1.015 | 0.10707 | 0.08 | 0.3 | 3.75 | 13.8 |  |  | GT (Gas Turbine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38544 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 15 | 54 | 0 | 20 | 337 | 0.2 | 54.2 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 45 | 9.0096 | JE | 76.94 |  | NO | 0 | 1e-05 | 1.341 | 1.0318 | 0.1092 | 0.479 | 4.3864 | 13.8 |  | ALMOND2 UNIT 2 | JE (Jet Engine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38545 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 15 | 54 | 0 | 20 | 337 | 0.2 | 54.2 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 45 | 9.3134 | JE | 76.94 |  | NO | 0 | 1e-05 | 1.341 | 1.0318 | 0.1092 | 0.479 | 4.3864 | 13.8 |  | ALMOND2 UNIT 3 | JE (Jet Engine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38546 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 15 | 54 | 0 | 20 | 337 | 0.2 | 54.2 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 45 | 9.3631 | JE | 76.94 |  | NO | 0 | 1e-05 | 1.341 | 1.0318 | 0.1092 | 0.479 | 4.3864 | 13.8 |  | ALMOND2 UNIT 4 | JE (Jet Engine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38554 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 8 | 38.2 | 0 | 17.1 | 337 | 7e-08 | 38.2 |  | GENTPJ |  | HYG3 | ESST1A_GE | Closed | 30 | 1.136 | HY | 38.2 |  | YES | 0 | 1.072 | 3 | 1.146 | 0.205 | 0.369 | 1.8 | 13.8 |  | DON PEDRO UNIT 4 | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 337 | Turlock Irrigation District |  | 38570 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 40 | 82.3 | 0 | 40 | 337 | 1.7 | 84 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 79.5 | 29.7938 | GT | 111.6 |  | YES | 0 | 1e-05 | 5.607 | 6.2574 | 0.08 | 0.3 | 3.75 | 13.8 |  | WEC PWR PLNT UNIT 1 | GT (Gas Turbine) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38572 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 25 | 93.6 | 0 | 60 | 337 | -93.6 |  |  | GENROU | PSS2A |  | ESST4B | Closed | 91 | 30.9244 | CC | 130.3 |  | YES | 0 | 1e-05 | 3.93 | 5.1208 | 0.0806 | 0.357 | 4.4293 | 13.8 |  | WEC PWR PLNT UNIT 3 | CC (Combined Cycle Generic) | 1
30 | PG AND E | 337 | Turlock Irrigation District |  | 38574 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 40 | 82.3 | 0 | 40 | 337 | 1.7 | 84 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Closed | 79.5 | 28.1659 | GT | 111.6 |  | YES | 0 | 1e-05 | 5.607 | 6.2574 | 0.08 | 0.3 | 3.75 | 13.8 |  | WEC PWR PLNT UNIT 2 | GT (Gas Turbine) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 38700 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 32 | -10.71 | 10.71 | 999 | 2.316 | 34.316 |  | GENTPJ | PSS2B | HYG3 | ESAC6A | Closed | 32 | 10.71 | HY | 34.316 |  | NO | 0.003 | 0.34 | 2.4 | 0.82358 | 0.208 | 0.458 | 2.2019 | 13.8 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38760 | 10 | 10 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 10 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38760 | 11 | 11 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 11 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38765 | 8 | 8 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 8 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38765 | 9 | 9 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 9 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38770 | 6 | 6 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 6 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38770 | 7 | 7 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 7 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -6.54 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 6 |  | NO | 0 | 1 | 1.7167 | 0.103 | 0.5 | 0.67 | 1.34 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -6.54 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 6 |  | NO | 0 | 1 | 1.7167 | 0.103 | 0.5 | 0.67 | 1.34 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -6.54 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 6 |  | NO | 0 | 1 | 1.7167 | 0.103 | 0.5 | 0.67 | 1.34 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 5 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38775 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 6 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38780 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -13.07 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -12.428 | 0 | MP | 13 |  | NO | 0 | 1 | 1.4154 | 0.184 | 0.27 | 0.67 | 2.4815 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -7.69 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 7 |  | NO | 0 | 1 | 1.8286 | 0.128 | 0.455 | 0.818 | 1.7978 | 13.2 |  |  | MP (Motor/Pump) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -7.69 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 7 |  | NO | 0 | 1 | 1.8286 | 0.128 | 0.455 | 0.818 | 1.7978 | 13.2 |  |  | MP (Motor/Pump) | 2
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -7.69 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 7 |  | NO | 0 | 1 | 1.8286 | 0.128 | 0.455 | 0.818 | 1.7978 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.5 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38785 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.5 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 5 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.5 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.5 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.5 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38790 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | -15.38 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -14.5 | 0 | MP | 15 |  | NO | 0 | 1 | 1.18 | 0.177 | 0.242 | 0.69 | 2.8512 | 13.2 |  |  | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38795 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -16.92 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -16.4 | 0 | MP | 16 |  | NO | 0 | 1 | 1.9062 | 0.30499 | 0.321 | 0.64 | 1.9938 | 13.2 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38795 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -16.92 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 16 |  | NO | 0 | 1 | 1.9062 | 0.30499 | 0.321 | 0.64 | 1.9938 | 13.2 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38795 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -16.92 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 16 |  | NO | 0 | 1 | 1.9062 | 0.30499 | 0.321 | 0.64 | 1.9938 | 13.2 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38815 | 4 | 4 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 4 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38815 | 5 | 5 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Closed | -27.125 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 5 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38820 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -8.9 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 9 |  | NO | 0 | 1e-05 | 1.7689 | 0.1592 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 1
30 | PG AND E | 362 | Department of Water Resources |  | 38820 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | -8.9 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 9 |  | NO | 0 | 1e-05 | 1.7689 | 0.1592 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 2
30 | PG AND E | 362 | Department of Water Resources |  | 38820 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | -29.4 | 0 | 0 | 0 | 999 | 0 |  |  | GENTPF |  |  | EXDC1 | Open | 0 | 0 | MP | 28 |  | NO | 0 | 1e-05 | 1.7064 | 0.47779 | 1.167 | 0.949 | 0.8132 | 13.2 |  | BANKPP_2_NSPIN | MP (Motor/Pump) | 3 |  | PSS Exempt
30 | PG AND E | 362 | Department of Water Resources |  | 38835 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 123.157 | -34 | 38 | 999 | -5.4e-07 | 123.157 |  | GENTPJ | PSS2A | HYG3 | EXDC1 | Closed | 106.816 | 38 | HY | 123.157 |  | NO | 0.002 | 0.18 | 3.6 | 4.4337 | 0.164 | 0.379 | 2.311 | 12.5 |  | HYTTHM_2_UNITS | HY (Hydro) | 1 |  | PSS Exempt
30 | PG AND E | 394 | Silicon Valley Power |  | 38921 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [5 empty] | Gen on HV |  | Miss Turbine Type | Missing Model | Missing PS | Missing Sub R/X |  | 0 | 50 | -31.57 | 31.57 | 999 | -50 | [6 empty] | Closed | 50 | 31.57 | UN | 50 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 60 |  | BESS_SVP | UN (Unknown) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38950 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -418 | 0 | 0.01765 | 0.01765 | 999 | 0 | [6 empty] | Closed | -413.7203 | 0.01765 | DC | 400 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 180.5 | BES Exempt |  | DC (Represents DC ties) | 1 | Netting Exempt | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 39185 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -13.15 | 13.15 | -9.9 | 9.9 | 999 | -13.15 |  |  | REGC_A |  |  | REEC_C | Closed | 9.205 | -9.9 | BA | 16.5 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 39233 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 78.2 | -38.2 | 38.2 | 999 | -78.2 |  |  | REGC_A |  |  | REEC_A | Closed | 78.2 | 14.4313 | W4 | 87.04 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWPJR_UNITS wind | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 39346 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | -313.5 | 306.8 | -103 | 103 | 999 | -306.8 |  |  | REGC_A |  |  | REEC_C | Closed | 135 | 103 | BA | 330 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
40 | NORTHWEST | 449 | Centralia City Light | Bonneville Power Admin | 40199 | 1 | 1 | [10 empty] | Unreas Sat |  | Gen on HV | [6 empty] | 0 | 12 | 0 | 0 | 14 | -12 |  |  | GENTPF |  |  |  | Closed | 3 | 0 | HY | 25 |  | NO | 0 | 0.2 | 3 | 0.75 | 0 | 0 | NAN | 69 |  | B_STREET_69_YELM_G1_3 | HY (Hydro) | 1
40 | NORTHWEST | 417 | Midstate Electric Co-op | Bonneville Power Admin | 40237 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 5 | -0.5 | -0.2 | 14 | -5 | [6 empty] | Closed | 4.5 | -0.35 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 115 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 427 | Cosmo Speciality Fiber | Bonneville Power Admin | 40277 | C1 | C1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 15.8 | 0 | 0 | 14 | -15.8 | [6 empty] | Closed | 15.8 | 0 | ST | 12 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | WEYERHSR | ST (Steam Turbine) | C1
40 | NORTHWEST | 187 | Sierra Pacific Industries | Bonneville Power Admin | 40277 | S1 | S1 | [12 empty] | Gen on HV | [6 empty] | 0 | 12 | 0 | 0 | 14 | -12 |  |  | (GENROU) |  |  |  | Closed | 8 | 0 | GT | 12 |  | NO | 0 | 0.2 | 0 |  | 0.05 | 0.3 | 6 | 115 |  | SIERRA_G | GT (Gas Turbine) | S1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40278 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | -50 | 50 | -32 | 16 | 14 | 1.5 | 51.5 |  | GENTPJ | PSSSB | HYG3 | ST1C | Open | 0 | 0 | HY | 50 | PF<-0.85 | YES | 0 | 0.2 | 3.13 | 1.565 | 0.223 | 0.535 | 2.3991 | 13.8 |  | G_COULEE_13.8_PG8 | HY (Hydro) | 8
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40279 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | -53.5 | 53.5 | -21 | 16 | 14 | -8.5 | 45 |  | GENTPJ | PSS2B | HYG3 | ST1C | Open | 0 | 0 | HY | 53.5 |  | YES | 0 | 0.2 | 3.1 | 1.6585 | 0.2 | 0.6 | 3 | 13.8 |  | G_COULEE_13.8_PG11 | HY (Hydro) | 12
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40282 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40282 | 2 | 2 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 51.5 | PF<0.8 | NO | 0 | 0.2 | 3.36 | 1.7304 | 0.091 | 0.318 | 3.4945 | 13.8 |  |  | HY (Hydro) | 2
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40284 | 3 | 3 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 3
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40284 | 4 | 4 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 51.5 | PF<0.8 | NO | 0 | 0.2 | 3.36 | 1.7304 | 0.091 | 0.318 | 3.4945 | 13.8 |  |  | HY (Hydro) | 4
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40286 | 5 | 5 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 5
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40286 | 6 | 6 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | -51.5 | -51.5 | 0 | 0 | 14 | 51.5 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 49.5 | PF<0.8 | NO | 0 | 0.2 | 3.49 | 1.7275 | 0.156 | 0.439 | 2.8141 | 13.8 |  |  | HY (Hydro) | 6
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40297 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 710.1 | -83.2071 | 82.2046 | 14 | 115.9 | 826 |  | GENTPJ | PSS2B | HYGOVR | ESST5B | Closed | 700 | 82.2046 | HY | 825.6 |  | YES | 0 | 0.2 | 4.972 | 41.0488 | 0.05 | 0.2 | 4 | 15 |  | G_COULEE_15_G23 | HY (Hydro) | 1
40 | NORTHWEST | 54 | Lewis PUD | Bonneville Power Admin | 40307 | 1 | 1 | [12 empty] | Gen on HV |  |  |  | Missing PS |  |  | 0 | 39 | -34.04 | 22.02 | 14 | -3.9 | 35.1 |  | GENTPJ |  | HYG3 | EXST1_GE | Closed | 19.9 | 2.4452 | HY | 39 | PF<-0.85 | YES | 0 | 0.2 | 2.8 | 1.092 | 0.155 | 0.33 | 2.129 | 230 |  | COWFALLS_230_G01 | HY (Hydro) | 1
40 | NORTHWEST | 54 | Lewis PUD | Bonneville Power Admin | 40307 | 2 | 2 | [12 empty] | Gen on HV |  |  |  | Missing PS |  |  | 0 | 39 | -12.6 | 16.1 | 14 | -3.9 | 35.1 |  | GENTPJ |  | HYG3 | EXST1_GE | Closed | 19.9 | 2.4452 | HY | 39 |  | NO | 0 | 0.2 | 2.8 | 1.092 | 0.155 | 0.33 | 2.129 | 230 |  | COWFALLS_230_G02 | HY (Hydro) | 2
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 40346 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 15 | -10.05 | 2.16 | 14 | 2.25 | 17.25 |  | (GENTPJ) | (PSS2A) | (HYGOV4) | (EXST1_GE) | Closed | 13.9 | 2.16 | HY | 17.25 | PF<-0.85 | YES | 0 | 0.2 | 0 |  | 0.21 | 0.6 | 2.8571 | 13.8 |  | DEXTER_13.8_G01 | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 40365 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 266.3 | -125.14 | 82.85 | 14 | -266.3 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 224.3 | -11.2265 | HY | 266.32 |  | YES | 0.004 | 0.24 | 2.75 | 7.3238 | 0.21 | 0.42 | 2 | 13.8 |  |  | HY (Hydro) | 3
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 40561 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 103.6 | -72.8372 | 49.2696 | 14 | -23.81 | 79.79 |  | GENTPJ | PSS2A | HYG3 | ESST4B | Closed | 79 | -72.8372 | HY | 108.95 | PF<-0.85 | YES | 0 | 0.2 | 2.946 | 3.2097 | 0.12 | 0.4 | 3.3333 | 13.8 |  | ICE_HARB_13.8_G03 | HY (Hydro) | 3
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 40756 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 13.6 | -4.2 | 6.5 | 14 | -13.6 |  |  | GENTPJ | PSS2A |  | ST4C | Closed | 8 | -4.2 | HY | 13.6 |  | YES | 0 | 0.234 | 1.8 | 0.2448 | 0.124 | 0.283 | 2.2823 | 6.6 |  | ROZA_12.5_PH1 | HY (Hydro) | 1
40 | NORTHWEST | 28 | Northern Wasco PUD | Bonneville Power Admin | 41011 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 6 | 0 | 0 | 14 | -6 | [6 empty] | Closed | 5 | 0 | HY | 5 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 1479 | Pacific Marine Energy Center | Bonneville Power Admin | 41081 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model | Missing PS |  |  | 0 | 20 | -3.3 | 3.3 | 14 | -20 | [6 empty] | Closed | 1 | 0 | HB | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | HB (Hydrokinetic, Wave Buoy) | 1
40 | NORTHWEST | 496 | Bonners Ferry City of | Bonneville Power Admin | 41240 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | 0 | 0 | 14 | -2 |  |  | GENTPF |  |  |  | Closed | 2 | 0 | HY | 4.4 |  | NO | 0 | 0.2 | 3 | 0.132 | 0 | 0 | NAN | 115 |  | MOYIE_115_G01 | HY (Hydro) | 1
40 | NORTHWEST | 1457 | Smith Creek Hydro LLC | Bonneville Power Admin | 41298 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 38 | -8 | 5.8 | 14 | -38 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | HY | 36 |  | NO | 0 | 0.2 | 3 | 1.08 | 0 | 0 | NAN | 13.8 |  | SMITHFLS_13.8_G01 | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 41303 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 20 | -12.8 | 11.8 | 14 | -20 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Open | 0 | 0 | HY | 23 | PF<-0.85 | YES | 0 | 0.2 | 2.632 | 0.60536 | 0.185 | 0.54 | 2.9189 | 13.8 |  | DETROIT_13.8_G03 | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 41306 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 12 | 29.9 | -25.275 | 15.23 | 14 | 2.1 | 32 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 14.9 | 5.14 | HY | 29.9 | PF<-0.85 | YES | 0.007 | 0.299 | 3.28 | 0.98072 | 0.25 | 0.52 | 2.08 | 13.8 |  | LSTCR_PH_13.8_LSTC_G01 | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 41306 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 12 | 29.9 | -26 | 17.5 | 14 | 2.1 | 32 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Open | 0 | 0 | HY | 29.9 | PF<-0.85 | YES | 0.007 | 0.299 | 3.28 | 0.98072 | 0.25 | 0.52 | 2.08 | 13.8 |  | LSTCR_PH_13.8_LSTC_G02 | HY (Hydro) | 2
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 41729 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | 0 | 125 | -50 | 6 | 14 | 5 | 130 |  | GENTPJ | PSSSB | HYG3 | ESDC1A | Closed | 115 | -12.4795 | HY | 125 |  | YES | 0 | 0.2 | 4.457 | 5.5712 | 0.05 | 0.19 | 3.8 | 13.8 |  | G_COULEE_13.8_G09 | HY (Hydro) | 9
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 41734 | E | E | [10 empty] | Unreas Sat | [8 empty] | 0 | 125 | -50 | 5 | 14 | 8 | 133 |  | GENTPJ | PSS2A | HYG3 | ESDC1A | Closed | 115 | -12.4794 | HY | 125 |  | YES | 0 | 0.2 | 4.779 | 5.9737 | 0.05 | 0.49 | 9.8 | 13.8 |  | G_COULEE_13.8_G14 | HY (Hydro) | E
40 | NORTHWEST | 50 | US Bur Reclam | Bonneville Power Admin | 41735 | F | F | [10 empty] | Unreas Sat | [8 empty] | 0 | 125 | -50 | 5 | 14 | 8 | 133 |  | GENTPJ | PSS2A | HYG3 | ESDC1A | Closed | 115 | -12.4794 | HY | 125 |  | YES | 0 | 0.2 | 4.779 | 5.9737 | 0.05 | 0.55 | 11 | 13.8 |  | G_COULEE_13.8_G15 | HY (Hydro) | F
40 | NORTHWEST | 30 | Puget Sound Energy | Puget Sound Energy | 42131 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 42.2 | -8 | 20 | 30 | -3.86 | 38.34 |  | GENTPJ |  | GGOV1 | REXS | Closed | 38.3 | -8 | GT | 46.68 |  | NO | 0 | 0.2 | 5.38 | 2.5114 | 0.08 | 0.39 | 4.875 | 13.8 |  | TEXACO_W_13.8_GEN1 | GT (Gas Turbine) | 1 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Puget Sound Energy | 42132 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 42.2 | -8 | 20 | 30 | -3.86 | 38.34 |  | GENTPJ |  | GGOV1 | REXS | Closed | 38.3 | -8 | GT | 46.68 |  | NO | 0 | 0.2 | 5.38 | 2.5114 | 0.08 | 0.39 | 4.875 | 13.8 |  | TEXACO_W_13.8_GEN2 | GT (Gas Turbine) | 2 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Puget Sound Energy | 42133 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 42.2 | -8 | 20 | 30 | -0.2 | 42 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 38.3 | -8 | GT | 46.68 |  | NO | 0 | 0.2 | 7.56 | 3.529 | 0.101 | 0.585 | 5.7921 | 13.8 |  | TEXACO_W_13.8_GEN3 | GT (Gas Turbine) | 3 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 42990 | Z4 | Z4 | [17 empty] | Missing Sub R/X |  | 0 | 151.8 | -73.5 | 73.5 | 14 | -151.8 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 151.8 | 58.5734 | W4 | 171.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | PHALGLCH_0.69_Z1 | W4 (Wind Turbine, Type 4) | Z4 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 42994 | Z4 | Z4 | [17 empty] | Missing Sub R/X |  | 0 | 190.9 | -92.5 | 92.5 | 14 | -190.9 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 101.48 | 91.6818 | W4 | 215.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | DODGEJCT_0.69_GN1 | W4 (Wind Turbine, Type 4) | Z4 |  | PSS Exempt
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43359 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 25.7 | -16.8 | 15.4 | 32 | 0.03 | 25.73 |  | GENTPJ | PSS2A | HYGOV4 | ESST1A_GE | Closed | 3.5808 | 4.3036 | HY | 34.5 | PF<-0.85 | NO | 0.004 | 1.52 | 1.71 | 0.58995 | 0.22 | 0.58 | 2.6364 | 13.8 |  | N_FORK_13.8_G02 | HY (Hydro) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43425 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 23 | -12.2634 | 11.7567 | 32 | -23 |  |  | GENTPF |  |  |  | Closed | 8.9597 | 1.093 | HY | 25 |  | YES | 0 | 1.4 | 2.4 | 0.6 | 0 | 0 | NAN | 13.8 |  | PTLHYDRO_13.8_G1 | HY (Hydro) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43429 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11 | -7.5 | 6.2 | 32 | -11 |  |  | GENTPF |  |  |  | Open | 0 | 0 | HY | 12.5 | PF<-0.85 | YES | 0 | 1.4 | 3.616 | 0.452 | 0 | 0 | NAN | 13.8 |  | PTLHYDRO_13.8_G2 | HY (Hydro) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43465 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -2 | 2.4 | 32 | -5 |  |  | GENTPJ | PSS2B |  | ESST1A_GE | Closed | 1.7103 | 2.4 | HY | 5.5 |  | NO | 0.004 | 0.82 | 2.8 | 0.154 | 0.12 | 0.33 | 2.75 | 11 |  | RIVRMILL_11_G3 | HY (Hydro) | 3
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43466 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -2 | 0 | 32 | -5 |  |  | GENTPJ | PSS2B |  | ESST1A_GE | Closed | 1.7103 | 0 | HY | 5.5 |  | NO | 0.003 | 0.737 | 2.2 | 0.121 | 0.2 | 0.35 | 1.75 | 11 |  | RIVRMILL_11_G4 | HY (Hydro) | 4
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43466 | 5 | 5 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 5 | -2 | 2.4 | 32 | -5 |  |  | GENTPJ | PSS2B |  | ESST1A_GE | Closed | 1.7103 | 2.4 | HY | 5.5 |  | NO | 0.004 | 1 | 2 | 0.11 | 0.12 | 0.35 | 2.9167 | 11 |  | RIVRMILL_11_G5 | HY (Hydro) | 5
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43488 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 130 | -89.9035 | 58.4511 | 32 | -130 |  |  | GENTPJ | PSS2A | H6E | ESST1A_GE | Closed | 51.2837 | 32.5721 | HY | 144 | PF<-0.85 | YES | 0.003 | 1.902 | 3.85 | 5.544 | 0.185 | 0.6 | 3.2432 | 13.8 |  | ROUND_BU_13.8_G02 | HY (Hydro) | 2
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43556 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 18 | -10.1614 | -10.1614 | 32 | 15.11 | 33.11 |  | WT1G |  | WT1T |  | Closed | 8.4678 | -10.1614 | HY | 33.11 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | SULIVAN_57_G01 | HY (Hydro) | 1 |  | PSS Exempt
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43963 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | -75 | 75 | -24.65 | 24.65 | 32 | -75 | [6 empty] | Closed | 75 | -24.65 | BA | 105.2 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.48 |  | CONSTABLE_0.48_B01 | BA (Energy Storage, Battery) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43966 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | -200 | 204.75 | -65.75 | 65.75 | 32 | -204.75 | [6 empty] | Closed | 200 | 65.75 | BA | 225 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.55 |  | SEASIDE_0.55_B01 | BA (Energy Storage, Battery) | 1
40 | NORTHWEST | 32 | Portland General Elec | Portland General Elec | 43973 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | -204.2 | 204.2 | -65.75 | 65.75 | 32 | -204.2 | [6 empty] | Closed | 200 | -65.75 | BA | 245.7 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.66 |  | SUNDIAL_0.66_B01 | BA (Energy Storage, Battery) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 44031 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 12.1 | -5.3 | 6.1 | 14 | 1.9 | 14 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 4.5 | 6.1 | HY | 12.1 |  | YES | 0 | 0.2 | 2.3 | 0.2783 | 0.21 | 0.6 | 2.8571 | 4.16 |  | FOSTER_4.2_G01 | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44101 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G01 | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44102 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G02 | HY (Hydro) | 2
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44103 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G03 | HY (Hydro) | 3
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44104 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 83.7 | -42.9894 | 30.9275 | 14 | -83.7 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 68 | 30.9275 | HY | 100 |  | YES | 0.003 | 0.2 | 3.955 | 3.955 | 0.085 | 0.3 | 3.5294 | 13.8 |  | MCNARY_13.2_G04 | HY (Hydro) | 4
40 | NORTHWEST | 28 | Northern Wasco PUD | Bonneville Power Admin | 44128 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model | Missing PS |  |  | 0 | 10 | 0 | 0 | 14 | -10 | [6 empty] | Closed | 8 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 115 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44231 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 155.3 | -35.75 | 50.375 | 14 | 8.12 | 163.42 |  | GENTPJ | PSS2B | IEEEG3_GE | ESST1A_GE | Closed | 138.5 | -15.2414 | HY | 163.42 |  | YES | 0.006 | 0.39 | 3.25 | 5.3111 | 0.184 | 0.48 | 2.6087 | 13.8 |  | LOW_GRAN_13.8_G02 | HY (Hydro) | 1
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44231 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 132 | -42.5 | 53.75 | 14 | 31.42 | 163.42 |  | GENTPJ | PSS2B | IEEEG3_GE | ESST1A_GE | Closed | 125 | -15.2414 | HY | 163.42 |  | YES | 0.006 | 0.39 | 3.25 | 5.3111 | 0.184 | 0.48 | 2.6087 | 13.8 |  | LOW_GRAN_13.8_G01 | HY (Hydro) | 2
40 | NORTHWEST | 989 | USACE-Walla Walla District | Bonneville Power Admin | 44232 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 155.3 | -63.4353 | 45.375 | 14 | -155.3 |  |  | GENTPJ | PSS2A | H6E | ESST4B | Closed | 138.5 | -15.2414 | HY | 163.42 |  | YES | 0.006 | 0.39 | 2.961 | 4.8389 | 0.028 | 0.2 | 7.1429 | 13.8 |  | LOW_GRAN_13.8_G04 | HY (Hydro) | 4
40 | NORTHWEST | 606 | EDP Renewables | Bonneville Power Admin | 44279 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 102.2 | -43.5947 | -43.5947 | 14 | -102.2 |  |  | WT2G |  | WT2T | WT2E | Closed | 102.2 | -43.5947 | W2 | 111.34 |  | YES | 0.017 | 0.34 | 0 |  |  |  | NAN | 0.6 |  | KITASVLY_0.6_G1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44508 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 5 | 0 | 0 | 13 | -5 | [6 empty] | Closed | 4 | 0 | HY | 5 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44574 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 47.25 | -22.88 | 22.88 | 13 | -47.25 | [6 empty] | Closed | 37.8 | 11.2687 | PV | 52.5 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 0.55 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44577 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44586 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 40 | -19.37 | 19.37 | 13 | -40 | [6 empty] | Closed | 17.26 | 10.0476 | W4 | 44.448 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44623 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model | Missing PS |  |  | 0 | 36.94 | -33.57 | 33.57 | 13 | -36.94 | [6 empty] | Closed | 7.388 | 19.3899 | ST | 43.42 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | ST (Steam Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44624 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44625 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 8 | 0 | 0 | 13 | -8 | [6 empty] | Closed | 6.4 | 0 | PV | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44625 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44626 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44627 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 20.8 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44628 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 2 | 0 | 0 | 13 | -2 | [6 empty] | Closed | 1.6 | 0 | PV | 2 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44628 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 8 | 0 | 0 | 13 | -8 | [6 empty] | Closed | 6.4 | 0 | PV | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44628 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 3
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44629 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44630 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44630 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44630 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 3
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44631 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44632 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | 0 | 0 | 13 | -10 | [6 empty] | Closed | 8 | 0 | PV | 10 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44654 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 55.398 | -29.988 | 29.988 | 13 | -55.398 | [6 empty] | Closed | 23.91 | -29.988 | WT | 63.168 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44834 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 6.25 | 4.69 | 4.69 | 13 | -6.25 | [6 empty] | Closed | 1.25 | 0.938 | ST | 7.81 | PF<0.8 | NO | 0 | 0.18 | 0 |  |  |  | NAN | 13.2 |  |  | ST (Steam Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44836 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4 | 9 | 13 | -15 |  |  | GENTPJ | PSS2B |  | EXST4B | Closed | 12 | 1.9989 | HY | 16.67 |  | NO | 0 | 0.25 | 2.61 | 0.43509 | 0.35 | 1.27 | 3.6286 | 6.9 |  | TOKETEE_6.9_G01 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44837 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4 | 7 | 13 | -15 |  |  | GENTPJ |  |  | ESDC3A | Closed | 12 | 1.9914 | HY | 16.67 |  | NO | 0 | 0.31 | 2.61 | 0.43509 | 0.36 | 1.4 | 3.8889 | 6.9 |  | TOKETEE_6.9_G02 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44838 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4 | 4 | 13 | -15 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 12 | 1.9947 | HY | 16.67 |  | NO | 0 | 0.31 | 2.53 | 0.42175 | 0.25 | 1.07 | 4.28 | 6.9 |  | TOKETEE_6.9_G03 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44839 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 13.41 | -5.59 | 6.49 | 13 | -13.41 | [6 empty] | Closed | 2.682 | -3.8861 | ST | 14.9 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  | RFP_13.8_RFP | ST (Steam Turbine) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44881 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 41 | -8.3 | -8.3 | 13 | 4.51 | 45.51 |  | WT1G | WT1P_B | WT1T |  | Closed | 17.69 | -1.66 | W1 | 45.14 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | COL_HILL_34.5_G01 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 44971 | N | N | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 5 | -2 | 2.4 | 13 | 0.55 | 5.55 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 4 | -2 | HY | 5.55 |  | NO | 0 | 0.18 | 3 | 0.1665 | 0 | 0 | NAN | 69 |  | LKSISKIU_69_G01 | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45022 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1 | 0 | 0 | 13 | -1 |  |  | GENTPF |  |  |  | Closed | 0.8 | 0 | HY | 1 |  | NO | 0 | 0.18 | 3 | 0.03 | 0 | 0 | NAN | 4.2 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45026 | N | N | [10 empty] | Unreas Sat | [8 empty] | 0 | 24 | -4 | 8 | 13 | 1 | 25 |  | GENTPJ |  | GGOV1 | EXST4B | Closed | 19.2 | -0.68525 | HY | 25 |  | NO | 0 | 0.18 | 3 | 0.75 | 0.2 | 0.8 | 4 | 13.8 |  | BIOMASS_13.8_GN1 | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45045 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 9.9 | 0 | 0 | 13 | -9.9 | [6 empty] | Closed | 7.92 | 0 | PV | 9.9 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 115 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45056 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 5 | 0 | 0 | 13 | -5 | [6 empty] | Closed | 4 | 0 | PV | 5 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45086 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 4.8 | 0 | 0 | 13 | -4.8 | [6 empty] | Closed | 3.84 | 0 | PV | 4.8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45122 | N | N | [10 empty] | Unreas Sat | [8 empty] | 0 | 3 | 0 | 0 | 13 | -3 |  |  | GENTPF |  |  |  | Closed | 2.4 | 0 | HY | 3 |  | NO | 0 | 0.18 | 3 | 0.09 | 0 | 0 | NAN | 69 |  |  | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45138 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 3.3 | 0 | 0 | 13 | -3.3 | [6 empty] | Closed | 2.64 | 0 | PV | 3.3 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45168 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 3 | 0 | 0 | 13 | -3 |  |  | GENTPF |  |  |  | Closed | 2.4 | 0 | HY | 3.1 |  | NO | 0 | 0.18 | 3 | 0.093 | 0 | 0 | NAN | 2.4 |  | EAGLEPT_2.4_G1 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45172 | 1 | 1 | [10 empty] | Unreas Sat |  | Gen on HV | [6 empty] | 0 | 1 | 0 | 0 | 13 | -1 |  |  | GENTPF |  |  |  | Closed | 0.8 | 0 | HY | 13.7 |  | NO | 0 | 0.18 | 3 | 0.411 | 0 | 0 | NAN | 69 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45176 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2.2 | 0 | 0 | 13 | 1e-08 | 2.2 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 1.76 | 0 | HY | 2.2 |  | NO | 0 | 0.18 | 3 | 0.066 | 0 | 0 | NAN | 2.3 |  | FALLCRK_2.4_GEN | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45178 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.8 | 0 | 0 | 13 | -1.8 |  |  | GENTPF |  |  |  | Closed | 1.44 | 0 | HY | 5.1 |  | NO | 0 | 0.18 | 3 | 0.153 | 0 | 0 | NAN | 69 |  | FARMIRR_69_TOT_GEN | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45180 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 11 | -6.8 | 6.8 | 13 | -11 |  |  | GENTPJ |  |  | ESDC3A | Closed | 8.8 | 6.8 | HY | 12.94 |  | NO | 0 | 0.18 | 2.26 | 0.29244 | 0.12 | 0.34 | 2.8333 | 6.9 |  | FISH_CRK_6.9_G01 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45256 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 29 | -9.5 | 9.5 | 13 | -29 |  |  | GENTPJ | PSS2B |  | ESDC4B | Closed | 23.2 | 1.8229 | HY | 34.5 |  | NO | 0 | 0.31 | 3.08 | 1.0626 | 0.2 | 1.08 | 5.4 | 12 |  | LEMOLO_1_12_G01 | HY (Hydro) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45290 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 33 | -7.9 | 12.6 | 13 | 5.5 | 38.5 |  | GENTPJ | PSS2A | HYGOV | ESST4B | Closed | 26.4 | 3.5069 | HY | 45 |  | NO | 0 | 0.301 | 2.4 | 1.08 | 0.26 | 1 | 3.8462 | 11.5 |  | LEMOLO_2_11.5_G01 | HY (Hydro) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45338 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 8 | 0 | 0 | 13 | -8 | [6 empty] | Closed | 6.4 | 0 | PV | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45351 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 81.2 | -16 | 21 | 13 | 2.3 | 83.5 |  | GENTPJ | PSS2A | IEEEG3_GE | ESST1A_GE | Closed | 58.64 | 7.5982 | HY | 83.5 |  | NO | 0 | 0.21 | 3 | 2.505 | 0.219 | 0.941 | 4.2968 | 13.8 |  | YALE_13.8_GEN1 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45351 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 80.2 | -16.3 | 21.2 | 13 | 3.3 | 83.5 |  | GENTPJ | PSS2A | IEEEG3_GE | ESST1A_GE | Open | 0 | 0 | HY | 83.5 |  | NO | 0 | 0.21 | 3 | 2.505 | 0.219 | 0.941 | 4.2968 | 13.8 |  | YALE_13.8_GEN2 | HY (Hydro) | 2
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45368 | N | N | [10 empty] | Unreas Sat | [8 empty] | 0 | 5 | 0 | 0 | 13 | -5 |  |  | GENTPF |  |  |  | Closed | 4 | 0 | HY | 5 |  | NO | 0 | 0.18 | 3 | 0.15 | 0 | 0 | NAN | 69 |  |  | HY (Hydro) | N
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45439 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 20.3 | -3.6 | 3.6 | 13 | -20.3 |  |  | GENTPJ |  |  | EXST4B | Closed | 16.24 | -3.107 | HY | 20.3 |  | NO | 0 | 0.18 | 3 | 0.609 | 0.2 | 1 | 5 | 6.9 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45445 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 0.8 | -0.6 | 0.6 | 13 | 0.2 | 1 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 0.64 | 0.48 | HY | 1 | PF<-0.85 | NO | 0 | 0.18 | 3 | 0.03 | 0.2 | 1 | 5 | 2.3 |  | PROSPECT_2.3_G04 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45453 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -6 | 12 | 13 | 0.7 | 4.7 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 3.2 | -1.7316 | HY | 4.7 | PF<0.8 | NO | 0 | 0.18 | 3 | 0.141 | 0.2 | 1 | 5 | 2.3 |  | PROSPECT_2.3_G01 | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45485 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.2 | -1 | 2 | 13 | 0.47 | 4.67 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 3.36 | -0.30365 | HY | 4.67 |  | NO | 0 | 0.18 | 3 | 0.1401 | 0 | 0 | NAN | 4.2 |  | SLATECRK_4.16_GEN | HY (Hydro) | 1
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45502 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 0.83 | 0 | 0 | 13 | -0.83 | [6 empty] | Closed | 0.664 | 0 | PV | 0.83 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45502 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 2.9 | 0 | 0 | 13 | -2.9 | [6 empty] | Closed | 2.32 | 0 | PV | 2.9 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 69 | BES Exempt |  | PV (Photovoltaic) | 2 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | PacifiCorp - West | 45549 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -3 | 5 | 13 | 2 | 9 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 5.6 | 2.2343 | HY | 9 |  | NO | 0 | 0.18 | 3 | 0.27 | 0.2 | 1 | 5 | 6.6 |  | PROSPECT_6.6_G03 | HY (Hydro) | 1
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46055 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 6.7 | 0 | 0 | 35 | -6.7 | [6 empty] | Closed | 4 | 0 | HY | 6.7 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | PEC_115_G01 | HY (Hydro) | 1
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46071 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 9.4 | 0 | 0 | 35 | -9.4 | [6 empty] | Closed | 7 | 0 | HY | 9.4 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 115 |  | QUIN_CH_115_G01 | HY (Hydro) | 1
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46171 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 100 | -37 | 33 | 35 | 0 | 100 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 80 | 33 | HY | 100 |  | YES | 0 | 0.2 | 3.325 | 3.325 | 0.09 | 0.41 | 4.5556 | 13.2 |  | P_RAPIDS_13.8_G02 | HY (Hydro) | 2
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46172 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 100 | -35 | 32 | 35 | 0 | 100 |  | GENTPJ | PSS2A | HYGOV4 | EXST1_GE | Closed | 80 | 32 | HY | 100 |  | YES | 0 | 0.2 | 3.55 | 3.55 | 0.14 | 0.32 | 2.2857 | 13.2 |  | P_RAPIDS_13.8_G03 | HY (Hydro) | 3
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46174 | 5 | 5 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 100 | -35 | 32 | 35 | 0 | 100 |  | GENTPJ | PSS2A | HYGOV4 | EXST1_GE | Closed | 80 | 32 | HY | 100 |  | YES | 0 | 0.2 | 3.55 | 3.55 | 0.14 | 0.32 | 2.2857 | 13.2 |  | P_RAPIDS_13.8_G05 | HY (Hydro) | 5
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46175 | 6 | 6 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 100 | -35 | 32 | 35 | 0 | 100 |  | GENTPJ | PSS2A | HYGOV4 | EXST1_GE | Closed | 80 | 32 | HY | 100 |  | YES | 0 | 0.2 | 3.55 | 3.55 | 0.14 | 0.32 | 2.2857 | 13.2 |  | P_RAPIDS_13.8_G06 | HY (Hydro) | 6
40 | NORTHWEST | 35 | Grant PUD | Grant PUD [Bus] | 46177 | 8 | 8 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 100 | -37 | 33 | 35 | 0 | 100 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 80 | 33 | HY | 100 |  | YES | 0 | 0.2 | 3.325 | 3.325 | 0.09 | 0.41 | 4.5556 | 13.2 |  | P_RAPIDS_13.8_G08 | HY (Hydro) | 8
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46210 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 10.5 | -4.81 | 4.68 | 14 | -10.5 |  |  | GENTPJ |  |  | ESST4B | Closed | 6.3 | -4.81 | HY | 10.5 |  | YES | 0 | 0.2 | 1.9 | 0.1995 | 0.17 | 0.6 | 3.5294 | 11.5 |  | TRAILBRG_11.5_G01 | HY (Hydro) | 3 |  | PSS Exempt
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46268 | 1 | 1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 31.4 | -6 | 25 | 14 | -31.4 |  |  | GENROU |  |  | ESST2A | Closed | 25.3 | 13.3647 | ST | 58.871 | PF<0.8 | NO | 0 | 0.2 | 1.71 | 1.0067 | 0.092 | 0.284 | 3.087 | 13.8 |  | WEYRHSR3_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46297 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 19.8 | 9 | 15 | 14 | -0.022 | 19.778 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 16 | 9 | ST | 19.778 | PF<0.8 | NO | 0 | 1e-05 | 3 | 0.59334 | 0.15 | 0.45 | 3 | 13.8 |  | ENID_RD_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 33 | Eugene Water & Elec Bd | Bonneville Power Admin | 46306 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 9.8 | -4 | 5.5 | 14 | -9.8 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 5 | -4 | HY | 9.412 |  | NO | 0 | 1e-05 | 1.97 | 0.18542 | 0.0059 | 0.1302 | 22.0678 | 11.5 |  | WALTVILE_66_G01 | HY (Hydro) | 1
40 | NORTHWEST | 647 | WestRock CP LLC | Bonneville Power Admin | 46606 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 64 | -28 | 40 | 14 | -64 |  |  | GENROU | PSS2B |  | ESAC8B_GE | Open | 0 | 0 | ST | 75.5 |  | YES | 0 | 1.89 | 6.9 | 5.2095 | 0.0565 | 1.1551 | 20.4442 | 13.8 |  | TACOBMAS_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 38 | Tacoma Power | Tacoma Power [Bus] | 46617 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 2 | 0 | 0 | 38 | -2 |  |  | GENTPJ |  |  |  | Closed | 2 | 0 | HY | 2.5 |  | YES | 0 | 0.16 | 0.7583 | 0.018957 | 0.1261 | 0.4167 | 3.3045 | 13.8 |  | NFORK_13.8_G34 | HY (Hydro) | 1
40 | NORTHWEST | 38 | Tacoma Power | Tacoma Power [Bus] | 46617 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 2 | 0 | 0 | 38 | -2 |  |  | GENTPJ |  |  |  | Closed | 2 | 0 | HY | 2.5 |  | YES | 0 | 0.16 | 0.7583 | 0.018957 | 0.1261 | 0.4167 | 3.3045 | 13.8 |  | NFORK_13.8_G35 | HY (Hydro) | 2
40 | NORTHWEST | 36 | Chelan PUD | Chelan PUD | 46891 | B3 | B3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 23 | -10.36 | 10.4 | 36 | -4.2e-07 | 23 |  | GENTPF |  | GPWSCC | EXDC1 | Closed | 20 | 10.4 | HY | 23 |  | YES | 0 | 0.325 | 2.78 | 0.6394 | 0.052 | 0.214 | 4.1154 | 13.8 |  | ROCK_ISL_13.8_B3 | HY (Hydro) | B3
40 | NORTHWEST | 36 | Chelan PUD | Chelan PUD | 46891 | B4 | B4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 23 | -10.36 | 10.4 | 36 | -4.2e-07 | 23 |  | GENTPF | PSS2B | HYG3 | ESAC7B | Closed | 20 | 10.4 | HY | 23 |  | YES | 0 | 0.325 | 2.78 | 0.6394 | 0.16 | 0.33 | 2.0625 | 13.8 |  | ROCK_ISL_13.8_B4 | HY (Hydro) | B4
40 | NORTHWEST | 44 | Pend Oreille PUD | Bonneville Power Admin | 47010 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 22.5 | -12.5 | 14.945 | 29 | 2.5 | 25 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 12.9 | -4.8271 | HY | 25 |  | YES | 0 | 0.35 | 1.57 | 0.3925 | 0.22 | 0.52 | 2.3636 | 13.8 |  | BOX_CANY_13.8_G01 | HY (Hydro) | 1
40 | NORTHWEST | 44 | Pend Oreille PUD | Bonneville Power Admin | 47012 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 22.5 | -12.5 | 14.945 | 29 | 2.5 | 25 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 12.9 | -4.769 | HY | 25 |  | YES | 0 | 0.35 | 1.57 | 0.3925 | 0.22 | 0.52 | 2.3636 | 13.8 |  | BOX_CANY_13.8_G02 | HY (Hydro) | 2
40 | NORTHWEST | 51 | Emerald PUD | Bonneville Power Admin | 47023 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 3 | -0.5 | -0.5 | 14 | -3 |  |  | GENTPF |  |  |  | Closed | 2.5 | 0 | IC | 5 |  | NO | 0 | 0.2 | 3 | 0.15 | 0 | 0 | NAN | 115 |  |  | IC (Internal Combustion) | 1
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47104 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G01 | HY (Hydro) | 1
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47104 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -60 | 51.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Open | 0 | 0 | HY | 81.5 | PF<-0.85 | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G02 | HY (Hydro) | 2
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47105 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G03 | HY (Hydro) | 3
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47105 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G04 | HY (Hydro) | 4
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47106 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Open | 0 | 0 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G05 | HY (Hydro) | 5
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47106 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G06 | HY (Hydro) | 6
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47107 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G07 | HY (Hydro) | 7
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47107 | 8 | 8 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G08 | HY (Hydro) | 8
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47108 | 9 | 9 | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G10 | HY (Hydro) | 9
40 | NORTHWEST | 46 | Douglas PUD | Douglas PUD | 47108 | A | A | [10 empty] | Unreas Sat | [8 empty] | 0 | 85.5 | -39 | 33.5 | 46 | 3.5 | 89 |  | GENTPF | WSCCST | GPWSCC | EXDC1 | Closed | 80 | 5.0863 | HY | 81.5 |  | YES | 0.014 | 0.32 | 3.27 | 2.665 | 0.25 | 1.17 | 4.68 | 14.4 |  | WELLS_14.4_G09 | HY (Hydro) | A
40 | NORTHWEST | 39 | Energy Northwest | Bonneville Power Admin | 47271 | 2 | 2 | [8 empty] | RX Ratio | [6 empty] | Missing Model |  |  |  | 0 | 3.2 | -0.4 | 0.4 | 14 | -3.2 | [6 empty] | Closed | 3 | 0 | PV | 3.2 |  | NO | 0.8 | 1e-05 | 0 |  |  |  | NAN | 115 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 428 | Georgia Pacific | Bonneville Power Admin | 47290 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 42 | -26.5 | 33 | 14 | -42 |  |  | GENROU | PSS2B |  | ESAC8B_GE | Open | 0 | 0 | ST | 42 | PF<0.8 | NO | 0 | 0.2 | 3 | 1.26 | 0.072 | 0.337 | 4.6806 | 13.8 |  | WAUNA_13.8_G02 | ST (Steam Turbine) | 1
40 | NORTHWEST | 412 | Klickitat County PUD | Bonneville Power Admin | 47294 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 10.5 | -3.5 | 3.5 | 14 | -10.5 | [6 empty] | Open | 0 | 0 | CC | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | CC (Combined Cycle Generic) | 1
40 | NORTHWEST | 412 | Klickitat County PUD | Bonneville Power Admin | 47296 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 20 | -6.6 | 6.6 | 14 | -20 | [6 empty] | Open | 0 | 0 | JE | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | JE (Jet Engine) | 2
40 | NORTHWEST | 412 | Klickitat County PUD | Bonneville Power Admin | 47296 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 6 | -2 | 2 | 14 | -6 | [6 empty] | Open | 0 | 0 | CC | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | CC (Combined Cycle Generic) | 3
40 | NORTHWEST | 13 | PacifiCorp - West | Bonneville Power Admin | 47359 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1 | 0 | 0 | 14 | -1 |  |  | GENTPF |  |  |  | Closed | 1 | 0 | HY | 1 |  | NO | 0 | 0.18 | 3 | 0.03 | 0 | 0 | NAN | 230 |  | LION_MTN_230_G01 | HY (Hydro) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47378 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 81.3 | -53.4 | 53.4 | 937 | -81.3 |  |  | REGC_A |  |  | REEC_A | Closed | 81.3 | -13.3258 | PV | 131.04 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.7 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 652 | Southern California Power Auth | Bonneville Power Admin | 47384 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 50 | 0 | 0 | 14 | -50 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 41.58 | 0 | W3 | 51.25 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.58 |  | LINDN_0.6_G1 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47397 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 100.4 | -33 | 33 | 937 | -100.4 |  |  | REGC_A |  |  | REEC_A | Closed | 100.4 | -3.7891 | W3 | 124.332 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 47446 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | 0 | 32 | -1.5 | 18.2 | 14 | -32 |  |  | GENTPF |  |  | EXST4B | Closed | 18 | 3.2521 | ST | 14 |  | NO | 0 | 1 | 3 | 0.42 | 0 | 0 | NAN | 13.8 |  |  | ST (Steam Turbine) | 7
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 47448 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 25.6 | 0 | 11.4 | 14 | -25.6 |  |  | GENTPF |  |  | EXST4B | Closed | 12 | 6.461 | ST | 14 |  | NO | 0 | 1 | 3 | 0.42 | 0 | 0 | NAN | 13.8 |  |  | ST (Steam Turbine) | 6
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47452 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 132.5 | -51.5 | 62 | 14 | -132.5 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 132.5 | 15.71 | W4 | 298.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSNC_0.7_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47455 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 132.5 | -51.5 | 62 | 14 | -132.5 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 70.43 | 3.2138 | W4 | 298.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSNC_0.7_Z2 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47458 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -38.5 | 42 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | 7.1991 | W4 | 324.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSCC_0.7_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47461 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -38.5 | 42 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | 7.1991 | W4 | 298.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSCC_0.7_Z2 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47464 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -66 | 76 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | 40.4247 | W4 | 324.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSSC_0.7_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 492 | Caithness | Bonneville Power Admin | 47469 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 145 | -66 | 79 | 14 | -145 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 145 | -0.071971 | W4 | 324.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | SHEPDSSC_0.7_Z2 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47489 | Z1 | Z1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 5.9 | 98.9 | -30.2 | 42.8 | 937 | -98.9 |  |  | REGC_A |  |  | REEC_A | Closed | 53.05 | -30.2 | W3 | 98.9 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.72 |  |  | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 487 | Cannon Power | Bonneville Power Admin | 47495 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 115 | -50 | 25 | 14 | -115 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 115 | 14.8216 | W4 | 127.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | DOOLEY_0.69_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 487 | Cannon Power | Bonneville Power Admin | 47498 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 117.3 | -51 | 25.5 | 14 | -117.3 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 52.16 | 14.8216 | W4 | 130.36 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 448 | Rathdrum Power LLC | Bonneville Power Admin | 47568 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 122 | 211 | -111.2 | 111.2 | 29 | -39 | 172 |  | GENROU | PSS2A | GGOV1 | ESST4B | Closed | 165 | 39.5546 | CT | 211 |  | NO | 0.003 | 0.18 | 6.1 | 12.871 | 0.052 | 0.092 | 1.7692 | 18 |  | RATH_PWR_18_GT | CT (Combined Cycle Combustion Turbine Part) | 1
40 | NORTHWEST | 448 | Rathdrum Power LLC | Bonneville Power Admin | 47569 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 70 | 143 | -75.6 | 75.6 | 29 | -143 |  |  | GENROU | PSS2A |  | REXS | Closed | 65 | 39.5547 | CA | 143.6 |  | NO | 0.003 | 0.18 | 4.35 | 6.2466 | 0.09 | 0.45 | 5 | 13.8 |  | RATH_PWR_13.8_ST | CA (Combined Cycle Steam Part) | 1
40 | NORTHWEST | 458 | Frederickson Power LLP | Bonneville Power Admin | 47577 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 192 | -50 | 110 | 14 | -25.7 | 166.3 |  | GENROU | PSS2A | GGOV1 | EXST4B | Closed | 150 | -11.6862 | GT | 192 |  | YES | 0.002 | 0.202 | 5.92 | 11.3664 | 0.053 | 0.445 | 8.3962 | 18 |  | FREDCOGN_18_GT | GT (Gas Turbine) | 1
40 | NORTHWEST | 1423 | Grays Harbor Energy LLC | Bonneville Power Admin | 47596 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 216.2 | -73.2 | 170.4 | 14 | -52.6 | 163.6 |  | GENQEC | PSS2A | GGOV1 | EXST4B | Closed | 138 | -55.0953 | GT | 245.7 | PF<0.8 | YES | 0 | 0.2 | 1.033 | 2.5381 |  |  | NAN | 18 |  | GRAYS_H_18_G01 | GT (Gas Turbine) | 1
40 | NORTHWEST | 1423 | Grays Harbor Energy LLC | Bonneville Power Admin | 47597 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 216.2 | -73.2 | 170.4 | 14 | -52.6 | 163.6 |  | GENQEC | PSS2A | GGOV1 | EXST4B | Closed | 138 | -55.0953 | GT | 245.7 | PF<0.8 | YES | 0 | 0.2 | 1.033 | 2.5381 |  |  | NAN | 18 |  | GRAYS_H_18_G02 | GT (Gas Turbine) | 1
40 | NORTHWEST | 451 | NextEra Energy | Bonneville Power Admin | 47608 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 50 | -25 | 25 | 14 | -50 | [6 empty] | Closed | 45 | 4.4297 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 452 | Calpine Corporation | Bonneville Power Admin | 47641 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 251 | -77.75 | 172.75 | 14 | -251 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 189 | 172.75 | CC | 311 |  | YES | 0.001 | 0.2 | 5.395 | 16.7784 | 0.158 | 0.838 | 5.3038 | 18 |  | CALPINE_16_ST3 | CC (Combined Cycle Generic) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47675 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 207 | -60.4 | 122.8 | 30 | 6.68e-06 | 207 |  | GENQEC | PSS2B | GGOV3 | ESST4B | Closed | 138 | -18.8207 | GT | 219 |  | NO | 0 | 1e-05 | 5.08 | 11.1252 |  |  | NAN | 18 |  | MINTFARM_18_CTG | GT (Gas Turbine) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47676 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 134 | -39.7333 | 98.6667 | 30 | -134 |  |  | GENQEC | PSS2C |  | ESST4B | Closed | 107 | -11.9288 | CC | 157.6 |  | YES | 0 | 1e-05 | 6.75 | 10.638 |  |  | NAN | 13.8 |  | MINTFARM_13.2_STG | CC (Combined Cycle Generic) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47687 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 207 | -42.1 | 125.8 | 30 | -22 | 185 |  | GENQEC | PSS2B | GGOV1 | ESST4B | Closed | 167.6 | -42.1 | GT | 200 |  | NO | 0.002 | 0.202 | 5.57 | 11.14 |  |  | NAN | 18 |  | GLDNDPSE_18_CT | GT (Gas Turbine) | 1
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47688 | L | L | [5 empty] | At Mvar Limit | Limit Power Fact | [12 empty] | 0 | 110.6 | -55.9 | 90.3 | 30 | -110.6 |  |  | GENQEC | PSS2A |  | ST4C | Closed | 78.9 | -55.9 | CC | 134.5 | PF<0.8 | NO | 0.002 | 0.2 | 5.5 | 7.3975 |  |  | NAN | 13.8 |  | GLDNDPSE_18_ST | CC (Combined Cycle Generic) | L
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47799 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 50 | -16.4 | 16.4 | 937 | -50 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 41.58 | 4.8847 | W3 | 50 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BIG_HORN_0.6_G03 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 646 | Eurus Energy America Corp | Bonneville Power Admin | 47805 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 63 | -19.6611 | -19.6611 | 14 | 4.8e-07 | 63 |  | WT1G |  | WT1T |  | Closed | 33.49 | -19.6611 | W1 | 69.3 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | COMB_H_2_0.6_Z1 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47806 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 8.4 | 0 | 0 | 937 | -8.4 |  |  | WT2G |  | WT2T | WT2E | Closed | 15 | 0 | W2 | 97.86 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | LEANJUN2_0.6_PG1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47810 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 111 | -39.4 | 39.4 | 937 | -111 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 58.4 | 17.8333 | W3 | 123.58 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | LEANJUN2_0.6_PG2 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 13 | PacifiCorp - West | Bonneville Power Admin | 47866 | Z1 | Z1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 94 | -30 | 20.7 | 13 | -94 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 94 | 20.7 | W3 | 96.35 |  | NO | 0.02 | 0.19 | 0 |  |  |  | NAN | 0.575 |  | IMRIE_0.6_G1 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47872 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 102 | -33.5 | 33.5 | 937 | -102 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 102 | 1.5708 | W3 | 113.56 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BIG_HORN_0.6_G01 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47873 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 97.5 | -32.1 | 32.1 | 937 | -97.5 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 97.5 | 4.8847 | W3 | 108.55 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | BIG_HORN_0.6_G02 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 30 | Puget Sound Energy | Bonneville Power Admin | 47879 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 82.8 | -8.9 | -8.9 | 14 | -82.8 |  |  | WT2G | WT1P_B | WT2T | WT2E | Closed | 59.17 | -8.9 | W2 | 91 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | HOPKRIDG_0.6_G02 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1425 | Harvest Wind LLC | Bonneville Power Admin | 47909 | Z2 | Z2 | [15 empty] | Missing Model |  |  |  | 0 | 34.5 | -20.2 | 20.2 | 14 | -34.5 | [6 empty] | Closed | 26.29 | 4.6475 | W4 | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | Z2
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47912 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 24 | -8.4 | 8.4 | 937 | -24 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 17.53 | -3.231 | W3 | 26.72 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  | KLONDIKE_0.6_Z1 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47914 | Z2 | Z2 | [15 empty] | Missing Model |  |  |  | 0 | 22.7 | -8 | 8 | 937 | -22.7 | [6 empty] | Closed | 9.46 | -3.231 | W3 | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.575 |  |  | W3 (Wind Turbine, Type 3) | Z2
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47917 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 58.3 | -17.8 | 17.8 | 937 | -58.3 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 24.3 | -6.3946 | W3 | 60.12 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  | KLONDIKE_0.6_Z2 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47924 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 132 | -39.4 | 39.4 | 937 | -132 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 132 | -24.4592 | W3 | 146.7 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  | KLNDSCHL_0.6_Z3 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47925 | 1 | 1 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | -0.8 | 0.8 | 937 | -10 | [6 empty] | Closed | 9 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 487 | Cannon Power | Bonneville Power Admin | 47937 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 29.9 | -13 | 6.5 | 14 | -29.9 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 25 | -12.4641 | W4 | 33.23 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | ENERGIZE_0.7_G1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 337 | Turlock Irrigation District | Bonneville Power Admin | 47939 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 96.6 | -42 | 21 | 14 | -96.6 |  |  | REGC_A |  | WTGT_A | REEC_A | Closed | 44.37 | 2.5136 | W4 | 107.35 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TUOLUMNE_0.69_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 337 | Turlock Irrigation District | Bonneville Power Admin | 47940 | Z2 | Z2 | [17 empty] | Missing Sub R/X |  | 0 | 40 | 0 | 0 | 14 | -40 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 15.86 | 0 | W3 | 40 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | TUOLUMNE | W3 (Wind Turbine, Type 3) | Z2
40 | NORTHWEST | 451 | NextEra Energy | Bonneville Power Admin | 47944 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 25.1 | -8.6744 | -8.6744 | 14 | -0.3 | 24.8 |  | WT1G |  | WT1T |  | Closed | 13.24 | -8.6744 | W2 | 27.3 |  | YES | 0 | 0.2 | 0 |  |  |  | NAN | 0.69 |  | VANSYCLE_0.69_G1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1458 | Energy Northwest Packwood | Bonneville Power Admin | 47948 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 32.5 | 0 | 0 | 14 | -0.5 | 32 |  | WT1G |  | WT1T |  | Closed | 17.1 | 0 | W1 | 35.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | NINECNYN_0.69_Z1 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1458 | Energy Northwest Packwood | Bonneville Power Admin | 47952 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 31.2 | 0 | 0 | 14 | -0.2 | 31 |  | WT1G |  | WT1T |  | Closed | 16.52 | 0 | W1 | 34.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | NINECNYN_0.69_Z2 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1458 | Energy Northwest Packwood | Bonneville Power Admin | 47956 | Z1 | Z1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 32.5 | -15 | 12 | 14 | -32.5 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 27 | -15 | W4 | 33.6 |  | NO | 0 | 0.79 | 0 |  |  |  | NAN | 0.6 |  | NINECNYN_0.69_Z3 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47974 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 100.8 | -32.624 | -32.624 | 937 | -100.8 |  |  | WT2G |  | WT2T | WT2E | Closed | 68.34 | -32.624 | W2 | 109.25 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | HAYCANYN_0.6_Z1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 47975 | Z1 | Z1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 98.7 | -38.1224 | -38.1224 | 937 | -98.7 |  |  | WT2G |  | WT2T | WT2E | Closed | 82.5 | -38.1224 | W2 | 106.972 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | STAR_PT_0.6_Z1 | W2 (Wind Turbine, Type 2) | Z1 |  | PSS Exempt
40 | NORTHWEST | 1425 | Harvest Wind LLC | Bonneville Power Admin | 47981 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 64.4 | -35.8 | 35.8 | 14 | -64.4 |  |  | REGC_A |  |  | REEC_A | Closed | 34.23 | -11.5858 | W4 | 72 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | HARVESTW_0.6_Z1 | W4 (Wind Turbine, Type 4) | Z1 |  | PSS Exempt
40 | NORTHWEST | 472 | Condon Wind Power LLC | Bonneville Power Admin | 47989 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 25 | 0 | 0 | 14 | 25 | 50 |  | WT1G |  | WT1T |  | Closed | 20.79 | 0 | W1 | 55 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | CONDWIND_0.6_G01 | W1 (Wind Turbine, Type 1) | Z1 |  | PSS Exempt
40 | NORTHWEST | 491 | Invenergy LLC | Bonneville Power Admin | 47995 | Z1 | Z1 | [17 empty] | Missing Sub R/X |  | 0 | 72 | -25.6 | 25.6 | 14 | -72 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 72 | 17.7443 | W3 | 82.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.58 |  | HORN_BTE_0.6_G1 | W3 (Wind Turbine, Type 3) | Z1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 38054 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 4.2 | 0 | 0 | 999 | -4.2 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 4.42 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 60 |  |  | PV (Photovoltaic) | 1
30 | PG AND E | 334 | Modesto Irrigation District |  | 38207 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 26.32 | -8.08 | 9.54 | 888 | -26.32 |  |  | REGC_A |  |  | REEC_B | Closed | 16 | -4.9424 | PV | 28.69 |  | YES | 0 | 1e-05 | 0 |  |  |  | NAN | 0.34 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48189 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 8.8 | -5.5 | 6 | 29 | -8.8 |  |  | GENQEC |  |  | ESST4B | Closed | 8 | -0.81047 | HY | 12 | PF<-0.85 | NO | 0 | 0.168 | 1.88 | 0.2256 |  |  | NAN | 4 |  | LITTFALL_4_GEN2 | HY (Hydro) | 2
40 | NORTHWEST | 295 | Hydro Technology Systems | Avista | 48227 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 1.3 | 0 | 0 | 29 | -1.3 | [6 empty] | Closed | 1.2 | 0 | HY | 1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 11 |  | Meyers Falls UN1 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 295 | Hydro Technology Systems | Avista | 48227 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 0.3 | 0 | 0 | 29 | -0.3 | [6 empty] | Closed | 0.2 | 0 | HY | 0.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 11 |  | Meyers Falls UN2 | HY (Hydro) | 2 | Netting Exempt
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48331 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 1.8 | 2.8 | 0 | 0 | 29 | -2.8 | [6 empty] | Closed | 2.5 | 0 | HY | 2.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.4 |  | POST_FLS_2.4_G01 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48335 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 1 | 10.2 | 0 | 6 | 29 | -10.2 | [6 empty] | Closed | 3 | 1.7406 | HY | 15.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | POST STR 4.16 G02 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 291 | City of Spokane | Avista | 48433 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 2 | 0 | 1.5 | 29 | -2 | [6 empty] | Closed | 1.5 | 0 | HY | 2.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.4 |  | Upriver UN1 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 291 | City of Spokane | Avista | 48433 | 2 | 2 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 2 | 0 | 1.5 | 29 | -2 | [6 empty] | Closed | 1.5 | 0 | HY | 2.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.4 |  | Upriver UN2 | HY (Hydro) | 2 | Netting Exempt
40 | NORTHWEST | 291 | City of Spokane | Avista | 48435 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 5.8 | -4.5 | 3.6 | 29 | -5.8 | [6 empty] | Closed | 5 | 0.52478 | HY | 6.5 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | Upriver UN4 | HY (Hydro) | 1 | Netting Exempt
40 | NORTHWEST | 293 | Potlatch Paper | Avista | 48482 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 33.3 | -10 | 25 | 29 | -4.3e-07 | 33.3 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 22 | 25 | ST | 41.6 | PF<0.8 | YES | 0 | 0.275 | 1.76 | 0.73216 | 0.1765 | 0.3333 | 1.8884 | 12 |  | CLEARWTR_12_G03 | ST (Steam Turbine) | 1
40 | NORTHWEST | 293 | Potlatch Paper | Avista | 48483 | 1 | 1 | [9 empty] | Unreas H | [6 empty] | Missing PS |  |  | 0 | 50 | -10 | 55 | 29 | 0 | 50 |  | GENTPJ |  | IEEEG3_GE | EXST4B | Closed | 28 | 35.126 | ST | 66.92 | PF<0.8 | YES | 0 | 0.197 | 1.362 | 0.91145 | 0.146 | 0.368 | 2.5205 | 12 |  | CLEARWTR_12_G04 | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50170 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 22 | -3 | 5 | 10 | 8 | 30 |  | GENTPJ |  | HYGOV | ESAC8B_GE | Closed | 21.941 | 3.09 | HY | 30 |  | NO | 0.004 | 0.25 | 2.79 | 0.837 | 0.2636 | 0.7692 | 2.9181 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50293 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 6.67 | -3.23 | 3.23 | 10 | -6.67 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 6.657 | -1.2683 | HY | 12 |  | NO | 0 | 0.14 | 0.81 | 0.0972 | 0.11 | 0.6 | 5.4545 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50293 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 6.67 | -3.23 | 3.23 | 10 | -6.67 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 6.657 | -1.2683 | HY | 7.41 |  | NO | 0 | 0.14 | 0.81 | 0.060021 | 0.11 | 0.6 | 5.4545 | 4.16 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 50401 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 26 | -12.6 | 12.6 | 10 | -26 |  |  | GENROU |  |  | ESAC6A | Closed | 25.871 | 0.6971 | GT | 28.89 |  | NO | 0 | 0.15 | 2.5 | 0.72225 | 0.2 | 0.5 | 2.5 | 12.6 |  |  | GT (Gas Turbine) | 1
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50437 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 60 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.958 | 9.0108 | HY | 132 |  | NO | 0 | 0.27 | 3.2 | 4.224 | 0.21 | 0.45 | 2.1429 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50438 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 64 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.958 | 9.6115 | HY | 132 |  | NO | 0 | 0.27 | 4.74 | 6.2568 | 0.2 | 0.39 | 1.95 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50442 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 64 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.958 | 9.6115 | HY | 132 |  | NO | 0 | 0.28 | 5.25 | 6.93 | 0.14 | 0.24 | 1.7143 | 13.8 |  |  | HY (Hydro) | 6
50 | B.C.HYDRO | 201 | BCH Rio Tinto Alcan |  | 50443 | 7 | 7 | [10 empty] | Unreas Sat | [8 empty] | 0 | 120 | -41 | 60 | 10 | 12 | 132 |  | GENTPJ | PSS2A | HYG3 | EXST1_GE | Closed | 107.958 | 9.0108 | HY | 132 |  | NO | 0 | 0.27 | 3.2 | 4.224 | 0.19 | 0.42 | 2.2105 | 13.8 |  |  | HY (Hydro) | 7
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 50845 | B | B | [10 empty] | Unreas Sat | [8 empty] | 0 | 28.8 | -10 | 14 | 10 | 3.2 | 32 |  | GENTPJ | PSS2A | GGOV1 | ESST1A_GE | Open | 0 | 0 | CC | 32 |  | NO | 0 | 0.22 | 2.24 | 0.7168 | 0.08 | 0.18 | 2.25 | 13.8 |  |  | CC (Combined Cycle Generic) | B
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50922 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 29 | -18.75 | 18.75 | 10 | 2.2 | 31.2 |  | GENTPJ | IEEEST | HYGOV | EXST1_GE | Closed | 28.918 | -0.89391 | HY | 31.2 | PF<-0.85 | NO | 0 | 0.215 | 3.221 | 1.005 | 0.175 | 0.542 | 3.0971 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50925 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 29 | -18.75 | 18.75 | 10 | 2.2 | 31.2 |  | GENTPJ | IEEEST | HYGOV | EXST1_GE | Closed | 28.918 | -0.89391 | HY | 31.2 | PF<-0.85 | NO | 0 | 0.215 | 3.221 | 1.005 | 0.175 | 0.542 | 3.0971 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 50952 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 15 | -9.95 | 9.95 | 10 | -15 | [6 empty] | Closed | 15 | 7.2933 | WT | 20 | PF<-0.85 | NO | 0 | 0.74 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 318684 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 0.445 | 0 | 0 | 999 | -0.445 |  |  | MOTOR1 |  |  |  | Closed | 0.445 | 0 | HY | 0.45 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 4.16 |  | HATLOS_6_LSCRK unit 2 | HY (Hydro) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365364 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 20 | -9.69 | 9.69 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 22.222 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.8 |  | Q0653B SPV | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365374 | 1 | 1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20 | -9.165 | 9.165 | 999 | -20 |  |  | REGC_A |  |  | REEC_B | Closed | 14 | 9.165 | P4 | 22.222 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.8 |  | Q0654 SPV | P4 (Photovoltaic, Tracking) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51037 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15 | -11.25 | 11.25 | 10 | -15 |  |  | GENROU |  |  | EXST1_GE | Open | 0 | 0 | ST | 18.8 | PF<-0.85 | NO | 0 | 0.2 | 2.04 | 0.38352 | 0.065 | 0.305 | 4.6923 | 13.2 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51037 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 43.2 | -15 | 35 | 10 | -43.2 |  |  | GENROU | WSCCST |  | ESAC2A | Open | 0 | 0 | ST | 54 | PF<0.8 | NO | 0 | 0.2 | 2.11 | 1.1394 | 0.082 | 0.223 | 2.7195 | 13.2 |  |  | ST (Steam Turbine) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51039 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 276.5 | -116 | 151 | 10 | -1.049e-05 | 276.5 |  | GENROU | PSS2A | GGOV1 | EXST1_GE | Closed | 275.129 | -12.2599 | CC | 290 |  | NO | 0 | 0.17 | 7.48 | 21.692 | 0.038 | 0.104 | 2.7368 | 21 |  |  | CC (Combined Cycle Generic) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51043 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 5.5 | -2.6 | 2.6 | 10 | -5.5 |  |  | GENTPJ |  |  | EXAC8B | Closed | 5.478 | -2.6 | HY | 5 |  | NO | 0 | 0.24 | 2.2 | 0.11 | 0.2 | 0.4 | 2 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51054 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 3.501 | -1.695 | 1.695 | 10 | -3.501 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 3.499 | 0.27259 | HY | 4.3 |  | NO | 0 | 0.14 | 0.81 | 0.03483 | 0.11 | 0.6 | 5.4545 | 4.16 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51055 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 29.52 | -14.286 | 14.286 | 10 | -29.52 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 29.506 | 0.24363 | HY | 34.81 |  | NO | 0 | 0.23 | 1.72 | 0.59873 | 0.064 | 1.18 | 18.4375 | 25.2 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51104 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 21 | -12.6 | 12.6 | 10 | 3 | 24 |  | GENROU | PSS2A | IEEEG1_GE | EXST4B | Closed | 20.3 | 0.80714 | ST | 24 |  | NO | 0 | 0.234 | 2.87 | 0.6888 | 0.065 | 0.16 | 2.4615 | 12 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51135 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 25 | -12.1 | 12.1 | 10 | -25 |  |  | GENTPJ | PSS2A |  | EXST4B | Closed | 24.892 | 2.2269 | HY | 27.8 |  | NO | 0 | 0.25 | 1.44 | 0.40032 | 0.051 | 0.11 | 2.1569 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51135 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 25 | -12.1 | 12.1 | 10 | -25 |  |  | GENTPJ | PSS2A |  | EXST4B | Closed | 24.892 | 2.2269 | HY | 27.8 |  | NO | 0 | 0.25 | 1.44 | 0.40032 | 0.06 | 0.139 | 2.3167 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51140 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 24.75 | -14 | 14 | 10 | -24.75 |  |  | GENTPJ | PSS2A |  | EXAC1 | Closed | 24.721 | -1.0848 | ST | 26.5 |  | NO | 0 | 0.35 | 5 | 1.325 | 0.075 | 0.173 | 2.3067 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51212 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.32 | -7.2 | 7.2 | 10 | -10.32 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 10.281 | -0.016122 | HY | 12 | PF<-0.85 | NO | 0 | 0.274 | 1 | 0.12 | 0.1 | 0.4 | 4 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51212 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.32 | -7.2 | 7.2 | 10 | -10.32 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 10.281 | -0.016122 | HY | 12 | PF<-0.85 | NO | 0 | 0.274 | 1 | 0.12 | 0.1 | 0.4 | 4 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51212 | 3 | 3 | [9 empty] | Unreas H | [9 empty] | 0 | 3.399 | -1.98 | 1.98 | 10 | -3.399 |  |  | GENTPJ |  |  | EXST1_GE | Closed | 3.386 | -0.016122 | HY | 3.3 |  | NO | 0 | 0.257 | 0.84 | 0.02772 | 0.1 | 0.4 | 4 | 13.8 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 1 | 1 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -6.73 | 8.41 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 12.148 | 2.0708 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 2 | 2 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -6.6 | 7.14 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 12.148 | 2.0708 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 3 | 3 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -4.36 | 6.2 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 12.148 | 2.0708 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51216 | 4 | 4 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 0 | 12.2 | -3.79 | 6.76 | 10 | 1.31 | 13.51 |  | GENTPJ | PSS2A | HYG3 |  | Closed | 12.148 | 2.0708 | HY | 13.51 |  | NO | 0 | 0.26 | 1.6 | 0.21616 | 0.22 | 0.65 | 2.9545 | 13.8 |  |  | HY (Hydro) | 4
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51240 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 17.37 | -5.9 | 8.3 | 10 | 1.93 | 19.3 |  | GENTPJ | PSS2B | HYG3 |  | Closed | 17 | -1.5923 | HY | 19.3 |  | NO | 0 | 0.234 | 2.15 | 0.41495 | 0.12 | 0.7 | 5.8333 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51240 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 0 | 17.37 | -5.9 | 8.3 | 10 | 1.93 | 19.3 |  | GENTPJ | PSS2B | HYG3 |  | Closed | 17 | -1.5923 | HY | 19.3 |  | NO | 0 | 0.234 | 2.15 | 0.41495 | 0.12 | 0.7 | 5.8333 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51246 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 5.4 | -0.26 | 0.26 | 10 | -5.4 | [6 empty] | Closed | 5.375 | 0 | HY | 5.95 |  | NO | 0 | 0.13 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 51273 | FD | FD | [11 empty] | Gen at 0.0 |  |  | Miss Turbine Type |  |  | Missing Sub R/X |  | 0 | 0 | -8 | 8 | 10 | 0 |  |  | GENROU |  |  |  | Closed | 0 | 2.3234 | UN | 8 | PF<0.8 | NO | 0 | 1e-05 | 2.4 | 0.192 | 0.05 | 0.3 | 6 | 25.2 |  |  | UN (Unknown) | FD
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51368 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 12.9 | -4.67 | 4.63 | 10 | 1.472 | 14.372 |  | GENTPJ | PSS2A | PIDGOV | EXAC8B | Closed | 12.844 | -2.3868 | HY | 14.372 |  | NO | 0 | 0.176 | 1.48 | 0.21271 | 0.266 | 0.499 | 1.8759 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 51392 | FD | FD | [11 empty] | Gen at 0.0 |  |  | Miss Turbine Type | Missing Model |  | Missing Sub R/X |  | 0 | 0 | -10 | 10 | 10 | 0 | [6 empty] | Closed | 0 | 2.2674 | UN | 10 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.65 |  |  | UN (Unknown) | FD
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 51393 | FD | FD | [11 empty] | Gen at 0.0 |  |  | Miss Turbine Type | Missing Model |  | Missing Sub R/X |  | 0 | 0 | -10 | 10 | 10 | 0 | [6 empty] | Closed | 0 | 2.2674 | UN | 10 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 2.65 |  |  | UN (Unknown) | FD
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51414 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.4 | -3.7 | 3.7 | 10 | -10.4 |  |  | GENTPJ | PSS2A |  | IEEET1 | Open | 0 | 0 | HY | 11.4 |  | NO | 0 | 0.15 | 1.622 | 0.18491 | 0.25 | 0.45 | 1.8 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51499 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 3 | -2.25 | 2.25 | 10 | -3 |  |  | GENTPJ |  |  |  | Closed | 2.986 | 0.92327 | HY | 3.75 | PF<0.8 | NO | 0 | 0.18 | 0.79 | 0.029625 | 0.154 | 0.447 | 2.9026 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51541 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16.26 | -5.99 | 8.37 | 10 | 0.49 | 16.75 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 16.189 | 0.6328 | HY | 16.75 |  | NO | 0.004 | 0.255 | 1.33 | 0.22278 | 0.185 | 0.322 | 1.7405 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51541 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16.26 | -5.99 | 8.37 | 10 | 0.49 | 16.75 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 16.189 | 0.6328 | HY | 16.75 |  | NO | 0.004 | 0.255 | 1.33 | 0.22278 | 0.203 | 0.353 | 1.7389 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 4.773 | -1.69 | 2.35 | 10 | 0.0050001 | 4.778 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 3.8 | 0.35452 | HY | 4.778 |  | NO | 0.063 | 0.151 | 0.9 | 0.043002 | 0.252 | 0.411 | 1.631 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11.042 | -4.06 | 5.67 | 10 | 0.343 | 11.385 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 10.994 | 0.35452 | HY | 11.385 |  | NO | 0.005 | 0.23 | 1.15 | 0.13093 | 0.201 | 0.328 | 1.6318 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11.042 | -4.06 | 5.67 | 10 | 0.343 | 11.385 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 10.994 | 0.35452 | HY | 11.385 |  | NO | 0.005 | 0.23 | 1.15 | 0.13093 | 0.211 | 0.345 | 1.6351 | 6.9 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51542 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11.042 | -4.06 | 5.67 | 10 | 0.343 | 11.385 |  | GENTPJ | PSS2A | HYGOV4 | ESAC7B | Closed | 10.994 | 0.35452 | HY | 11.385 |  | NO | 0.005 | 0.23 | 1.15 | 0.13093 | 0.215 | 0.352 | 1.6372 | 6.9 |  |  | HY (Hydro) | 4
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51556 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 3.5 | -1.7 | 1.7 | 10 | -3.5 |  |  | GENTPJ |  |  | EXAC8B | Closed | 3.486 | 0.55264 | HY | 3.89 |  | NO | 0 | 0.228 | 0.788 | 0.030653 | 0.091 | 0.335 | 3.6813 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51558 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 24 | -7 | 4.87 | 10 | -24 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 23.912 | 4.87 | W3 | 24 |  | NO | 0.036 | 0.221 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51559 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 24 | -7 | 4.87 | 10 | -24 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 23.912 | 4.87 | W3 | 24 |  | NO | 0.036 | 0.221 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51560 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 24 | -7 | 4.87 | 10 | -24 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 23.912 | 4.87 | W3 | 24 |  | NO | 0.036 | 0.221 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51561 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 27 | -7.88 | 5.48 | 10 | -27 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 26.897 | 5.48 | W3 | 27 |  | NO | 0.036 | 0.221 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | 4
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51562 | 5 | 5 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 24 | -7 | 4.87 | 10 | -24 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 23.912 | 4.87 | W3 | 24 |  | NO | 0.036 | 0.221 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | 5
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51563 | 6 | 6 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 21 | -6.13 | 4.26 | 10 | -21 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 20.927 | 4.26 | W3 | 21 |  | NO | 0.036 | 0.221 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | 6
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51592 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 8.5 | -2.5 | 2.5 | 10 | -8.5 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 8.465 | -0.77227 | HY | 9 |  | NO | 0 | 0.23 | 1.72 | 0.1548 | 0.064 | 1.18 | 18.4375 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51592 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 8.5 | -2.5 | 2.5 | 10 | -8.5 |  |  | GENTPJ | PSS2A |  | EXST1_GE | Closed | 8.465 | -0.77227 | HY | 9 |  | NO | 0 | 0.23 | 1.72 | 0.1548 | 0.064 | 1.18 | 18.4375 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51598 | A | A | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 28 | -18 | 18 | 10 | -28 |  |  | GENROU | PSS2A |  | EXST1_GE | Open | 0 | 0 | CC | 30 | PF<-0.85 | NO | 0 | 0.09 | 2.49 | 0.747 | 0.077 | 0.196 | 2.5455 | 13.8 |  |  | CC (Combined Cycle Generic) | A
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51599 | B | B | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 13 | -18 | 18 | 10 | -13 |  |  | GENROU | PSS2A |  | EXST1_GE | Open | 0 | 0 | CC | 30 | PF<0.8 | NO | 0 | 0.09 | 2.49 | 0.747 | 0.077 | 0.196 | 2.5455 | 13.8 |  |  | CC (Combined Cycle Generic) | B
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51719 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Closed | 1.99 | -0.2093 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 3
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51719 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Closed | 1.99 | -0.2093 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 4
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51719 | D2 | D2 | [9 empty] | Unreas H | [9 empty] | 0 | 3 | -1.19 | 2.286 | 10 | -3 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 3.81 | PF<0.8 | NO | 0 | 0.16 | 0.936 | 0.035662 | 0.1364 | 0.44 | 3.2258 | 12.5 |  |  | IC (Internal Combustion) | D2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51720 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Closed | 1.99 | -0.26816 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51720 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 2 | -1.47 | 1.47 | 10 | -2 |  |  | GENROU |  |  |  | Closed | 1.99 | -0.26816 | IC | 2.46 | PF<-0.85 | NO | 0 | 0.237 | 1.08 | 0.026568 | 0.27 | 0.67 | 2.4815 | 12.5 |  |  | IC (Internal Combustion) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51720 | D1 | D1 | [9 empty] | Unreas H | [9 empty] | 0 | 3 | -1.19 | 2.286 | 10 | -3 |  |  | GENROU |  |  |  | Open | 0 | 0 | IC | 3.81 | PF<0.8 | NO | 0 | 0.16 | 0.936 | 0.035662 | 0.1364 | 0.44 | 3.2258 | 12.5 |  |  | IC (Internal Combustion) | D1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 51739 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 32.63 | -4.19 | 12.15 | 10 | 3.62 | 36.25 |  | GENROU | PSS2B | GGOV1 | EXST2A | Open | 0 | 0 | ST | 36.25 |  | NO | 0 | 0.157 | 2.6 | 0.9425 | 0.04 | 0.13 | 3.25 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 51782 | 2 | 2 | [11 empty] | Gen at 0.0 |  |  |  | Missing Model |  |  |  | -8 | 0 | -9.1 | 9.1 | 10 | 0 | [6 empty] | Closed | 0 | 0.34985 | MP | 8 | PF<0.8 | NO | 0 | 0.25 | 0 |  |  |  | NAN | 4.16 |  |  | MP (Motor/Pump) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51800 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 4.2 | -1.639 | 3.15 | 10 | -4.2 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 4.187 | -1.639 | HY | 5.25 | PF<0.8 | NO | 0 | 0.186 | 1.46 | 0.07665 | 0.085 | 0.354 | 4.1647 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 51859 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 1 | -0.376 | 0.376 | 10 | -1 | [6 empty] | Closed | 1 | 0 | PV | 1.11 |  | NO | 0 | 0.74 | 0 |  |  |  | NAN | 0.38 |  |  | PV (Photovoltaic) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54014 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 6 | 18 | -10.5 | 13.6 | 76 | 3.111 | 21.111 |  | GENTPJ |  | IEEEG1_GE | ESAC7B | Closed | 17.1 | -6.2232 | ST | 21.111 | PF<0.8 | NO | 0 | 0.13 | 3 | 0.63333 | 0.1395 | 0.3571 | 2.5599 | 13.8 |  |  | ST (Steam Turbine) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54033 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -0.5 | 8.4 | -2.8 | 4.1 | 76 | 0.9 | 9.3 |  | GENTPJ |  | IEEEG3_GE | EXDC1 | Open | 0 | 0 | HY | 9.3 |  | NO | 0.002 | 0.21 | 4.2 | 0.3906 | 0.328 | 0.684 | 2.0854 | 13.2 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54054 | G1 | G1 | [16 empty] | Missing PS |  |  | 0 | 100 | -37.5 | 49.06 | 76 | 0 | 100 |  | GENQEC |  | GGOV1 | EXST2A | Open | 0 | 0 | GT | 110.556 |  | NO | 0.002 | 2.346 | 4.97 | 5.4946 |  |  | NAN | 14.4 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54102 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 60 | -19.7 | 29.1 | 76 | 6.7 | 66.7 |  | GENTPJ | PSS2B | HYGOV | ESDC4B | Closed | 25.9 | 2.5293 | HY | 66.7 |  | NO | 0.003 | 0.28 | 3.52 | 2.3478 | 0.21 | 0.625 | 2.9762 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54108 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 60 | -19.4 | 28.6 | 76 | -2.38e-06 | 60 |  | GENTPJ | PSS2B | HYGOV | ESAC8B_GE | Closed | 25.9 | 2.0991 | HY | 65.5 |  | NO | 0.002 | 0.34 | 3.7 | 2.4235 | 0.186 | 0.599 | 3.2204 | 13.8 |  |  | HY (Hydro) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54151 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 160 | -54.4 | 80.2 | 76 | 5 | 165 |  | GENTPJ | PSS2A | G2WSCC | EXAC8B | Closed | 14.3861 | 1.0987 | HY | 184 |  | NO | 0.002 | 0.242 | 3.65 | 6.716 | 0.328 | 0.684 | 2.0854 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54189 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -15 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3 | 0 | MP | 100 |  | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54189 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -15 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3 | 0 | MP | 100 |  | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54196 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 4.08 | -1.3 | 1.9 | 76 | 0.42 | 4.5 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.4 | 1.9 | HY | 4.5 |  | NO | 0.002 | 0.2 | 3.22 | 0.1449 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54196 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 4.08 | -1.3 | 1.9 | 76 | 0.42 | 4.5 |  | GENTPJ |  | IEEEG3_GE | IEEET1 | Closed | 1.4 | 1.9 | HY | 4.5 |  | NO | 0.002 | 0.2 | 3.22 | 0.1449 | 0.17 | 0.55 | 3.2353 | 12 |  |  | HY (Hydro) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54222 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 11 | -3.3 | 4.9 | 76 | 0.25 | 11.25 |  | GENTPJ |  | GPWSCC | EXDC1 | Closed | 4.3 | 0.7776 | HY | 11.25 |  | NO | 0.002 | 0.25 | 3.44 | 0.387 | 0.25 | 0.536 | 2.144 | 13.2 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54366 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 22.5 | 0 | 0 | 76 | -22.5 | [6 empty] | Closed | 16.5 | 0 | WT | 25.2 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54403 | 3 | 3 | [7 empty] | PSS No Ex | [11 empty] | 142 | 512 | -164 | 280 | 76 | 74 | 586 |  | GENTPJ | PSS2A | IEEEG1_GE |  | Closed | 277.022 | 78.3132 | CA | 586 |  | NO | 0.004 | 0.277 | 2.9 | 16.994 | 0.07 | 0.25 | 3.5714 | 22 |  |  | CA (Combined Cycle Steam Part) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54424 | 2 | 2 | [16 empty] | Missing PS |  |  | 199 | 418 | -137.37 | 202.45 | 76 | -418 | [6 empty] | Open | 0 | 0 | CA | 477 |  | NO | 0.005 | 0.3 | 0 |  |  |  | NAN | 19 |  |  | CA (Combined Cycle Steam Part) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54490 | 3 | 3 | [16 empty] | Missing PS |  |  | 176 | 525 | -169.6 | 255.4 | 76 | -525 | [6 empty] | Open | 0 | 0 | CA | 586 |  | NO | 0.002 | 0.277 | 0 |  |  |  | NAN | 22 |  |  | CA (Combined Cycle Steam Part) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54491 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 322 | -104 | 200 | 76 | 160.353 | 482.353 |  | GENTPJ | PSS2A | IEEEG1_GE | EXST1_GE | Closed | 322.032 | 121.2226 | CA | 482.353 |  | NO | 0.002 | 0.25 | 3.742 | 18.0496 | 0.142 | 0.31 | 2.1831 | 20.5 |  |  | CA (Combined Cycle Steam Part) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54492 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 322 | -88 | 212 | 76 | 183.88 | 505.88 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST1A_GE | Closed | 322.127 | 118.5114 | CA | 505.882 |  | NO | 0.002 | 0.25 | 3.57 | 18.06 | 0.069 | 0.288 | 4.1739 | 20.5 |  |  | CA (Combined Cycle Steam Part) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54625 | G2 | G2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -9 | 0 | -4.1 | -4.1 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -4.5 | -4.1 | MP | 100 | PF<0.8 | NO | 0 | 0.167 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54626 | M6 | M6 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -25.6 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -13.5 | 0 | MP | 100 |  | NO | 0 | 0.233 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | M6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54627 | G1 | G1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 96 | -28.4 | 41.9 | 76 | -12 | 84 |  | GENROU | PSS2C | GGOV3 | AC7C | Closed | 83.8 | 16.6377 | GT | 96.1 |  | NO | 0.002 | 0.21 | 6.37 | 6.1216 | 0.017 | 0.224 | 13.1765 | 13.8 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54713 | 14 | 14 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 20 | 45 | -12.6 | 44.48 | 76 | 22.5 | 67.5 |  | GENROU | PSS2C | GGOV1 |  | Closed | 44.8 | 17.4194 | JE | 67.5 | PF<0.8 | NO | 0.001 | 0.19 | 1.209 | 0.81607 | 0.099 | 0.38 | 3.8384 | 13.8 |  |  | JE (Jet Engine) | 14
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365547 | RN | RN |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 24.58 | -4.42 | 6.64 | 999 | -24.58 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | PV | 25.35 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | 1257-RD | PV (Photovoltaic) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365624 | 1 | 1 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 41.88 | -21.228 | 21.228 | 999 | -41.88 |  |  | REGC_A |  |  | REEC_B | Closed | 29.316 | -11.1835 | PV | 48.7 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | Q0356 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365663 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 21.344 | -11.52 | 11.52 | 999 | -21.344 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | P4 | 24.255 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1127 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365673 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 51.83 | -27.98 | 27.98 | 999 | -51.83 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | P4 | 58.905 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1128 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365675 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 51.83 | -27.98 | 27.98 | 999 | -51.83 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | P4 | 58.905 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1128 | P4 (Photovoltaic, Tracking) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55015 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 2 | 42 | -13.805 | 35.5 | 76 | 16.588 | 58.588 |  | GENQEC | PSS2B | GGOV1 | ESAC6A | Closed | 41.3 | 8.7924 | JE | 58.588 | PF<0.8 | NO | 0.002 | 0.144 | 1.8 | 1.0546 |  |  | NAN | 13.8 |  |  | JE (Jet Engine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55035 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 47 | -18.3 | 34.9 | 76 | 1.2e-07 | 47 |  | GENQEC | PSS2C | GGOV3 | AC8C | Closed | 36.3 | -18.3 | JE | 58.59 |  | NO | 0.002 | 0.162 | 2.3 | 1.3476 |  |  | NAN | 13.8 |  |  | JE (Jet Engine) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55087 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 5 | 23.3 | -7.657 | 11.28 | 76 | 6.2 | 29.5 |  | (GENTPJ) | (PSS2A) | (GGOV1) | (EXAC8B) | Closed | 10.8 | 6.0637 | CC | 29.5 |  | NO | 0.002 | 0.14 | 0 |  | 0.282 | 0.906 | 3.2128 | 13.8 |  |  | CC (Combined Cycle Generic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365936 | 1 | 1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 9.535 | -9.98 | 9.98 | 999 | -9.535 |  |  | REGC_A |  |  | REEC_B | Closed | 6.6745 | -0.66362 | PV | 14.123 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.12 |  |  | PV (Photovoltaic) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55482 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 143.885 | 408 | -126 | 178.8 | 76 | 57 | 465 |  | GENTPJ | PSS2A | IEEEG1_GE |  | Closed | 146.3 | 93.1965 | CA | 465 |  | NO | 0.005 | 0.298 | 2.43 | 11.2995 | 0.07 | 0.3 | 4.2857 | 19 |  |  | CA (Combined Cycle Steam Part) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55487 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 143.885 | 408 | -131 | 170 | 76 | 57 | 465 |  | GENTPJ | PSS2A | IEEEG1_GE |  | Closed | 148.2 | -20.6548 | CA | 465 |  | NO | 0.003 | 0.32 | 2.43 | 11.2995 | 0.093 | 0.325 | 3.4946 | 19 |  |  | CA (Combined Cycle Steam Part) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55496 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 36 | 166.3 | -42 | 78 | 76 | 17 | 183.3 |  | GENTPJ | PSS2A | IEEEG1_GE | ESST1A_GE | Closed | 36.6 | 18.1173 | CA | 183.3 |  | NO | 0.001 | 0.18 | 3 | 5.499 | 0.056 | 0.16 | 2.8571 | 16 |  |  | CA (Combined Cycle Steam Part) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55516 | G1 | G1 | [6 empty] | Limit Power Fact |  |  | Unreas H | [9 empty] | 0 | 45 | -15.77 | 38.5 | 76 | 22.5 | 67.5 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 67.5 | PF<0.8 | NO | 0 | 0.17 | 1.25 | 0.84375 | 0.11 | 0.32 | 2.9091 | 13.8 |  |  | JE (Jet Engine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55695 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 15 | 86 | -35.1 | 45.1 | 76 | -86 |  |  | GENROU | PSS2B |  | ESAC7B | Closed | 55.3 | 45.1 | CC | 107.5 |  | NO | 0 | 0.156 | 2.11 | 2.2682 | 0.11 | 0.22 | 2 | 13.8 |  |  | CC (Combined Cycle Generic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55715 | 15 | 15 | [7 empty] | PSS No Ex | [11 empty] | 17 | 43 | -14.1 | 22 | 76 | 28.176 | 71.176 |  | GENROU | PSS2C | GGOV1 |  | Closed | 42.8 | 17.3064 | JE | 71.18 |  | NO | 0.005 | 0.144 | 1.193 | 0.84918 | 0.121 | 0.485 | 4.0083 | 13.8 |  |  | JE (Jet Engine) | 15
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55734 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | -13.05 | 0 | -4.7 | 6.5 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.5 | -1.9629 | MP | 14.9 | PF<0.8 | NO | 0.009 | 0.28 | 0.904 | 0.1347 | 0.1 | 0.3 | 3 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55793 | G1 | G1 | [9 empty] | Unreas H | [9 empty] | 20 | 45.8 | -15.4 | 22.69 | 76 | -4.3e-07 | 45.8 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 36.2 | 9.1234 | GT | 76.941 |  | NO | 0.006 | 0.156 | 1.341 | 1.0318 | 0.11 | 0.49 | 4.4545 | 13.8 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56085 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.9 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56134 | 5 | 5 | [9 empty] | Unreas H | [9 empty] | 0 | 3.4 | -1.1 | 1.6 | 76 | -1.8e-07 | 3.4 |  | GENTPJ |  | GGOV1 | EXDC2_GE | Open | 0 | 0 | IT | 3.4 |  | NO | 0 | 0.287 | 0.785 | 0.02669 | 0.17 | 0.55 | 3.2353 | 6.9 |  |  | IT (Internal Combustion Turbo Charged) | 5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56185 | M1 | M1 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.7 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56209 | 16 | 16 | [9 empty] | Unreas H | [9 empty] | -10 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.5 | 0 | MP | 100 |  | NO | 0 | 0.275 | 0.882 | 0.882 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 16 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56210 | 15 | 15 | [9 empty] | Unreas H | [9 empty] | -8 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.5 | 0 | MP | 100 |  | NO | 0 | 0.275 | 0.882 | 0.882 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 15 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56241 | G3 | G3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 11.5 | -4 | 7 | 76 | 1.5 | 13 |  | GENROU |  | GPWSCC | EXAC1 | Closed | 9.5 | 2.1509 | ST | 13 |  | NO | 0 | 0.19 | 11.3 | 1.469 | 0.2 | 0.6 | 3 | 13.8 |  |  | ST (Steam Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56241 | G4 | G4 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 11.5 | -4 | 7 | 76 | 1.5 | 13 |  | GENROU |  | GPWSCC | EXAC1 | Closed | 9.5 | 2.1509 | ST | 13 |  | NO | 0 | 0.19 | 11.3 | 1.469 | 0.2 | 0.6 | 3 | 13.8 |  |  | ST (Steam Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56266 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -26.35 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -19.5 | 0 | MP | 28 |  | NO | 0.004 | 0.21 | 1.2 | 0.336 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56272 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 8.5 | -2.8 | 4.1 | 76 | -8.5 | [6 empty] | Closed | 7.9 | -1.6459 | W4 | 9.4 |  | NO | 0 | 0.232 | 0 |  |  |  | NAN | 25 |  |  | W4 (Wind Turbine, Type 4) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56308 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 45 | -28 | 28 | 76 | -45 |  |  | REGC_A |  |  | REEC_A | Closed | 6 | 17.2244 | WS | 53 | PF<-0.85 | NO | 0.3 | 1.2 | 0 |  |  |  | NAN | 0.72 |  |  | WS (Wind Turbine, Offshore) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56320 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 11.5 | -4 | 7 | 76 | -11.5 | [6 empty] | Closed | 8.2 | -3.2279 | GT | 13.5 |  | NO | 0 | 0.19 | 0 |  |  |  | NAN | 13.8 |  |  | GT (Gas Turbine) | G1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365940 | 2 | 2 |  |  |  | Unapproved Gen Model | [13 empty] | Missing Sub R/X |  | 0 | 2.88 | -3.01 | 3.01 | 999 | -2.88 |  |  | REGC_A |  |  | REEC_B | Closed | 2.016 | -0.41626 | PV | 4.264 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.12 |  |  | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366367 | RE | RE |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 30.33 | -16.75 | 16.75 | 999 | -30.33 |  |  | REGC_A |  |  | REEC_B | Open | 0 | 0 | P4 | 29.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | 1501-WD | P4 (Photovoltaic, Tracking) | RE
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56367 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 8.75 | -4.238 | 4.238 | 76 | -8.75 | [6 empty] | Closed | 8.1 | 4.2006 | WT | 8.75 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 13.8 |  |  | WT (Wind Turbine) | G1
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48166 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | -24.7 | -24.6 | 6.5 | 6.5 | 29 | 24.6 |  |  | GENROU |  |  | SEXS_GE | Closed | -24.6 | 6.5 | MP | 24.608 | PF<0.8 | NO | 0 | 0.3 | 5.01 | 1.2329 | 0.05 | 0.3 | 6 | 13.8 |  | Inland Empire Paper UN1 | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56401 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 24.5 | -2.7643 | -2.7643 | 76 | -24.5 |  |  | REGC_A |  |  |  | Closed | 19.4 | -2.764 | PV | 24.75 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56402 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 16.2 | -1.2793 | -1.2793 | 76 | -16.2 |  |  | GENROU |  |  |  | Closed | 6.3 | -1.279 | W1 | 18 |  | NO | 0 | 0.302 | 3 | 0.54 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56402 | 3 | 3 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 14.4 | -1.1371 | -1.1371 | 76 | -14.4 |  |  | GENROU |  |  |  | Closed | 5.6 | -1.137 | W1 | 16 |  | NO | 0 | 0.302 | 3 | 0.48 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56436 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | 0.082888 | GT | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 6.9 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56436 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | 0.082888 | GT | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 6.9 |  |  | GT (Gas Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56436 | G3 | G3 | [15 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | 0.082888 | GT | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 6.9 |  |  | GT (Gas Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56436 | G4 | G4 | [15 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.335 | 0.082888 | GT | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 6.9 |  |  | GT (Gas Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56436 | G5 | G5 | [15 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.3 | 0.082888 | GT | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 6.9 |  |  | GT (Gas Turbine) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56436 | G6 | G6 | [15 empty] | Missing Model |  |  |  | 0 | 3.335 | -1.096 | 1.615 | 76 | -3.335 | [6 empty] | Closed | 3.3 | 0.082888 | GT | 4.145 |  | NO | 0 | 0.189 | 0 |  |  |  | NAN | 6.9 |  |  | GT (Gas Turbine) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56516 | G2 | G2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 101 | -24.88 | 36.39 | 76 | 26.28 | 127.28 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Open | 0 | 0 | CC | 127.28 |  | NO | 0 | 0.121 | 2.503 | 3.1858 | 0.047 | 0.123 | 2.617 | 13.8 |  |  | CC (Combined Cycle Generic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M2 | M2 | [15 empty] | Missing Model |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Closed | -1.9 | -1.559 | MP | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | MP (Motor/Pump) | M2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M3 | M3 | [15 empty] | Missing Model |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Closed | -1.9 | -1.559 | MP | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | MP (Motor/Pump) | M3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M4 | M4 | [15 empty] | Missing Model |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Closed | -1.8 | -1.559 | MP | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | MP (Motor/Pump) | M4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56609 | M5 | M5 | [15 empty] | Missing Model |  |  |  | -5.22 | 0 | -1.559 | -1.559 | 76 | 0 | [6 empty] | Closed | -1.9 | -1.559 | MP | 5.686 | PF<0.8 | NO | 0.004 | 0.216 | 0 |  |  |  | NAN | 6.9 |  |  | MP (Motor/Pump) | M5
40 | NORTHWEST | 29 | Avista Corp. | Avista | 48168 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | -24.7 | -24.6 | 6.5 | 6.5 | 29 | 24.6 |  |  | GENROU |  |  | SEXS_GE | Closed | -24.6 | 6.5 | MP | 24.608 | PF<0.8 | NO | 0 | 0.3 | 5.01 | 1.2329 | 0.05 | 0.3 | 6 | 13.8 |  | Inland Empire Paper UN2 | MP (Motor/Pump) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50975 | 1 | 1 |  |  |  | Unapproved Gen Model | [7 empty] | Gen at 0.0 |  |  |  |  | Missing PS |  |  | 0 | 0 | -80 | 131 | 10 | 0 |  |  | GENTPJ |  |  | ESURRY | Closed | 0 | -6.3791 | ST | 180 | PF<0.8 | NO | 0.003 | 0.2 | 1.55 | 2.79 | 0.126 | 0.54 | 4.2857 | 16.5 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50977 | 3 | 3 |  |  |  | Unapproved Gen Model | [7 empty] | Gen at 0.0 |  |  |  |  | Missing PS |  |  | 0 | 0 | -80 | 131 | 10 | 0 |  |  | GENTPJ |  |  | ESURRY | Closed | 0 | -6.5456 | ST | 180 | PF<0.8 | NO | 0.003 | 0.2 | 1.55 | 2.79 | 0.126 | 0.54 | 4.2857 | 16.5 |  |  | ST (Steam Turbine) | 3
50 | B.C.HYDRO | 10 | British Columbia Hydro Auth. |  | 50978 | 4 | 4 |  |  |  | Unapproved Gen Model | [7 empty] | Gen at 0.0 |  |  |  |  | Missing PS |  |  | 0 | 0 | -80 | 131 | 10 | 0 |  |  | GENTPJ |  |  | ESURRY | Closed | 0 | -6.5778 | ST | 180 | PF<0.8 | NO | 0.003 | 0.2 | 1.55 | 2.79 | 0.126 | 0.54 | 4.2857 | 16.5 |  |  | ST (Steam Turbine) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54789 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 97.7 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54798 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 3 | 122.32 | -72.6 | 72.6 | 76 | -122.32 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 3.2 | -72.3985 | W4 | 66.7 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W4 (Wind Turbine, Type 4) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56785 | M2 | M2 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.7 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54846 | G4 | G4 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 16 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54848 | G5 | G5 |  |  |  | Unapproved Gen Model | [15 empty] | 0.675 | 14.4 | -6.8 | 7 | 76 | -14.4 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 14.4 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 54852 | G6 | G6 |  |  |  | Unapproved Gen Model | [15 empty] | 0.675 | 14.4 | -7 | 7 | 76 | -14.4 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 14.4 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 55328 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 40.8 | -11.4 | 7.9 | 76 | -40.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 2.5 | -0.18619 | W3 | 39.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56941 | M1 | M1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -32.49 | 0 | -15.7 | -15.7 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -4.6 | -15.7 | MP | 28 | PF<0.8 | NO | 0 | 0.2 | 1.2 | 0.336 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | M1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57210 | 21 | 21 | [9 empty] | Unreas H | [9 empty] | -6.5 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.5 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 21 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57210 | 22 | 22 | [9 empty] | Unreas H | [9 empty] | -5.4 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 22 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57233 | 11 | 11 | [6 empty] | Limit Power Fact | [12 empty] | 2 | 22 | -13 | 27 | 76 | 11.8 | 33.8 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | ST | 33.8 | PF<0.8 | NO | 0.004 | 0.147 | 1.86 | 0.62868 | 0.119 | 0.374 | 3.1429 | 13.8 |  |  | ST (Steam Turbine) | 11
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57265 | 51 | 51 | [9 empty] | Unreas H | [9 empty] | -11.6 | 0 | -7.2 | -7.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -11.6 | -7.2 | MP | 14 | PF<0.8 | NO | 0.008 | 0.25 | 0.95 | 0.133 | 0.06 | 0.27 | 4.5 | 13.8 |  |  | MP (Motor/Pump) | 51
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57274 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 207 | -86.77 | 157.033 | 76 | 6.68e-06 | 207 |  | GENTPJ | PSS2C | GGOV3 | ST4C | Closed | 172.8 | 35.3926 | GT | 204.5 | PF<0.8 | NO | 0.001 | 0.175 | 4.95 | 10.1227 | 0.058 | 0.25 | 4.3103 | 18 |  |  | GT (Gas Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57516 | G3 | G3 | [10 empty] | Unreas Sat | [8 empty] | 25 | 101 | -26.25 | 39.47 | 76 | 26.28 | 127.28 |  | GENROU | PSS2A | GGOV1 | ESAC7B | Open | 0 | 0 | CC | 127.28 |  | NO | 0 | 0.121 | 2.503 | 3.1858 | 0.047 | 0.123 | 2.617 | 13.8 |  |  | CC (Combined Cycle Generic) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56328 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 28.2 | -7.9 | 5.5 | 76 | -28.2 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.7 | -5.0886 | W3 | 27.5 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57535 | 2 | 2 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 26 | -8.5 | 12.6 | 76 | -26 | [6 empty] | Closed | 7.6 | 12.6 | GT | 28.9 |  | NO | 0 | 0.132 | 0 |  |  |  | NAN | 14.4 |  |  | GT (Gas Turbine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57590 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 21.6 | 0 | 0 | 76 | -21.6 | [6 empty] | Closed | 10.6 | 0 | WT | 21.6 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56338 | 1 | 1 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [13 empty] | 0 | 41.4 | -1.6651 | 1.6651 | 76 | -41.4 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 20 | -1.6651 | W3 | 44 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57834 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | -13.05 | 0 | -4.7 | 6.5 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.5 | 6.1654 | MP | 14.9 | PF<0.8 | NO | 0.009 | 0.28 | 0.904 | 0.1347 | 0.1 | 0.3 | 3 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56389 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 30 | -14.5 | 14.5 | 76 | -30 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 30 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 25 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57885 | M5 | M5 | [15 empty] | Missing Model |  |  |  | -11.19 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -6.7 | 0 | MP | 12.8 |  | NO | 0 | 0.32 | 0 |  |  |  | NAN | 6.9 |  |  | MP (Motor/Pump) | M5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57886 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 25 | -2.1374 | -2.1374 | 76 | -25 | [6 empty] | Closed | 15 | -2.137 | WT | 26.4 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56620 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58017 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 30 | -9.9 | 14.5 | 76 | 7.5 | 37.5 |  | GENROU |  | TGOV1 | ESST1A_GE | Closed | 19 | 7.4193 | OT | 37.5 |  | NO | 0 | 0.13 | 3.5 | 1.3125 | 0.065 | 0.3 | 4.6154 | 25 |  |  | OT (Other) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58030 | ST | ST | [6 empty] | Limit Power Fact | [12 empty] | 12 | 38 | -14.16 | 31.978 | 76 | -38 |  |  | GENROU | PSS2A |  | ESAC7B | Closed | 37 | 4.6854 | CC | 50.6 | PF<0.8 | NO | 0.001 | 0.174 | 4.7 | 2.3782 | 0.12 | 0.67 | 5.5833 | 14.7 |  |  | CC (Combined Cycle Generic) | ST
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58052 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -3.4 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.4 | 0 | MP | 100 |  | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58070 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 10.3 | -3.9 | 5.8 | 76 | 2.64 | 12.94 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Open | 0 | 0 | GT | 12.9 |  | NO | 0.005 | 0.173 | 0.899 | 0.11597 | 0.25 | 0.9 | 3.6 | 25 |  |  | GT (Gas Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58085 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58085 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58085 | 3 | 3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58111 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | -40.89 | 0 | 0 | 0.9 | 76 | 0 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | MP | 100 | PF<0.8 | NO | 0 | 0.16 | 3.425 | 3.425 | 0.25 | 0.38 | 1.52 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58121 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 2.521 | -1.098 | 2.193 | 76 | -2.521 | [6 empty] | Closed | 2.5 | 0.80481 | OT | 3.656 | PF<0.8 | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 25 |  |  | OT (Other) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58121 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 2.521 | -1.098 | 2.193 | 76 | -2.521 | [6 empty] | Closed | 2.5 | 0.80481 | OT | 3.656 | PF<0.8 | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 25 |  |  | OT (Other) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58124 | G1 | G1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 15 | -4.2 | 7.3 | 76 | 1 | 16 |  | GENROU |  | GGOV1 | EXAC8B | Closed | 11.9 | -0.54687 | GT | 15 |  | NO | 0 | 0.144 | 1.31 | 0.1965 | 0.01 | 0.08 | 8 | 25 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58124 | G2 | G2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 12.3 | -3.3 | 5.9 | 76 | 3.7 | 16 |  | GENROU |  | GGOV1 | EXAC8B | Closed | 11.9 | -0.54687 | GT | 15 |  | NO | 0 | 0.145 | 1.31 | 0.1965 | 0.01 | 0.08 | 8 | 25 |  |  | GT (Gas Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58124 | G3 | G3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 13.5 | -5.6 | 5.9 | 76 | 2.5 | 16 |  | GENROU |  | GGOV1 | EXAC8B | Closed | 12.3 | -0.54687 | GT | 15 |  | NO | 0 | 0.211 | 1.31 | 0.1965 | 0.01 | 0.08 | 8 | 25 |  |  | GT (Gas Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58187 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 58 | 225 | -73.95 | 108.95 | 76 | 28 | 253 |  | GENROU | PSS2C | GGOV1 | ESST4B | Closed | 127.5 | -32.0565 | GT | 253 |  | NO | 0.001 | 0.19 | 4.888 | 12.3666 | 0.09 | 0.17 | 1.8889 | 18 |  |  | GT (Gas Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58210 | G5 | G5 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 26 | -8.22 | 20.411 | 76 | 6 | 32 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 20.8 | 0.60845 | GT | 32 | PF<0.8 | NO | 0.001 | 0.201 | 8 | 2.56 | 0.13 | 0.34 | 2.6154 | 13.8 |  |  | GT (Gas Turbine) | G5 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58226 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0.3 | 3.2 | -1.1 | 1.5 | 76 | 0.4 | 3.6 |  | GENTPJ |  | GGOV1 | EXST1_GE | Closed | 1 | 0.7478 | IC | 3.6 |  | NO | 0 | 0.25 | 2 | 0.072 | 0.03 | 0.25 | 8.3333 | 4.16 |  |  | IC (Internal Combustion) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58226 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0.3 | 3.2 | -1.1 | 1.5 | 76 | -0.2 | 3 |  | GENTPJ |  | GGOV1 | EXST1_GE | Open | 0 | 0 | IC | 3 |  | NO | 0 | 0.25 | 2 | 0.06 | 0.03 | 0.25 | 8.3333 | 4.16 |  |  | IC (Internal Combustion) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58234 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 21.1 | -1.3314 | -1.3314 | 76 | -21.1 |  |  | WT2G |  | WT2T | WT2E | Closed | 7.6 | -1.331 | W4 | 21.1 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58247 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 48 | -18.5 | 36.332 | 76 | 23.176 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 29.7 | -7.4222 | JE | 71.18 | PF<0.8 | NO | 0.004 | 0.19 | 1.25 | 0.88975 | 0.07 | 0.2 | 2.8571 | 13.8 |  |  | JE (Jet Engine) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58251 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 40.8 | -17.3 | 49.4 | 76 | 7.6e-07 | 40.8 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 33.6 | -12.1713 | JE | 71.18 | PF<0.8 | NO | 0.002 | 0.181 | 1.176 | 0.83708 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58259 | S1 | S1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -7.2 | 0 | 0 | 0 | 76 | 0 |  |  | GENROU |  |  |  | Closed | -7.2 | 0 | MP | 10 |  | NO | 0.005 | 0.357 | 11.3 | 1.13 | 0.2 | 0.6 | 3 | 13.8 |  |  | MP (Motor/Pump) | S1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56621 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58266 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 16 | 0 | 0 | 76 | -16 | [6 empty] | Closed | 11.9 | 0 | WT | 18 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58269 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 0 | 7.4 | -2.4 | 3.6 | 76 | -7.4 | [6 empty] | Closed | 6.9 | -1.2135 | IC | 8.2 |  | NO | 0 | 0.232 | 0 |  |  |  | NAN | 25 |  |  | IC (Internal Combustion) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58286 | G4 | G4 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 24 | -4.7719 | -4.7719 | 76 | -24 |  |  | REGC_A |  |  | REEC_A | Closed | 23.5 | -4.772 | WT | 24.75 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58290 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 50.3 | -16.8 | 47.7 | 76 | -2.1e-06 | 50.3 |  | GENROU | PSS2B | GGOV3 | AC8C | Closed | 19.7 | 10.5757 | JE | 71.18 | PF<0.8 | NO | 0.002 | 0.213 | 1.18 | 0.83992 | 0.15 | 0.488 | 3.2533 | 13.8 |  |  | JE (Jet Engine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58297 | G9 | G9 | [10 empty] | Unreas Sat | [8 empty] | 1.4 | 93 | -30.56 | 45.04 | 76 | -93 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 66.2 | 20.9883 | GT | 103.2 |  | NO | 0.004 | 0.175 | 6.06 | 6.2539 | 0.025 | 0.348 | 13.92 | 13.8 |  |  | GT (Gas Turbine) | G9
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58320 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 13.9 | -4.7822 | -4.7822 | 76 | -13.9 | [6 empty] | Closed | 12.1 | -4.782 | WT | 16.8 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58334 | 10 | 10 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 5.25 | 9.3 | -5 | 9.7 | 76 | 2.4 | 11.7 |  | GENTPJ |  | GGOV1 | ESAC7B | Open | 0 | 0 | IT | 11.7 | PF<0.8 | NO | 0 | 0.167 | 6 | 0.702 | 0.866 | 0.295 | 0.34065 | 13.8 |  |  | IT (Internal Combustion Turbo Charged) | 10
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56623 | G3 | G3 |  |  |  | Unapproved Gen Model | [15 empty] | 0.6 | 12.8 | -6.2 | 6.2 | 76 | -12.8 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58364 | S2 | S2 | [10 empty] | Unreas Sat | [8 empty] | -7.2 | 0 | 0 | 0 | 76 | 0 |  |  | (GENROU) |  |  |  | Closed | -6.8 | 0 | MP | 8.13 |  | NO | 0.005 | 0.357 | 0 |  | 0.2 | 0.6 | 3 | 13.8 |  |  | MP (Motor/Pump) | S2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58379 | G1 | G1 | [9 empty] | Unreas H | [9 empty] | 17 | 50 | -16.43 | 24.22 | 76 | 0.4 | 50.4 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 41.7 | -12.1922 | JE | 76.941 |  | NO | 0.005 | 0.181 | 1.38 | 1.0618 | 0.07 | 0.288 | 4.1143 | 13.8 |  |  | JE (Jet Engine) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58380 | G2 | G2 | [9 empty] | Unreas H | [9 empty] | 17 | 50 | -16.43 | 24.22 | 76 | 0.4 | 50.4 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 41.7 | -12.2869 | JE | 76.941 |  | NO | 0.005 | 0.181 | 1.38 | 1.0618 | 0.07 | 0.288 | 4.1143 | 13.8 |  |  | JE (Jet Engine) | G2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58392 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 19.9 | -6.5 | 9.6 | 76 | -4.9 | 15 |  | GENTPJ | PSS2A | GGOV1 | ESAC1A | Closed | 14.5 | 9.6 | ST | 22.06 |  | NO | 0.003 | 0.363 | 10 | 2.206 | 0.119 | 0.399 | 3.3529 | 13.8 |  |  | ST (Steam Turbine) | 3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58402 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 14.4 | -1.1371 | -1.1371 | 76 | -14.4 |  |  | GENROU |  |  |  | Closed | 5.6 | -1.137 | W1 | 16 |  | NO | 0 | 0.302 | 3 | 0.48 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58402 | 4 | 4 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 18 | -1.3808 | -1.3808 | 76 | -18 |  |  | GENROU |  |  |  | Closed | 6.8 | -1.381 | W1 | 20 |  | NO | 0 | 0.302 | 3 | 0.6 | 0.05 | 0.3 | 6 | 34.5 |  |  | W1 (Wind Turbine, Type 1) | 4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58535 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 16 | -5.3 | 7.7 | 76 | -16 | [6 empty] | Closed | 5.1 | 7.7 | OT | 17.8 |  | NO | 0 | 0.137 | 0 |  |  |  | NAN | 14.4 |  |  | OT (Other) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58590 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 16.98 | 0 | 0 | 76 | -16.98 | [6 empty] | Closed | 8.8 | 0 | WT | 18 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58590 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 13.84 | 0 | 0 | 76 | -13.84 | [6 empty] | Closed | 7.2 | 0 | WT | 14.4 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58590 | G3 | G3 | [15 empty] | Missing Model |  |  |  | 0 | 19.59 | 0 | 0 | 76 | -19.59 | [6 empty] | Closed | 9.1 | 0 | WT | 21.6 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58670 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 3 | 13.7 | -4.1 | 6.1 | 76 | 0.389 | 14.089 |  | GENTPJ | PSS2A | GPWSCC | REXS | Closed | 11.9 | 3.9013 | HY | 14.089 |  | NO | 0 | 0.33 | 1.35 | 0.1902 | 0.13 | 0.22 | 1.6923 | 13.8 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58750 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 40.8 | -17.3 | 49.4 | 76 | 7.6e-07 | 40.8 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 33.4 | 31.0215 | JE | 71.18 | PF<0.8 | NO | 0.004 | 0.181 | 1.176 | 0.83708 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58780 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 2.521 | -1.098 | 2.193 | 76 | -2.521 | [6 empty] | Closed | 2.5 | 0.98863 | OT | 3.656 | PF<0.8 | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 25 |  |  | OT (Other) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58780 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 2.521 | -1.098 | 2.193 | 76 | -2.521 | [6 empty] | Closed | 2.5 | 0.98863 | OT | 3.656 | PF<0.8 | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 25 |  |  | OT (Other) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56624 | G4 | G4 |  |  |  | Unapproved Gen Model | [15 empty] | 0.75 | 16 | -7.8 | 7.8 | 76 | -16 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 17.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58985 | M3 | M3 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.7 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59083 | G1 | G1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 32.8 | 0 | 0 | 76 | -32.8 | [6 empty] | Closed | 18.3 | 0 | IC | 32.8 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 25 |  |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59109 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | -2 | 20 | -5.4443 | -5.4443 | 76 | -20 | [6 empty] | Closed | 15 | -5.444 | WT | 22.22 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59134 | G1 | G1 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 0 | 9.3 | -1.1542 | -1.1542 | 76 | -9.3 |  |  | GENTPJ |  |  |  | Closed | 8.1 | -1.154 | WT | 11.67 |  | NO | 0 | 0.167 | 0.83 | 0.096861 | 0.2 | 0.8 | 4 | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59145 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 1.8 | 6 | -2 | 2.9 | 76 | 1.2 | 7.2 |  | GENROU |  | GGOV1 | IEEET1 | Open | 0 | 0 | GT | 7.2 |  | NO | 0.003 | 0.232 | 1.5 | 0.108 | 0.03 | 0.4 | 13.3333 | 25 |  |  | GT (Gas Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59187 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 24 | 125 | -45 | 99.2 | 76 | -125 |  |  | GENROU | PSS2C |  | ESAC8B_GE | Closed | 88.6 | 9.2139 | CC | 157.6 | PF<0.8 | NO | 0 | 0.17 | 6.76 | 10.6538 | 0.13 | 0.35 | 2.6923 | 13.2 |  |  | CC (Combined Cycle Generic) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59209 | 18 | 18 | [9 empty] | Unreas H | [9 empty] | -6.95 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.5 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 18 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59209 | 19 | 19 | [9 empty] | Unreas H | [9 empty] | -6.5 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.5 | 0 | MP | 100 |  | NO | 0 | 0.247 | 0.785 | 0.785 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 19 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59209 | 20 | 20 | [9 empty] | Unreas H | [9 empty] | -4 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -3.5 | 0 | MP | 100 |  | NO | 0 | 0.25 | 0.75 | 0.75 | 0.17 | 0.55 | 3.2353 | 13.8 |  |  | MP (Motor/Pump) | 20 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59241 | 11 | 11 | [9 empty] | Unreas H | [9 empty] | -4.05 | 0 | -2 | -2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.4 | -2 | MP | 4.5 | PF<0.8 | NO | 0 | 0.3 | 0.785 | 0.035325 | 0.17 | 0.55 | 3.2353 | 4.2 |  |  | MP (Motor/Pump) | 11
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59247 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 48 | -18.5 | 36.332 | 76 | 23.176 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 29.7 | -15.3961 | JE | 71.18 | PF<0.8 | NO | 0.004 | 0.19 | 1.25 | 0.88975 | 0.07 | 0.2 | 2.8571 | 13.8 |  |  | JE (Jet Engine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59251 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 40.8 | -17.3 | 49.4 | 76 | 7.6e-07 | 40.8 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Closed | 33.6 | -12.0539 | JE | 71.18 | PF<0.8 | NO | 0.002 | 0.181 | 1.176 | 0.83708 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59272 | JC | JC | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12 | -10.5 | 11.98 | 76 | -12 | [6 empty] | Open | 0 | 0 | OT | 15 | PF<0.8 | NO | 0.002 | 0.17 | 0 |  |  |  | NAN | 25 |  |  | OT (Other) | JC
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59297 | G8 | G8 | [10 empty] | Unreas Sat | [8 empty] | 1.4 | 93 | -30.56 | 45.04 | 76 | -93 |  |  | GENTPJ | PSS2B |  | ESAC7B | Closed | 66.3 | 21.0929 | GT | 103.2 |  | NO | 0.004 | 0.175 | 6.06 | 6.2539 | 0.025 | 0.348 | 13.92 | 13.8 |  |  | GT (Gas Turbine) | G8
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59443 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 1.75 | 8 | -4.9 | 5.9 | 76 | -8 | [6 empty] | Closed | 4.5 | -1.3184 | GT | 9.8 |  | NO | 0.003 | 0.196 | 0 |  |  |  | NAN | 25 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59443 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 1.75 | 8 | -4.9 | 5.9 | 76 | -8 | [6 empty] | Closed | 4.5 | -1.3184 | GT | 9.8 |  | NO | 0.003 | 0.196 | 0 |  |  |  | NAN | 25 |  |  | GT (Gas Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59443 | G3 | G3 | [15 empty] | Missing Model |  |  |  | 0 | 7.5 | -1.5 | 1.5 | 76 | -7.5 | [6 empty] | Closed | 4.3 | -1.3184 | GT | 8.25 |  | NO | 0.002 | 0.156 | 0 |  |  |  | NAN | 25 |  |  | GT (Gas Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59476 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3 | 0.42748 | 0.42748 | 76 | -3 | [6 empty] | Closed | 3 | 0.427 | WT | 3.15 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59556 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -4.9 | 7.3 | 76 | -15 | [6 empty] | Closed | 9.7 | 1.7057 | OT | 16.7 |  | NO | 0 | 0.151 | 0 |  |  |  | NAN | 13.2 |  |  | OT (Other) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59605 | FD | FD | [15 empty] | Missing Model | Missing PS | Missing Sub R/X |  | 0 | 0 | -100 | 100 | 76 | 0 | [6 empty] | Closed | 0 | -97.6008 | SC | 100 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 23 |  |  | SC (Synchronous Condenser) | FD
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59685 | M4 | M4 | [9 empty] | Unreas H | [9 empty] | -11.19 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -6.7 | 0 | MP | 100 |  | NO | 0 | 0.32 | 1.099 | 1.099 | 0.06 | 0.27 | 4.5 | 6.9 |  |  | MP (Motor/Pump) | M4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56625 | G5 | G5 |  |  |  | Unapproved Gen Model | [15 empty] | 0.975 | 20.8 | -10.1 | 10.1 | 76 | -20.8 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 19.58 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59734 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | -13.05 | 0 | -4.7 | 6.5 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -2.5 | 6.3512 | MP | 14.9 | PF<0.8 | NO | 0.009 | 0.28 | 0.904 | 0.1347 | 0.1 | 0.3 | 3 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56634 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.018 | 39.6 | -17.1 | 20.5 | 76 | -39.6 |  |  | WT4G |  | WT4T | WT4E | Open | 0 | 0 | W4 | 44 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.4 |  |  | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56791 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0.675 | 14.4 | -7 | 7 | 76 | -14.4 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 14.4 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59841 | 12 | 12 | [9 empty] | Unreas H | [9 empty] | -4.05 | 0 | -2 | -2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.4 | -2 | MP | 4.5 | PF<0.8 | NO | 0 | 0.3 | 0.785 | 0.035325 | 0.17 | 0.55 | 3.2353 | 4.2 |  |  | MP (Motor/Pump) | 12
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59866 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -26.35 | 0 | 0 | 0 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -19.5 | 0 | MP | 28 |  | NO | 0.004 | 0.21 | 1.2 | 0.336 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59885 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.9 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59885 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.9 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59885 | 3 | 3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -8 | 0 | -4.2 | -4.2 | 76 | 0 |  |  | GENTPJ |  |  |  | Closed | -0.9 | -4.2 | MP | 100 | PF<0.8 | NO | 0 | 0.25 | 1.2 | 1.2 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | 3 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56793 | G3 | G3 |  |  |  | Unapproved Gen Model | [15 empty] | 0.6 | 12.8 | -6.2 | 6.2 | 76 | -12.8 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 12.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59934 | 2 | 2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 18.5 | -1.1737 | -1.1737 | 76 | -18.5 |  |  | WT2G |  | WT2T | WT2E | Closed | 6.7 | -1.174 | W4 | 18.5 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W4 (Wind Turbine, Type 4) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56822 | G1 | G1 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | 0 | 75.9 | -52.5 | 52.5 | 76 | -75.9 |  |  | WT4G |  | WT4T | WT4E | Closed | 17.6 | -27.4226 | W4 | 92.4 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.4 |  |  | W4 (Wind Turbine, Type 4) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59941 | M2 | M2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | -32.49 | 0 | -15.7 | -15.7 | 76 | 0 |  |  | GENTPJ |  |  | EXST1_GE | Closed | -4.6 | -15.7 | MP | 36 | PF<0.8 | NO | 0 | 0.2 | 1.2 | 0.432 | 0.03 | 0.25 | 8.3333 | 13.8 |  |  | MP (Motor/Pump) | M2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59983 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 22 | -4.2105 | -4.2105 | 76 | -22 | [6 empty] | Closed | 16.8 | -4.21 | WT | 24 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G2
60 | IDAHO | 11 | Idaho Power Company |  | 60097 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 121.8 | -57.495 | 63.36 | 11 | -1.8 | 120 |  | GENTPJ | PSS2B | HYGOV4 |  | Closed | 79.1 | 0.98198 | HY | 125 |  | YES | 0 | 0.245 | 2.682 | 3.3525 | 0.175 | 0.542 | 3.0971 | 13.8 |  | BROWNLEE_13.8_G012 | HY (Hydro) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 60203 | 1 | 1 | [11 empty] | Gen at 0.0 | [7 empty] | 0 | 17.3 | -5 | 7 | 11 | -17.3 |  |  | GENQEC |  |  | ESST4B | Closed | 0 | 4.6689 | HY | 17.5 |  | NO | 0.005 | 0.32 | 2.9 | 0.5075 |  |  | NAN | 13.8 |  | LSALMON_13.8_G13 | HY (Hydro) | 1
60 | IDAHO | 612 | Pleasant Valley Solar LLC |  | 60545 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 204.4 | -63 | 63 | 11 | -204.4 | [6 empty] | Closed | 179.9 | -1.3993 | P4 | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.64 |  | PVS1_0.6_PV | P4 (Photovoltaic, Tracking) | 1
60 | IDAHO | 612 | Pleasant Valley Solar LLC |  | 60546 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 127.3 | -41.1 | 41.1 | 11 | -127.3 | [6 empty] | Closed | 110 | -1.3993 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | PVS2_0.6_PV | PV (Photovoltaic) | 1
60 | IDAHO | 605 | US Geothermal | Bonneville Power Admin | 60807 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 10 | 0 | 0 | 11 | -10 | [6 empty] | Closed | 7.8 | 0 | BT | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  | raft_river_geo | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
60 | IDAHO | 11 | Idaho Power Company |  | 61229 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 20 | -6.6 | 6.6 | 11 | -20 |  |  | DER_A |  |  |  | Closed | 17.6 | 2.5081 | P4 | 22 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  | ELMORE-34.5_MHSR | P4 (Photovoltaic, Tracking) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64098 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 4.8 | 12 | 1 | 1 | 24 | 2.7e-07 | 12 |  | GENTPF |  | GGOV1 | EXAC1 | Closed | 8 | 1 | BT | 10 |  | NO | 0 | 0.222 | 4 | 0.4 | 0.19 | 0.676 | 3.5579 | 13.8 |  | RAG_1_2_IPP_GO | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64105 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 13.5 | -1.6 | 16.1 | 24 | 1.5 | 15 |  | GENTPF |  | GGOV1 |  | Open | 0 | 0 | BT | 18.75 | PF<0.8 | YES | 0.002 | 0.18 | 1.679 | 0.31481 | 1.084 | 1.28 | 1.1808 | 12.3 |  | STEAMBOT_12_G01 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Closed | 6.075 | 3.396 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Closed | 6 | 3.396 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Closed | 5 | 3.396 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G3 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64106 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 4.5 | 11.2 | -3.68 | 3.68 | 24 | 0.6 | 11.8 |  | GENTPF | PSS2A | GGOV1 | EXAC1 | Open | 0 | 0 | BT | 11.8 |  | NO | 0.002 | 0.161 | 4 | 0.472 | 0.19 | 0.676 | 3.5579 | 13.8 |  | CRD_IPP_GO_G4 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 4
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64150 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 7.5 | 10.97 | -1 | 12.7292 | 24 | 5.69 | 16.66 |  | GENROU |  | GGOV1 | ESAC7B | Open | 0 | 0 | BT | 18.9 | PF<0.8 | YES | 0.001 | 0.24 | 7.5 | 1.4175 | 0.212 | 0.75 | 3.5377 | 4.16 |  | BEOWAWE_4.16_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64150 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.72 | 0 | 0 | 24 | 0.28 | 2 |  | GENROU |  | GGOV1 | ESAC7B | Open | 0 | 0 | BT | 3.125 |  | YES | 0.001 | 0.15 | 1 | 0.03125 | 0.2 | 0.5 | 2.5 | 4.16 |  | BEOWAWE_4.16_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64267 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -6.25 | 18.2044 | 24 | 7.5 | 22.5 |  | GENTPF |  | GGOV1 |  | Closed | 3.031 | -0.49267 | BT | 22.5 | PF<0.8 | YES | 0.002 | 0.15 | 1.6 | 0.36 | 1.084 | 1.28 | 1.1808 | 13.2 |  | JERSEYV_13.8_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64267 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 1 | 7.5 | -1.7892 | 7.5189 | 24 | 15 | 22.5 |  | GENTPF |  | GGOV1 |  | Closed | 2.869 | -0.49267 | BT | 22.5 | PF<0.8 | YES | 0.003 | 0.144 | 1.6 | 0.36 | 1.084 | 1.28 | 1.1808 | 13.2 |  | JERSEYV_13.8_GEN2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64311 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 5 | 20 | -7 | 19.372 | 24 | 5 | 25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 7.8 | -0.54097 | BT | 25 | PF<0.8 | YES | 0 | 0.133 | 1.76 | 0.44 | 0.065 | 0.17 | 2.6154 | 12.47 |  | ORMAT_13.8_G2A | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64350 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 2.2 | 22 | -7 | 8.4 | 24 | -22 | [6 empty] | Closed | 15 | -0.054571 | PV | 28.13 |  | NO | 0 | 0.02 | 0 |  |  |  | NAN | 13.8 |  | CRD_IPP_PV_G1 | PV (Photovoltaic) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64467 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -1.1078 | 13.7191 | 24 | 3.75 | 18.75 |  | GENTPF |  | GGOV1 |  | Closed | 9.3021 | 6.2944 | BT | 18.75 | PF<0.8 | YES | 0.002 | 0.187 | 1.679 | 0.31481 | 1.084 | 1.28 | 1.1808 | 13.8 |  | GALENA_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64467 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -1.1078 | 13.7191 | 24 | 3.75 | 18.75 |  | GENTPF |  | GGOV1 |  | Closed | 9.3021 | 6.2944 | BT | 18.75 | PF<0.8 | YES | 0.002 | 0.187 | 1.679 | 0.31481 | 1.084 | 1.28 | 1.1808 | 13.8 |  | GALENA_13.8_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64469 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 4 | 15 | -7.5 | 17.88 | 24 | 3.75 | 18.75 |  | GENTPF |  | GGOV1 | REXS | Closed | 5.5 | 4.1636 | BT | 18.75 | PF<0.8 | YES | 0 | 0.15 | 1.08 | 0.2025 | 1.084 | 1.28 | 1.1808 | 13.8 |  | DESRT_PK_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64469 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 2 | 11 | -3.168 | 11.268 | 24 | 7.75 | 18.75 |  | GENTPF |  | GGOV1 | REXS | Closed | 3.8135 | 4.1636 | BT | 18.75 | PF<0.8 | YES | 0 | 0.164 | 1.08 | 0.2025 | 1.084 | 1.28 | 1.1808 | 13.8 |  | DESRT_PK_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64502 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 12.4 | 31 | -7.5 | 15 | 24 | -31 |  |  | GENTPF | PSS2A |  | EXAC1 | Open | 0 | 0 | BT | 33 |  | NO | 0 | 0.197 | 4 | 1.32 | 0.19 | 0.676 | 3.5579 | 4.16 |  | SALTWLLS_13.8_G01 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64577 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 5 | 20 | -7 | 18.67 | 24 | 5 | 25 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 10.5 | -0.23985 | BT | 25 | PF<0.8 | YES | 0 | 0.133 | 1.76 | 0.44 | 0.065 | 0.17 | 2.6154 | 12.47 |  | ORMAT_13.8_G1A | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64593 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 20 | -7 | 8.4 | 24 | -20 | [6 empty] | Closed | 16 | 0.15522 | PV | 28.125 |  | NO | 0.004 | 0.18 | 0 |  |  |  | NAN | 13.8 |  | CRD_IPP_PV_G2 | PV (Photovoltaic) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64788 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 27.1 | -15.9104 | 23.684 | 24 | -27.1 |  |  | GENTPJ | PSS2B |  | ESAC8B_GE | Closed | 17.0913 | 12.1818 | BT | 30.235 | PF<0.8 | YES | 0.003 | 0.17 | 1.15 | 0.3477 | 0.07 | 0.17 | 2.4286 | 12.47 |  | CAITHNES_12.47_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64788 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 7.98 | -3.5285 | 4.7135 | 24 | 7.02 | 15 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 4.1087 | 3.0455 | BT | 6.9 |  | YES | 0.003 | 0.152 | 0.76 | 0.05244 | 0.096 | 0.199 | 2.0729 | 12.47 |  | CAITHNES_12.47_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64801 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 3.4 | 14.2 | -6.1836 | 17.2687 | 24 | -14.2 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 9.647 | 1.2771 | BT | 21.25 | PF<0.8 | YES | 0.003 | 0.15 | 1.17 | 0.24862 | 0.063 | 0.334 | 5.3016 | 12.47 |  | BLUEMTN_12.5_G1A | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64801 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 6.3 | 13.8 | -6.1906 | 17.3249 | 24 | -13.8 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 9.4729 | 1.2771 | BT | 21.25 | PF<0.8 | YES | 0.003 | 0.15 | 1.17 | 0.24862 | 0.063 | 0.334 | 5.3016 | 12.47 |  | BLUEMTN_12.5_G1B | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64801 | 3 | 3 | [9 empty] | Unreas H | [9 empty] | 4.6 | 11.7 | -6.2275 | 17.6197 | 24 | -11.7 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 8.5589 | 1.2771 | BT | 21.25 | PF<0.8 | YES | 0.003 | 0.15 | 1.17 | 0.24862 | 0.063 | 0.334 | 5.3016 | 12.47 |  | BLUEMTN_12.5_G1C | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64855 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 94 | 235 | -79.171 | 128.7624 | 24 | -235 |  |  | GENTPJ | PSS2B |  | REXS | Closed | 180.9 | 62.6344 | ST | 270 |  | YES | 0.001 | 0.178 | 4.13 | 11.151 | 0.283 | 0.639 | 2.258 | 18 |  | NWMNTGEN_18_G01 | ST (Steam Turbine) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64923 | 3 | 3 | [7 empty] | PSS No Ex |  |  | Unreas Sat | [8 empty] | 2 | 15 | -5.322 | 15.338 | 24 | -6e-07 | 15 |  | GENTPJ | PSS2B | GGOV1 |  | Closed | 3.7605 | 1.8003 | BT | 15 | PF<0.8 | YES | 0.003 | 0.133 | 1.5 | 0.225 | 0.031 | 0.097 | 3.129 | 12.47 |  | FRONTIRS_13.8_GEO6 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64929 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 102.58 | -24.57 | 55.28 | 24 | -102.58 |  |  | REGC_A |  |  | REEC_A | Closed | 101 | 7.246 | PV | 122.85 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | BATMNPV-G_0.63_1 | PV (Photovoltaic) | 1 |  | PSS Exempt
64 | SIERRA | 74 | Southern California Edison |  | 64931 | 2 | 2 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 25.5 | -10.95 | 13.35 | 24 | -25.5 | [6 empty] | Closed | 25.5 | 2.7963 | BT | 30 |  | YES | 0.011 | 0.21 | 0 |  |  |  | NAN | 12.47 |  | TUNGSTEN | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64945 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 5.5 | 12.4 | -4.56 | 8.06 | 24 | 2e-07 | 12.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 12.3 | 0.19847 | BT | 14.7 |  | YES | 0.002 | 0.129 | 2 | 0.294 | 0.2 | 0.67 | 3.35 | 12.47 |  | PRGATORY_12.5_GEN1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 64956 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 2 | 15 | -5.322 | 9.7358 | 24 | -6e-07 | 15 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 3.9905 | 2.064 | BT | 15 |  | YES | 0.003 | 0.133 | 3.4 | 0.51 | 0.031 | 0.097 | 3.129 | 12.47 |  | FRONTIRS_13.8_GEO3 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 3
65 | PACE | 7 | PacifiCorp - East |  | 65490 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 102.2 | 474 | -87.8286 | 220.8029 | 7 | 5 | 479 |  | GENROU | PSS2C | IEEEG1_GE |  | Closed | 450.3 | 123.0951 | CA | 525 |  | YES | 0.002 | 0.264 | 3.44 | 18.06 | 0.122 | 0.392 | 3.2131 | 24 |  |  | CA (Combined Cycle Steam Part) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65495 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 103.4 | 473 | -144.308 | 221.434 | 7 | 6 | 479 |  | GENROU | PSS2C | IEEEG1_GE |  | Closed | 449.3 | -44.2834 | CA | 525 |  | YES | 0.002 | 0.264 | 3.44 | 18.06 | 0.122 | 0.392 | 3.2131 | 24 |  |  | CA (Combined Cycle Steam Part) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65500 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 78.5 | 506.4 | -86.3667 | 206.2667 | 7 | 5.6328 | 512.0328 |  | GENROU | PSS2A | IEEEG1_GE |  | Closed | 449.8 | -47.7266 | CA | 527 |  | YES | 0.003 | 0.205 | 3.277 | 17.2698 | 0.18 | 0.4 | 2.2222 | 22 |  |  | CA (Combined Cycle Steam Part) | 1
65 | PACE | 7 | PacifiCorp - East |  | 65542 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 4 | 31 | -22 | 38 | 7 | 4.6 | 35.6 |  | GENROU | PSS2A | GGOV1 |  | Closed | 31 | 12.401 | GT | 57.41 | PF<0.8 | NO | 0.001 | 0.147 | 2.4 | 1.3778 | 0.149 | 0.76 | 5.1007 | 13.8 |  |  | GT (Gas Turbine) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 65543 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 4 | 31 | -22 | 38 | 7 | 4.6 | 35.6 |  | GENROU | PSS2A | GGOV1 |  | Closed | 31 | 12.401 | GT | 57.41 | PF<0.8 | NO | 0.001 | 0.147 | 2.4 | 1.3778 | 0.149 | 0.76 | 5.1007 | 13.8 |  |  | GT (Gas Turbine) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 65544 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 4 | 31 | -22 | 38 | 7 | 4.6 | 35.6 |  | GENROU | PSS2A | GGOV1 |  | Closed | 31 | 12.401 | GT | 57.41 | PF<0.8 | NO | 0.001 | 0.147 | 2.4 | 1.3778 | 0.149 | 0.76 | 5.1007 | 13.8 |  |  | GT (Gas Turbine) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 65680 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 0 | -40 | 75 | 7 | 0 |  |  | GENTPJ |  |  |  | Closed | 0 | 62.9623 | SC | 75 | PF<0.8 | NO | 0.001 | 0.34 | 1.05 | 0.7875 | 0.19 | 0.38 | 2 | 13.8 |  |  | SC (Synchronous Condenser) | 1 |  | PSS Exempt
65 | PACE | 8 | UAMPS |  | 66069 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 66.5 | -31.1944 | 52.0278 | 7 | -66.5 |  |  | GENTPJ | PSS2C |  | ESAC7B | Closed | 66.5 | 32.6483 | CC | 92 | PF<0.8 | YES | 0.003 | 0.157 | 3.82 | 3.5144 | 0.0657 | 0.5474 | 8.3318 | 13.8 |  |  | CC (Combined Cycle Generic) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66120 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -8.3 | 6.9364 | 7 | -10 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 5 | -5.3595 | HY | 11.11 | PF<-0.85 | YES | 0.003 | 0.11 | 2 | 0.2222 | 0 | 0 | NAN | 6.6 |  |  | HY (Hydro) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66120 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -8.3 | 6.9364 | 7 | -10 |  |  | GENTPJ |  |  | ESST1A_GE | Closed | 5 | -5.3595 | HY | 11.11 | PF<-0.85 | YES | 0.003 | 0.11 | 2 | 0.2222 | 0 | 0 | NAN | 6.6 |  |  | HY (Hydro) | 2
65 | PACE | 7 | PacifiCorp - East |  | 66125 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10 | -8.5 | 7.6 | 7 | -10 |  |  | GENTPJ |  |  | ESST1A_GE | Open | 0 | 0 | HY | 11.11 | PF<0.8 | YES | 0.003 | 0.11 | 2 | 0.2222 | 0 | 0 | NAN | 6.6 |  |  | HY (Hydro) | 1
65 | PACE | 7 | PacifiCorp - East |  | 66439 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 106 | 226 | -60.074 | 116.444 | 7 | -226 |  |  | GENROU | PSS2B |  | ESAC7B | Closed | 214.63 | 116.444 | CC | 251 |  | YES | 0.001 | 0.2 | 7.36 | 18.4736 | 0.114 | 0.489 | 4.2895 | 16.5 |  |  | CC (Combined Cycle Generic) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 56858 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 36 | -16.7 | 16.7 | 76 | -36 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 2.9 | -10.5932 | W3 | 36 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.575 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 68020 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12 | -8 | 8.9 | 7 | 2.7e-07 | 12 |  | GENTPJ |  | GGOV1 | ESAC5A | Closed | 12 | 1.5645 | GT | 14.86 | PF<-0.85 | NO | 0 | 0.157 | 1.44 | 0.21398 | 0.1 | 0.3 | 3 | 13.8 |  |  | GT (Gas Turbine) | 1
65 | PACE | 7 | PacifiCorp - East |  | 68020 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12 | -8 | 8.9 | 7 | 2.7e-07 | 12 |  | GENTPJ |  | GGOV1 | ESAC5A | Closed | 12 | 1.5645 | GT | 14.86 | PF<-0.85 | NO | 0 | 0.157 | 1.44 | 0.21398 | 0.1 | 0.3 | 3 | 13.8 |  |  | GT (Gas Turbine) | 2
65 | PACE | 7 | PacifiCorp - East |  | 68514 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 135.945 | -100.873 | 100.873 | 7 | -135.945 | [6 empty] | Open | 0 | 0 | WT | 135.945 | PF<-0.85 | NO | 0 | 999 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57534 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0.019 | 41.8 | -18.1 | 21.7 | 76 | -41.8 |  |  | WT4G |  | WT4T | WT4E | Open | 0 | 0 | W4 | 46.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.4 |  |  | W4 (Wind Turbine, Type 4) | 1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57735 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 37.7 | -22.3 | 22.3 | 76 | -37.7 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.7 | 0.60126 | W3 | 36.7 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G2 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 69707 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 60 | -18.1 | 18.1 | 7 | -60 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 27 | -18.1 | W4 | 100 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.7 |  |  | W4 (Wind Turbine, Type 4) | 1 |  | PSS EXEMPT
65 | PACE | 7 | PacifiCorp - East |  | 69790 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 59.32 | -37.8 | 37.8 | 7 | -59.32 |  |  | REGC_A |  |  | REEC_A | Closed | 56.3 | 14.0934 | PV | 63 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1 |  | PSS Exempt
65 | PACE | 7 | PacifiCorp - East |  | 69794 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 124.57 | -79.38 | 79.38 | 7 | -124.57 |  |  | REGC_A |  |  | REEC_A | Closed | 118.3 | 14.0934 | WT | 132.3 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | 1
70 | PSCOLORADO | 65 | PSColorado |  | 70106 | G4 | G4 | [5 empty] | At Mvar Limit | [13 empty] | 194 | 308 | -69 | 170 | 65 | 67 | 375 |  | GENTPJ | IEEEST | IEEEG1_GE | ESST1A_GE | Closed | 290 | 170 | ST | 448 |  | NO | 0.03 | 0.26 | 2.75 | 12.32 | 0.179 | 0.362 | 2.0223 | 22 |  | CHER_21_ | ST (Steam Turbine) | G4
70 | PSCOLORADO | 65 | PSColorado |  | 70310 | C1 | C1 | [5 empty] | At Mvar Limit | [13 empty] | 224.2 | 526 | -132.2 | 278.1 | 65 | 20.994 | 546.994 |  | GENROU | PSS2C | IEEEG1_GE | ESAC7B | Closed | 473.5305 | 278.1 | ST | 614 |  | NO | 0.004 | 0.205 | 2.13 | 13.0782 | 0.099 | 0.455 | 4.596 | 22 |  | PAWN_22_NO_1 | ST (Steam Turbine) | C1
70 | PSCOLORADO | 65 | PSColorado |  | 70314 | G1 | G1 | [7 empty] | PSS No Ex | [11 empty] | 110.3 | 131.5 | -49.5 | 54.5 | 65 | 18.5 | 150 |  | GENROU | PSS2C | GGOV1 |  | Closed | 130 | 16.3545 | GT | 150 |  | NO | 0.003 | 0.202 | 7.068 | 10.602 | 0.14 | 0.49 | 3.5 | 16 |  | MANG_15.2_GSU11 | GT (Gas Turbine) | G1
70 | PSCOLORADO | 65 | PSColorado |  | 70315 | G2 | G2 | [7 empty] | PSS No Ex | [11 empty] | 110 | 131 | -52.5 | 46 | 65 | 19 | 150 |  | GENROU | PSS2C | GGOV1 |  | Closed | 130 | 16.3545 | GT | 150 |  | NO | 0.003 | 0.202 | 7.068 | 10.602 | 0.14 | 0.49 | 3.5 | 16 |  | MANG_15.2_GSU12 | GT (Gas Turbine) | G2
70 | PSCOLORADO | 65 | PSColorado |  | 70406 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 60.03 | 133.4 | -69 | 111.5 | 65 | 30.3 | 163.7 |  | GENTPJ | PSS2B | GGOV3 | ESST4B | Closed | 130 | 66.5656 | CT | 206 | PF<0.8 | NO | 0.003 | 0.22 | 5.3 | 10.918 | 0.055 | 0.217 | 3.9455 | 18 |  | FSVR_18_NO_2 | CT (Combined Cycle Combustion Turbine Part) | G2
70 | PSCOLORADO | 65 | PSColorado |  | 70409 | ST | ST | [5 empty] | At Mvar Limit | [13 empty] | 53.3 | 314.8 | -127 | 153.9 | 65 | -314.8 |  |  | GENTPJ | PSS2B |  | ESST4B | Closed | 310 | 153.9 | CC | 403 |  | NO | 0.003 | 0.25 | 3.3 | 13.299 | 0.067 | 0.286 | 4.2687 | 22 |  | FSVR_22_NO_1 | CC (Combined Cycle Generic) | ST
70 | PSCOLORADO | 65 | PSColorado |  | 70485 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 4.9 | 18.8 | 0.8 | 18.3 | 65 | -1.4 | 17.4 |  | GENTPJ |  | GGOV1 | ESST2A | Open | 0 | 0 | GT | 29.6 | PF<0.8 | NO | 0.004 | 0.169 | 7.4 | 2.1904 | 0.079 | 0.281 | 3.557 | 13.8 |  | ATER_13.8_GEN1 | GT (Gas Turbine) | G1
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70487 | G4 | G4 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 12.8 | 35.3 | -0.5 | 22.8 | 65 | 6.7 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT4 | CC (Combined Cycle Generic) | G4
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70487 | G5 | G5 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 14.1 | 33 | -0.4 | 23.8 | 65 | 9 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT5 | CC (Combined Cycle Generic) | G5
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70490 | G3 | G3 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 14.8 | 37.8 | 1 | 15.7 | 65 | 4.2 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 27.8 | 15.7 | CC | 57.4 |  | NO | 0 | 0.18 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT3 | CC (Combined Cycle Generic) | G3
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70490 | ST | ST | [5 empty] | At Mvar Limit | [13 empty] | 7.4 | 45 | 0 | 22.5 | 65 | 2 | 47 |  | GENTPJ | PSS2A | IEEEG1_GE | ESAC8B_GE | Closed | 31.8 | 22.5 | CC | 52.22 |  | NO | 0 | 0.186 | 4.83 | 2.5222 | 0.11 | 0.25 | 2.2727 | 13.8 |  | JMSHAFER_13.8_ST2 | CC (Combined Cycle Generic) | ST
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70495 | G1 | G1 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 12.9 | 36.3 | 4.3 | 23.2 | 65 | 5.7 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 26.3 | 23.2 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT1 | CC (Combined Cycle Generic) | G1
70 | PSCOLORADO | 982 | Thermo Cogeneration Partnership |  | 70495 | G2 | G2 | [5 empty] | At Mvar Limit |  |  |  | Unreas H | Unreas Sat | [8 empty] | 14.8 | 35 | 4.6 | 23.2 | 65 | 7 | 42 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 25 | 23.2 | CC | 57.4 |  | NO | 0 | 0.181 | 1.176 | 0.67502 | 0.25 | 0.5 | 2 | 13.8 |  | JMSHAFER_13.8_GT2 | CC (Combined Cycle Generic) | G2
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70498 | G3 | G3 | [16 empty] | Missing PS |  |  | 17 | 34.1 | -7 | 14 | 65 | 14.9 | 49 |  | GENTPF |  | GGOV1 | EXST2A | Open | 0 | 0 | CT | 49 |  | NO | 0.005 | 0.192 | 5.84 | 2.8616 | 0.0545 | 0.657 | 12.055 | 13.8 |  | CPP1_13.8_GT3 | CT (Combined Cycle Combustion Turbine Part) | G3
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70498 | ST | ST | [16 empty] | Missing PS |  |  | 17 | 36 | -7 | 24 | 65 | 11 | 47 |  | GENTPF |  | GGOV1 | EXST2A | Open | 0 | 0 | CA | 47 |  | NO | 0.005 | 0.122 | 6.116 | 2.8745 | 0.124 | 0.55 | 4.4355 | 13.8 |  | CPP1_13.8_ST2 | CA (Combined Cycle Steam Part) | ST
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70501 | ST | ST | [16 empty] | Missing PS |  |  | 10 | 27 | -5 | 15 | 65 | 12 | 39 |  | GENTPF |  | GGOV1 | EXST2A | Open | 0 | 0 | CA | 39 |  | NO | 0 | 0.18 | 4.4 | 1.716 | 0.13 | 0.45 | 3.4615 | 13.8 |  | CPP1_13.8_ST_1 | CA (Combined Cycle Steam Part) | ST
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70553 | G5 | G5 | [6 empty] | Limit Power Fact | [12 empty] | 9.75 | 39 | -19.4 | 38.9 | 65 | 1.7 | 40.7 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 71.18 | PF<0.8 | NO | 0.005 | 0.19 | 1.2 | 0.85416 | 0.105 | 0.412 | 3.9238 | 13.8 |  | ARAP_13.2_NO_5 | JE (Jet Engine) | G5
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70553 | G6 | G6 | [6 empty] | Limit Power Fact | [12 empty] | 10 | 39.5 | -19.5 | 39.5 | 65 | 1.2 | 40.7 |  | GENTPJ | PSS1A | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 71.18 | PF<0.8 | NO | 0.005 | 0.19 | 1.2 | 0.85416 | 0.105 | 0.412 | 3.9238 | 13.8 |  | ARAP_13.2_NO_6 | JE (Jet Engine) | G6
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70556 | ST | ST | [16 empty] | Missing PS |  |  | 17 | 70 | -13 | 35 | 65 | -20 | 50 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 49.5 | -5.6196 | CA | 40 |  | NO | 0.005 | 0.132 | 4 | 1.6 | 0.124 | 0.55 | 4.4355 | 12.5 |  | CPP1_12.5_ST4 | CA (Combined Cycle Steam Part) | ST
70 | PSCOLORADO | 65 | PSColorado |  | 70563 | G2 | G2 | [5 empty] | At Mvar Limit | [13 empty] | 76.8 | 135.5 | -70.7 | 57.1 | 65 | 98.5 | 234 |  | GENROU | PSS2B | GGOV1 | ESST4B | Closed | 130 | 57.1 | GT | 234 |  | NO | 0.003 | 0.196 | 4.85 | 11.349 | 0.07 | 0.29 | 4.1429 | 18 |  | BSNG_18_GEN2 | GT (Gas Turbine) | G2
70 | PSCOLORADO | 73 | Tri-State G&T |  | 70565 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 39.5 | 67.4 | -31 | 51.2 | 65 | -0.020002 | 67.38 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 90.8 | PF<0.8 | NO | 0 | 0.135 | 6.31 | 5.7295 | 0.103 | 0.385 | 3.7379 | 13.8 |  | BARR_13.8_BRIGHTON_1 | JE (Jet Engine) | G1
70 | PSCOLORADO | 73 | Tri-State G&T |  | 70566 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 40 | 67.3 | -31.2 | 51.5 | 65 | 0.079996 | 67.38 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 90.8 | PF<0.8 | NO | 0 | 0.135 | 6.31 | 5.7295 | 0.103 | 0.385 | 3.7379 | 13.8 |  | BARR_13.8_BRIGHTON_2 | JE (Jet Engine) | G2
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70593 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 79.42 | 143.07 | -60.61 | 108.53 | 65 | 11.33 | 154.4 |  | GENTPJ | PSS2B | GGOV1 | ESST4B | Closed | 135 | 63.664 | GT | 247 | PF<0.8 | NO | 0.003 | 0.205 | 4.87 | 12.0289 | 0.068 | 0.58 | 8.5294 | 18 |  | SPIN_18_SPINDLE_G1 | GT (Gas Turbine) | G1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70704 | W1 | W1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 75 | -36.32 | 36.32 | 65 | -75 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 30 | -36.32 | W3 | 83.5 |  | YES | 0 | 0.15 | 0 |  |  |  | NAN | 0.575 |  | COGR_0.5 | W3 (Wind Turbine, Type 3) | W1
70 | PSCOLORADO | 65 | PSColorado |  | 70777 | C3 | C3 | [5 empty] | At Mvar Limit | [13 empty] | 493 | 804.9 | -122 | 167.2 | 65 | 50.1 | 855 |  | GENROU | PSS2B | IEEEG1_GE | ESST4B | Closed | 780 | 167.2 | CA | 1008 |  | NO | 0.002 | 0.266 | 3.17 | 31.9536 | 0.233 | 0.797 | 3.4206 | 27 |  | COMA_24_ | CA (Combined Cycle Steam Part) | C3
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70824 | W2 | W2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 80 | -65.699 | 65.699 | 65 | -80 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 32 | 15.3489 | W3 | 84.21 | PF<0.8 | NO | 0 | 0.8 | 0 |  |  |  | NAN | 34.5 |  | CEDARCK_34.5_WIND_UN3 | W3 (Wind Turbine, Type 3) | W2 |  | PSS Exempt
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70825 | W1 | W1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 102.5 | -71.776 | 71.776 | 65 | -102.5 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 41 | 7.6718 | W4 | 125.132 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.66 |  | CEDARCK_34.5_WIND_UN1 | W4 (Wind Turbine, Type 4) | W1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70826 | W5 | W5 | [15 empty] | Missing Model |  |  |  | 0 | 68.8 | -20.55 | 20.55 | 65 | -68.8 | [6 empty] | Closed | 27.52 | 1.9349 | W4 | 71.8 |  | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | Not_in_WSM | W4 (Wind Turbine, Type 4) | W5
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70827 | W3 | W3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15 | -10.483 | 10.483 | 65 | -15 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 6 | 0.061929 | W4 | 18.3 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.66 |  | Not_in_WSM | W4 (Wind Turbine, Type 4) | W3
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 70933 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 30.965 | -21.679 | 21.679 | 65 | -30.965 |  |  | REGC_A |  |  | REEC_A | Closed | 20.15 | -7.8518 | P3 | 37.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | Not_In_WSM | P3 (Photovoltaic, Fixed) | S1 |  | PSS Exempt
70 | PSCOLORADO | 66 | West Plains G&T |  | 71003 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 | REXS | Closed | 39 | 2.546 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT41 | JE (Jet Engine) | G1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71003 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 | REXS | Closed | 39 | 2.546 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT42 | JE (Jet Engine) | G2
70 | PSCOLORADO | 66 | West Plains G&T |  | 71004 | G1 | G1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 |  | Closed | 39 | 2.5382 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT51 | JE (Jet Engine) | G1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71004 | G2 | G2 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 0 | 40 | -27 | 40 | 65 | 8.6 | 48.6 |  | GENTPJ | PSS2B | GGOV1 |  | Closed | 39 | 2.5382 | JE | 71.176 | PF<0.8 | NO | 0.005 | 0.175 | 1.193 | 0.84913 | 0.106 | 0.336 | 3.1698 | 13.8 |  | BACUMESA_13.8_CT52 | JE (Jet Engine) | G2
70 | PSCOLORADO | 66 | West Plains G&T |  | 71004 | S1 | S1 | [7 empty] | PSS No Ex | [11 empty] | 0 | 24.8 | -4.7 | 15.6 | 65 | -24.8 |  |  | GENROU | PSS2B |  |  | Closed | 22.5 | 2.5382 | CC | 29.53 |  | NO | 0.002 | 0.35 | 5.52 | 1.6301 | 0.132 | 0.439 | 3.3258 | 13.8 |  | BACUMESA_13.8_ST5 | CC (Combined Cycle Generic) | S1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71005 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 20 | 40 | -25 | 25 | 65 | 0.32 | 40.32 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 39 | 3.9331 | JE | 71.176 | PF<-0.85 | NO | 0.005 | 0.175 | 1.1 | 0.78294 | 0.075 | 0.26 | 3.4667 | 13.8 |  | BACUMESA_13.8_CT6 | JE (Jet Engine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57858 | 2 | 2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 36 | -17.4 | 17.4 | 76 | -36 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 2.9 | -8.4022 | W3 | 36 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.575 |  |  | W3 (Wind Turbine, Type 3) | 2 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 57901 | 1 | 1 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0 | 25.74 | -0.54443 | -0.54443 | 76 | -25.74 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 13 | -0.544 | W1 | 28.6 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W1 (Wind Turbine, Type 1) | 1
73 | WAPA R.M. | 1 | No owner defined |  | 72004 | W1 | W1 | [18 empty] | No Owner | 0 | 145 | -47.7 | 47.7 | 26 | -145 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 100 | 11.0495 | WT | 149.3 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.7 |  |  | WT (Wind Turbine) | W1
73 | WAPA R.M. | 273 | United Power |  | 72022 | PV | PV | [6 empty] | Limit Power Fact | [12 empty] | 0 | 13 | -8.7 | 8.7 | 26 | -13 | [6 empty] | Open | 0 | 0 | PV | 20 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 13.2 |  |  | PV (Photovoltaic) | PV
73 | WAPA R.M. | 273 | United Power |  | 72023 | PV | PV | [5 empty] | At Mvar Limit | [6 empty] | Gen on HV | [6 empty] | 0 | 16 | -2 | 2 | 26 | -16 |  |  | REGC_A |  |  | REEC_A | Closed | 16 | 2 | P4 | 16.725 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | P4 (Photovoltaic, Tracking) | PV
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72714 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 2.4 | 51.2 | -16.7 | 16.7 | 26 | -51.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 18.1 | -16.7 | W3 | 56.8 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1
73 | WAPA R.M. | 73 | Tri-State G&T |  | 72724 | PV | PV | [5 empty] | At Mvar Limit | [13 empty] | 0 | 145.2 | -57.3 | 57.3 | 26 | -145.2 |  |  | REGC_A |  |  | REEC_A | Closed | 138 | 57.3 | PV | 157 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | PV (Photovoltaic) | PV
73 | WAPA R.M. | 1 | No owner defined |  | 72746 | PV | PV |  | Missing BA | [9 empty] | Gen at 0.0 |  |  | Miss Turbine Type |  | Missing PS |  | No Owner | 0 | 81.3 | -22.6 | 37.4 | 9999 | -81.3 |  |  | REGC_A |  |  | REEC_A | Closed | 0 | 30.1865 | UN | 88.75 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | UN (Unknown) | PV
73 | WAPA R.M. | 26 | WAPA L.M. |  | 73181 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | -200 | 200 | -290 | 70 | 26 | -200 | [6 empty] | Closed | 195 | -290 | DC | 100 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 230 | BES Exempt |  | DC (Represents DC ties) | 1 | Netting Exempt | PSS Exempt
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73227 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 75.657 | -2.0104 | 10.0523 | 26 | 4.538 | 80.195 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 74 | -2.0104 | HY | 75.657 |  | YES | 0.004 | 0.227 | 2.57 | 1.9444 | 0.11 | 0.36 | 3.2727 | 13.8 |  |  | HY (Hydro) | 3
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73227 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 75.657 | -2.0104 | 10.0523 | 26 | 4.538 | 80.195 |  | GENTPJ | PSS2A | HYG3 | ESST1A_GE | Closed | 74 | -2.0104 | HY | 75.657 |  | YES | 0.004 | 0.227 | 2.57 | 1.9444 | 0.08 | 0.32 | 4 | 13.8 |  |  | HY (Hydro) | 4
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73306 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 15.7 | -8.4 | 9.4 | 26 | 4.4 | 20.1 |  | GENTPJ |  | HYGOV4 | ESST6B | Closed | 15 | 9.4 | HY | 19.2 |  | YES | 0.003 | 0.19 | 3 | 0.576 | 0.0732 | 0.2745 | 3.75 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73307 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 15.7 | -8.4 | 9.4 | 26 | 4.4 | 20.1 |  | GENTPJ |  | HYGOV4 | ESST6B | Closed | 15 | 9.4 | HY | 19.2 |  | YES | 0.003 | 0.19 | 3 | 0.576 | 0.0575 | 0.274 | 4.7652 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73308 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 15.7 | -8.4 | 9.4 | 26 | 4.4 | 20.1 |  | GENTPJ |  | HYGOV4 | ESST6B | Closed | 15 | 9.4 | HY | 19.2 |  | YES | 0.003 | 0.19 | 3 | 0.576 | 0.0525 | 0.2388 | 4.5486 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73319 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 10.35 | -3.5 | 5.025 | 26 | -1.35 | 9 |  | GENTPJ |  | HYGOV4 | ESST6B | Closed | 8.5 | 5.025 | HY | 10.35 |  | YES | 0.005 | 0.23 | 2.186 | 0.22625 | 0.16 | 0.36 | 2.25 | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73324 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 37.8 | -12.7848 | 14.9007 | 26 | -1.8 | 36 |  | GENTPJ | PSS2C | HYGOV4 | ST6C | Closed | 34.5 | 14.9007 | HY | 40.25 |  | YES | 0.002 | 0.21 | 2.66 | 1.0707 | 0.11 | 0.46 | 4.1818 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73333 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7.5 | -2.1 | 4.4 | 26 | -3e-07 | 7.5 |  | GENTPJ |  | HYGOV4 | ST5C | Closed | 7 | -2.1 | HY | 8.333 |  | NO | 0.005 | 0.227 | 2.25 | 0.18749 | 0.13 | 0.43 | 3.3077 | 4.2 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73333 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 7.5 | -2.5 | 4.4 | 26 | -3e-07 | 7.5 |  | GENTPJ |  | HYGOV4 | ST5C | Closed | 7 | -2.5 | HY | 8.333 |  | NO | 0.005 | 0.227 | 2.25 | 0.18749 | 0.13 | 0.43 | 3.3077 | 4.2 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73351 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 19 | -4.375 | 2.9138 | 26 | -3 | 16 |  | GENQEC |  | HYGOV4 | DC2C | Closed | 15.5 | 2.9138 | HY | 19 |  | YES | 0.007 | 0.3 | 1.377 | 0.26163 |  |  | NAN | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73352 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 19 | -4.375 | 2.9138 | 26 | -3 | 16 |  | GENQEC |  | HYGOV4 | DC2C | Closed | 15.5 | 2.9138 | HY | 19 |  | YES | 0.007 | 0.3 | 1.377 | 0.26163 |  |  | NAN | 6.9 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 95 | CSU |  | 73381 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 5 | 18 | -10.4 | 14.2 | 26 | -0.353 | 17.647 |  | GENTPJ |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | ST | 17.647 | PF<0.8 | NO | 0.002 | 0.18 | 4.5 | 0.79411 | 0.05 | 0.3 | 6 | 13.8 |  |  | ST (Steam Turbine) | G1
73 | WAPA R.M. | 95 | CSU |  | 73382 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 5 | 18 | -10.4 | 14.2 | 26 | -0.353 | 17.647 |  | GENTPJ |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | ST | 17.647 | PF<0.8 | NO | 0.002 | 0.18 | 4.5 | 0.79411 | 0.05 | 0.3 | 6 | 13.8 |  |  | ST (Steam Turbine) | G2
73 | WAPA R.M. | 95 | CSU |  | 73383 | G3 | G3 | [6 empty] | Limit Power Fact | [12 empty] | 6 | 23 | -14.3 | 20 | 26 | 4.059 | 27.059 |  | GENTPJ |  | GGOV1 | ESST1A_GE | Open | 0 | 0 | ST | 27.059 | PF<0.8 | NO | 0.002 | 0.18 | 4.5 | 1.2177 | 0.05 | 0.3 | 6 | 13.8 |  |  | ST (Steam Turbine) | G3
73 | WAPA R.M. | 95 | CSU |  | 73418 | C1 | C1 | [5 empty] | At Mvar Limit | [13 empty] | 120 | 225 | -11 | 45 | 26 | 5 | 230 |  | GENTPJ | PSS2B | IEEEG1_GE | ESST4B | Closed | 212.5 | 45 | CA | 230 |  | NO | 0.002 | 0.15 | 3.1645 | 7.2783 | 0.123 | 0.5208 | 4.2341 | 20 |  |  | CA (Combined Cycle Steam Part) | C1
73 | WAPA R.M. | 95 | CSU |  | 73434 | G1 | G1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 19.8 | 30.3 | -8.4 | 28 | 26 | -30.3 | [6 empty] | Open | 0 | 0 | GT | 41 | PF<0.8 | NO | 0.002 | 0.2 | 0 |  |  |  | NAN | 12.5 |  |  | GT (Gas Turbine) | G1
73 | WAPA R.M. | 95 | CSU |  | 73435 | G1 | G1 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 19.8 | 30.1 | -8.3 | 29.6 | 26 | -30.1 | [6 empty] | Open | 0 | 0 | GT | 41 | PF<0.8 | NO | 0.002 | 0.2 | 0 |  |  |  | NAN | 12.5 |  |  | GT (Gas Turbine) | G1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73444 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 3.2 | 1.428 | 1.428 | 26 | 0.5 | 3.7 |  | GENTPJ |  | HYGOV4 | ESST1A_GE | Closed | 3 | 1.428 | HY | 3.2 |  | NO | 0.004 | 0.168 | 2.1 | 0.0672 | 0.23 | 0.48 | 2.087 | 2.4 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73448 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 47.8 | -5 | 7.7703 | 26 | 2 | 49.8 |  | GENTPJ | PSS2B | HYGOV4 | ESST6B | Closed | 47 | 7.7703 | HY | 47.8 |  | YES | 0.005 | 0.235 | 2.4 | 1.1472 | 0.18 | 0.39 | 2.1667 | 13.8 |  |  | HY (Hydro) | 2 |  | PSS Exempt
73 | WAPA R.M. | 50 | US Bur Reclam |  | 73449 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 47.8 | -5 | 7.7703 | 26 | 2 | 49.8 |  | GENTPJ | PSS2B | HYGOV4 | ESST6B | Closed | 47 | 7.7703 | HY | 47.8 |  | YES | 0.005 | 0.235 | 2.4 | 1.1472 | 0.18 | 0.39 | 2.1667 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
73 | WAPA R.M. | 95 | CSU |  | 73509 | ST | ST |  |  |  |  | Exceed Gen Limit | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 50 | 206 | -90 | 108 | 26 | -206 |  |  | GENROU | PSS2B |  | ESST4B | Closed | 207.6 | 108 | CA | 274.5 |  | NO | 0.001 | 0.12 | 4 | 10.98 | 0.04 | 0.111 | 2.775 | 21 |  |  | CA (Combined Cycle Steam Part) | ST
73 | WAPA R.M. | 700 | Non Utility Owned - PSCO Area |  | 73719 | S1 | S1 | [15 empty] | Missing Model |  |  |  | 0 | 175 | -40 | 40 | 26 | -175 | [6 empty] | Closed | 130 | 8.4737 | P4 | 175 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.6 |  |  | P4 (Photovoltaic, Tracking) | S1
73 | WAPA R.M. | 700 | Non Utility Owned - PSCO Area |  | 73721 | S1 | S1 | [15 empty] | Missing Model |  |  |  | 0 | 60 | -30 | 30 | 26 | -60 | [6 empty] | Closed | 60 | 3.5565 | P4 | 60 |  | NO | 0.009 | 999 | 0 |  |  |  | NAN | 0.6 |  |  | P4 (Photovoltaic, Tracking) | S1
73 | WAPA R.M. | 95 | CSU |  | 73729 | G1 | G1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4.8 | 25.467 | -10.3 | 23.1 | 26 | 11.533 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 13.1135 | JE | 28 | PF<0.8 | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 95 | CSU |  | 73729 | G2 | G2 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4.8 | 25.467 | -10.3 | 23.1 | 26 | 11.533 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 13.1135 | JE | 28 | PF<0.8 | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G2
73 | WAPA R.M. | 95 | CSU |  | 73729 | G3 | G3 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4.8 | 25.467 | -10.3 | 23.1 | 26 | 11.533 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 13.1135 | JE | 28 | PF<0.8 | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G3
73 | WAPA R.M. | 95 | CSU |  | 73730 | G1 | G1 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4.8 | 25.667 | -10.3 | 23.1 | 26 | 11.333 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 17.6439 | JE | 28 | PF<0.8 | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 95 | CSU |  | 73730 | G2 | G2 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4.8 | 25.667 | -10.3 | 23.1 | 26 | 11.333 | 37 |  | GENROU | PSS2B | GGOV1 |  | Closed | 25 | 17.6439 | JE | 28 | PF<0.8 | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G2
73 | WAPA R.M. | 95 | CSU |  | 73730 | G3 | G3 | [6 empty] | Limit Power Fact | PSS No Ex | [11 empty] | 4.8 | 25.667 | -10.3 | 23.1 | 26 | 11.333 | 37 |  | GENROU | PSS2B | GGOV1 |  | Open | 0 | 0 | JE | 28 | PF<0.8 | NO | 0.005 | 0.132 | 1.597 | 0.44716 | 0.14 | 0.52 | 3.7143 | 13.8 |  |  | JE (Jet Engine) | G3
73 | WAPA R.M. | 700 | Non Utility Owned - PSCO Area |  | 73746 | S1 | S1 |  | Missing BA |  |  |  | At Mvar Limit | [8 empty] | Miss Turbine Type | Missing Model |  |  |  | 0 | 10 | -3 | 3 | 9999 | -10 | [6 empty] | Closed | 10 | 3 | UN | 10 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 13.2 |  |  | UN (Unknown) | S1
73 | WAPA R.M. | 60 | Black Hills |  | 74017 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 65 | 100 | -7.7 | 8.3 | 26 | -100 |  |  | GENTPJ | PSS2B |  | EXST4B | Closed | 100 | 8.3 | ST | 118.9 |  | NO | 0.001 | 0.199 | 3.94 | 4.6847 | 0.073 | 0.391 | 5.3562 | 13.8 |  |  | ST (Steam Turbine) | 1
73 | WAPA R.M. | 60 | Black Hills |  | 74061 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -24 | 39 | 26 | 6 | 46 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 37 | 4.7571 | JE | 71.176 | PF<0.8 | NO | 0.001 | 0.15 | 1.244 | 0.88543 | 0.128 | 0.351 | 2.7422 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 60 | Black Hills |  | 74061 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -24 | 39 | 26 | 6 | 46 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 35 | 4.7571 | JE | 71.18 | PF<0.8 | NO | 0.001 | 0.15 | 1.244 | 0.88548 | 0.128 | 0.351 | 2.7422 | 13.8 |  |  | JE (Jet Engine) | G2
73 | WAPA R.M. | 60 | Black Hills |  | 74062 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 40 | -24 | 39 | 26 | 6 | 46 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 35 | 5.897 | JE | 71.176 | PF<0.8 | NO | 0.001 | 0.15 | 1.244 | 0.88543 | 0.128 | 0.351 | 2.7422 | 13.8 |  |  | JE (Jet Engine) | G1
73 | WAPA R.M. | 60 | Black Hills |  | 74716 | PV | PV | [6 empty] | Limit Power Fact | [12 empty] | 0 | 162 | -121.5 | 121.5 | 26 | -162 |  |  | REGC_A |  |  | REEC_A | Closed | 97.5 | -18.8835 | PV | 162 | PF<0.8 | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | PV
73 | WAPA R.M. | 94 | Basin Electric Power Coop. |  | 76351 | 1 | 1 |  |  |  |  | Exceed Gen Limit | At Mvar Limit | [13 empty] | 0 | 200 | -10 | 10 | 26 | -200 | [6 empty] | Closed | -50 | -10 | DC | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 230 | BES Exempt |  | DC (Represents DC ties) | 1 | Netting Exempt | PSS Exempt
73 | WAPA R.M. | 65 | PSColorado |  | 79041 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 125 | 285 | -70 | 110 | 26 | 9.54e-06 | 285 |  | GENTPJ | PSS2A | IEEEG1_GE | REXS | Closed | 280 | -70 | ST | 306 |  | NO | 0.003 | 0.27 | 3.7 | 11.322 | 0.16 | 0.61 | 3.8125 | 22 |  |  | ST (Steam Turbine) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79152 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 138 | -48 | 50 | 26 | 18.687 | 156.687 |  | GENTPJ | PSS2C | HYGOV4 | ST1C | Closed | 115 | -11.0902 | HY | 173.7 |  | NO | 0.003 | 0.299 | 2.3 | 3.9951 | 0.1394 | 0.8978 | 6.4405 | 13.8 |  |  | HY (Hydro) | 5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58264 | 1 | 1 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0 | 19.5 | -2.1852 | -2.1852 | 76 | -19.5 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 7.3 | -2.185 | W4 | 21.8 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W4 (Wind Turbine, Type 4) | 1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79166 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.9 | -1.2 | 2.3 | 26 | 0.77 | 5.67 |  | GENTPJ | PSS2B | HYGOVR | ST6C | Closed | 4 | 0.983 | HY | 6.2 |  | NO | 0.003 | 0.192 | 1.52 | 0.09424 | 0.1842 | 0.4949 | 2.6868 | 4.2 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58338 | 2 | 2 |  |  |  | Unapproved Gen Model |  | At Mvar Limit | [13 empty] | 0 | 27 | -1.1168 | 1.1168 | 76 | -27 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 15 | -1.1168 | W3 | 30 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 2 |  | PSS Exempt
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79612 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20 | -1.78 | 17.02 | 26 | 51.2 | 71.2 |  | GENTPJ | PSS2A | GGOV1 | ESAC6A | Closed | 20 | 7.7248 | CC | 32.5 | PF<0.8 | NO | 0.002 | 0.15 | 4.45 | 1.4462 | 0.1476 | 0.3251 | 2.2026 | 13.8 |  |  | CC (Combined Cycle Generic) | 2
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79613 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -2 | 2 | 26 | -10 | [6 empty] | Closed | 9 | -1.103 | IC | 18 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79613 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -2 | 2 | 26 | -10 | [6 empty] | Closed | 9 | -1.103 | IC | 18 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 2
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79639 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 30 | -2 | 2 | 26 | -30 | [6 empty] | Open | 0 | 0 | GT | 30 |  | NO | 0 | 0.077 | 0 |  |  |  | NAN | 13.8 |  |  | GT (Gas Turbine) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79640 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 30 | -2 | 2 | 26 | -30 | [6 empty] | Open | 0 | 0 | GT | 30 |  | NO | 0 | 0.077 | 0 |  |  |  | NAN | 13.8 |  |  | GT (Gas Turbine) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79642 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16 | -3 | 3 | 26 | 0.8 | 16.8 |  | GENTPJ |  | HYGOV | EXST1_GE | Closed | 14 | 1.1891 | HY | 16.8 |  | NO | 0 | 0.171 | 3.6 | 0.6048 | 0.187 | 0.539 | 2.8824 | 13.8 |  |  | HY (Hydro) | 1
73 | WAPA R.M. | 925 | Farmington Electric Utility |  | 79642 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 16 | -3 | 3 | 26 | 0.8 | 16.8 |  | GENTPJ |  | HYGOV | EXST1_GE | Open | 0 | 0 | HY | 16.8 |  | NO | 0 | 0.171 | 3.6 | 0.6048 | 0.187 | 0.539 | 2.8824 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80000 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -0.58 | 0.81 | 10 | -4 |  |  | GENROU |  |  |  | Closed | 3.98 | 0.115 | HY | 1.968 |  | NO | 0 | 0.13 | 2.49 | 0.049003 | 0.077 | 0.196 | 2.5455 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80130 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.8 | -1.2 | 1.2 | 10 | -1.8 |  |  | GENROU |  |  |  | Open | 0 | 0 | ST | 2 | PF<-0.85 | NO | 0 | 0.14 | 2.49 | 0.0498 | 0.077 | 0.196 | 2.5455 | 0.6 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80159 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 1.8 | -1.2 | 1.2 | 10 | -1.8 |  |  | GENROU |  |  |  | Open | 0 | 0 | ST | 2 | PF<-0.85 | NO | 0 | 0.14 | 2.49 | 0.0498 | 0.077 | 0.196 | 2.5455 | 0.6 |  |  | ST (Steam Turbine) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80375 | 13 | 13 | [6 empty] | Limit Power Fact | [9 empty] | Missing PS |  |  | 0 | 12 | -16.8 | 16.8 | 10 | -12 | [6 empty] | Open | 0 | 0 | CC | 31.93 | PF<0.8 | NO | 0.002 | 0.14 | 0 |  |  |  | NAN | 13.8 |  |  | CC (Combined Cycle Generic) | 13
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 10.157 | 0.2379 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 10.157 | 0.2379 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 10.157 | 0.2379 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80386 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 10.2 | -6.44 | 5.33 | 10 | 2 | 12.2 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 10.157 | 0.2379 | HY | 12.2 | PF<-0.85 | NO | 0 | 0.216 | 1.106 | 0.13493 | 0.2 | 0.5 | 2.5 | 13.8 |  |  | HY (Hydro) | 4
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80389 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 3.285 | -1.47 | 1.87 | 10 | 0.365 | 3.65 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 3.27 | 0.51272 | HY | 3.65 |  | NO | 0 | 0.185 | 0.88 | 0.03212 | 0.06 | 0.29 | 4.8333 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80389 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7.76 | -3.21 | 3.51 | 10 | 0.862 | 8.622 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 7.726 | 0.51272 | HY | 8.622 |  | NO | 0 | 0.25 | 1.17 | 0.10088 | 0.038 | 0.155 | 4.0789 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80389 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7.76 | -3.25 | 3.6 | 10 | 0.862 | 8.622 |  | GENTPJ | PSS2B | HYG3 | ESAC8B_GE | Closed | 7.726 | 0.51272 | HY | 8.622 |  | NO | 0 | 0.25 | 1.17 | 0.10088 | 0.038 | 0.155 | 4.0789 | 6.9 |  |  | HY (Hydro) | 3
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80394 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 0.56 | -0.27 | 0.27 | 10 | -0.56 | [6 empty] | Closed | 0.558 | 0 | HY | 0.62 |  | NO | 0 | 0.13 | 0 |  |  |  | NAN | 0.6 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80416 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.08 | -4.84 | 4.84 | 10 | 0.02 | 10.1 |  | GENTPJ |  | G2WSCC | EXAC8B | Closed | 10.033 | -0.14424 | HY | 11.2 |  | NO | 0 | 0.225 | 1.06 | 0.11872 | 0.3 | 0.95 | 3.1667 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80416 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4.68 | -1.9 | 1.9 | 10 | 0.02 | 4.7 |  | GENTPJ |  | G2WSCC | EXAC8B | Closed | 4.658 | -0.14424 | HY | 5.2 |  | NO | 0 | 0.261 | 1.06 | 0.05512 | 0.3 | 0.95 | 3.1667 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80440 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 10.5 | -3.53 | 3.92 | 10 | -1.5 | 9 |  | GENROU |  | IEEEG1_GE | EXAC8B | Closed | 7 | 1.1818 | ST | 9 |  | NO | 0.004 | 0.195 | 1.61 | 0.1449 | 0.05 | 0.125 | 2.5 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80507 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 25.5 | -8.8 | 12.3 | 10 | 2.82 | 28.32 |  | GENTPJ |  | HYGOV | EXAC8B | Closed | 7 | 2.8817 | HY | 28.32 |  | NO | 0 | 0.2 | 1.38 | 0.39082 | 0.2 | 0.7 | 3.5 | 13.8 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80534 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 7.74 | -3.75 | 3.75 | 10 | 1.1e-07 | 7.74 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 7.707 | -1.4509 | HY | 8.6 |  | NO | 0 | 0.29 | 0.7401 | 0.063649 | 0.03 | 0.2 | 6.6667 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80535 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 8.28 | -4.01 | 4.01 | 10 | -9e-08 | 8.28 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 8.245 | -1.4652 | HY | 9.2 |  | NO | 0 | 0.13 | 0.97 | 0.08924 | 0.1398 | 0.3403 | 2.4342 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80536 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 9.72 | -4.71 | 4.71 | 10 | -6.2e-07 | 9.72 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 9 | -2.1958 | HY | 10.8 |  | NO | 0 | 0.16 | 0.64 | 0.06912 | 0.25 | 0.4 | 1.6 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80536 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 9.72 | -4.71 | 4.71 | 10 | -6.2e-07 | 9.72 |  | GENTPJ |  | HYG3 | ESAC8B_GE | Closed | 9 | -2.1958 | HY | 10.8 |  | NO | 0 | 0.16 | 0.64 | 0.06912 | 0.25 | 0.4 | 1.6 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80585 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 25 | -8.53 | 11.71 | 10 | 2.778 | 27.778 |  | GENTPJ |  | IEEEG1_GE | REXS | Open | 0 | 0 | CC | 27.778 |  | NO | 0 | 0.22 | 3.35 | 0.93056 | 0.19 | 0.52 | 2.7368 | 13.8 |  |  | CC (Combined Cycle Generic) | 4
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 80587 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 19.55 | -12.11 | 12.11 | 10 | -19.55 |  |  | GENROU |  |  |  | Closed | 19.453 | -1.1821 | ST | 23 |  | NO | 0 | 0.18 | 1.2 | 0.276 | 0.05 | 0.3 | 6 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80620 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 4 | -2.28 | 3 | 10 | 1 | 5 |  | GENTPJ |  | HYGOV |  | Closed | 3.982 | -0.24715 | HY | 5 |  | NO | 0 | 0.142 | 4.45 | 0.2225 | 0.337 | 0.982 | 2.9139 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 80657 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 62.5 | -21.7 | 30.2 | 10 | -62.5 |  |  | GENROU |  |  | REXS | Open | 0 | 0 | ST | 69.444 |  | NO | 0 | 0.221 | 2.3 | 1.5972 | 0.05 | 0.19 | 3.8 | 13.8 |  |  | ST (Steam Turbine) | 1 |  | PSS Exempt
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80730 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 8.9 | -4.25 | 4.25 | 10 | 0.86 | 9.76 |  | GENTPJ | PSS2B | HYG3 | ESST1A_GE | Closed | 8.856 | 3.6939 | HY | 9.76 |  | NO | 0 | 0.212 | 0.8 | 0.07808 | 0.1 | 0.22 | 2.2 | 6.9 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80730 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 8.9 | -4.25 | 4.25 | 10 | 0.86 | 9.76 |  | GENTPJ | PSS2B | HYG3 | ESST1A_GE | Closed | 8.856 | 3.6939 | HY | 9.76 |  | NO | 0 | 0.212 | 0.8 | 0.07808 | 0.1 | 0.22 | 2.2 | 6.9 |  |  | HY (Hydro) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80750 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.48 | -1.8 | 3.2 | 10 | -6.48 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 6.473 | -0.34634 | ST | 7.2 |  | NO | 0 | 0.128 | 2 | 0.144 | 0.07 | 0.16 | 2.2857 | 4.16 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80750 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.48 | -1.8 | 3.2 | 10 | -6.48 |  |  | GENTPJ |  |  | ESAC8B_GE | Closed | 6.473 | -0.34634 | CC | 7.2 |  | NO | 0 | 0.128 | 2 | 0.144 | 0.07 | 0.16 | 2.2857 | 4.16 |  |  | CC (Combined Cycle Generic) | 2
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 80902 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 0 | 6 | -2.082 | 2.906 | 10 | -6 |  |  | GENTPJ |  |  | EXAC8B | Closed | 5.971 | -2.082 | HY | 6.7 |  | NO | 0 | 0.216 | 1.89 | 0.12663 | 0.07 | 0.18 | 2.5714 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 204 | BCH Transmission Voltage Cust. |  | 80975 | 1 | 1 | [11 empty] | Gen at 0.0 |  |  |  | Missing Model |  |  |  | -8 | 0 | -2.4 | 2.4 | 10 | 0 | [6 empty] | Closed | 0 | 0.34985 | MP | 8 | PF<0.8 | NO | 0 | 0.25 | 0 |  |  |  | NAN | 4.16 |  |  | MP (Motor/Pump) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 81014 | C | C | [6 empty] | Limit Power Fact | [12 empty] | 0 | 32 | -23 | 23 | 10 | -32 |  |  | GENROU | PSS2A |  | EXAC8B | Open | 0 | 0 | CC | 38.4 | PF<-0.85 | NO | 0 | 0.13 | 3.3 | 1.2672 | 0.097 | 0.487 | 5.0206 | 13.8 |  |  | CC (Combined Cycle Generic) | C
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 81127 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 3.2 | -1.55 | 1.55 | 10 | -3.2 |  |  | GENTPJ |  |  | EXAC8B | Closed | 3.187 | -1.1609 | HY | 3.56 |  | NO | 0 | 0.16 | 0.75 | 0.0267 | 0.1 | 0.4 | 4 | 4.16 |  |  | HY (Hydro) | 1
50 | B.C.HYDRO | 203 | BCH Industrial Load/Gen Customer |  | 81130 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 43 | -18.7 | 18.7 | 10 | -43 |  |  | GENROU |  |  | EXST4B | Open | 0 | 0 | ST | 43 |  | NO | 0 | 0.22 | 2.02 | 0.8686 | 0.095 | 0.362 | 3.8105 | 13.8 |  |  | ST (Steam Turbine) | 1
50 | B.C.HYDRO | 202 | BCH Independent Power Producers |  | 81143 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 15 | -12 | 12 | 10 | -15 |  |  | REGC_A |  |  | REEC_A | Closed | 14.945 | 3.4605 | W3 | 15 | PF<0.8 | NO | 0 | 0.674 | 0 |  |  |  | NAN | 0.4 |  |  | W3 (Wind Turbine, Type 3) | 1
14 | APS | 2 | Arizona Public Service |  | 85393 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 6.4 | -2.1 | 2.1 | 2 | -6.4 | [6 empty] | Closed | 2.6 | 0.36874 | IC | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 12.47 |  | WASTEMGT_12.47_BIOGAS | IC (Internal Combustion) | 1
14 | APS | 2 | Arizona Public Service |  | 85647 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 19.9 | 0 | 0 | 2 | -19.9 | [6 empty] | Closed | 16 | 0 | P4 | 19.9 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.36 |  | CHVLYSLR_0.36 | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85650 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -0.81223 | -0.81223 | 2 | -15 | [6 empty] | Closed | 12 | -0.81223 | P4 | 15 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 12.5 |  | BAGDAD_SOLAR_12.5_PV | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85771 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -0.20306 | -0.20306 | 2 | -15 | [6 empty] | Closed | 11 | -0.20306 | P4 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.48 |  | GILSPIE_0.48_PV_U1 | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85775 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | 0 | 0 | 2 | -15 | [6 empty] | Closed | 12 | 0 | P4 | 15 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.3 |  | SADDLEMOUNTAIN_0.3_PV | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85781 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -0.20306 | 0.20306 | 2 | -15 | [6 empty] | Closed | 12 | 0 | P4 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.69 |  | BADGER_.69_PV | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 85792 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 4.5 | -0.31225 | -0.31225 | 2 | -4.5 | [6 empty] | Closed | 2.7 | -0.31225 | P4 | 100 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 12.47 |  | DARBY_12.47 | P4 (Photovoltaic, Tracking) | 1
14 | APS | 2 | Arizona Public Service |  | 148023 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -153.51 | 153.51 | -126.5 | 126.5 | 2 | -153.51 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 198.9 | PF<0.8 | NO | 99999 | 99999 | 0 |  |  |  | NAN | 0.66 |  |  | BA (Energy Storage, Battery) | 1
14 | APS | 2 | Arizona Public Service |  | 148040 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -151.731 | 151.731 | -109.13 | 109.13 | 2 | -151.731 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 186.9 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
14 | APS | 2 | Arizona Public Service |  | 148140 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 184.68 | -60.7 | 60.7 | 2 | -184.68 |  |  | REGC_A |  |  | REEC_A | Closed | 150 | 60.7 | PV | 194.4 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | A Solar | PV (Photovoltaic) | 1
14 | APS | 2 | Arizona Public Service |  | 148158 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -153.51 | 153.51 | -126.5 | 126.5 | 2 | -153.51 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 198.9 | PF<0.8 | NO | 99999 | 99999 | 0 |  |  |  | NAN | 0.66 |  |  | BA (Energy Storage, Battery) | 2
14 | APS | 2 | Arizona Public Service |  | 148167 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -151.747 | 151.747 | -105.47 | 105.47 | 2 | -151.747 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 184.8 | PF<-0.85 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 58901 | 3 | 3 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0 | 27.72 | -0.30459 | -0.30459 | 76 | -27.72 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 13 | -0.305 | W1 | 30.8 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W1 (Wind Turbine, Type 1) | 3
15 | SRP | 80 | Salt River Project | SRP | 150003 | ES | ES | [15 empty] | Missing Model |  |  |  | -25 | 25 | 0 | 0 | 80 | -25 | [6 empty] | Closed | 12.5 | 0 | BA | 8 |  | NO | 0 | 0.18 | 0 |  |  |  | NAN | 12.5 |  | SRP_Q46_12.5_SOLAR | BA (Energy Storage, Battery) | ES
15 | SRP | 801 | NON SRP Owned - other | SRP | 150006 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 100 | -38.9 | 38.9 | 80 | -100 |  |  | REGC_A |  |  | REEC_A | Closed | 50 | -38.9 | PV | 111 |  | NO | 0 | 10000 | 0 |  |  |  | NAN | 34.5 |  | HALO_Q44_PV | PV (Photovoltaic) | 1
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP | 150029 | PV | PV | [6 empty] | Limit Power Fact | [12 empty] | 0 | 68.4 | -43.2 | 43.2 | 80 | -68.4 |  |  | REGC_A |  |  | REEC_A | Closed | 34 | 17.5396 | PV | 72 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.63 |  | ANPP HVS_Q24 PV | PV (Photovoltaic) | PV
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP | 150030 | ST | ST | [6 empty] | Limit Power Fact | [12 empty] | -79.75 | 79.75 | -50.38 | 50.38 | 80 | -79.75 |  |  | REGC_A |  |  | REEC_C | Closed | 31 | 18.9927 | BA | 108.2 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | ANPP HVS_Q24 Batt | BA (Energy Storage, Battery) | ST
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP | 150034 | PV | PV | [6 empty] | Limit Power Fact | [12 empty] | 0 | 167.58 | -105.84 | 105.84 | 80 | -167.58 |  |  | REGC_A |  |  | REEC_A | Closed | 77 | 43.4648 | PV | 176.4 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.63 |  | ANPP HVS_Q25 PV | PV (Photovoltaic) | PV
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP | 150035 | ST | ST | [6 empty] | Limit Power Fact | [12 empty] | -188 | 188.22 | -118.89 | 118.89 | 80 | -188.22 |  |  | REGC_A |  |  | REEC_C | Closed | 73 | -46.376 | BA | 255.3 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.69 |  | ANPP HVS_Q25 Batt | BA (Energy Storage, Battery) | ST
15 | SRP | 80 | Salt River Project | SRP | 150133 | 13 | 13 | [16 empty] | Missing PS |  |  | 0 | 50 | -24.216 | 30.987 | 80 | -50 | [6 empty] | Open | 0 | 0 | JE | 58.824 |  | NO | 0.002 | 0.144 | 0 |  |  |  | NAN | 13.8 |  | COE_U13_Q76 | JE (Jet Engine) | 13
15 | SRP | 80 | Salt River Project | SRP | 150134 | 14 | 14 | [16 empty] | Missing PS |  |  | 0 | 50 | -24.216 | 30.987 | 80 | -50 | [6 empty] | Open | 0 | 0 | JE | 58.824 |  | NO | 0.002 | 0.144 | 0 |  |  |  | NAN | 13.8 |  | COE_U14_Q76 | JE (Jet Engine) | 14
15 | SRP | 80 | Salt River Project | SRP | 150135 | 15 | 15 | [16 empty] | Missing PS |  |  | 0 | 50 | -24.216 | 30.987 | 80 | -50 | [6 empty] | Open | 0 | 0 | JE | 58.824 |  | NO | 0.002 | 0.144 | 0 |  |  |  | NAN | 13.8 |  | COE_U15_Q76 | JE (Jet Engine) | 15
15 | SRP | 80 | Salt River Project | SRP | 150136 | 16 | 16 | [16 empty] | Missing PS |  |  | 0 | 50 | -24.216 | 30.987 | 80 | -50 | [6 empty] | Open | 0 | 0 | JE | 58.824 |  | NO | 0.002 | 0.144 | 0 |  |  |  | NAN | 13.8 |  | COE_U16_Q76 | JE (Jet Engine) | 16
15 | SRP | 80 | Salt River Project | SRP | 150137 | 17 | 17 | [16 empty] | Missing PS |  |  | 0 | 50 | -24.216 | 30.987 | 80 | -50 | [6 empty] | Open | 0 | 0 | JE | 58.824 |  | NO | 0.002 | 0.144 | 0 |  |  |  | NAN | 13.8 |  | COE_U17_Q76 | JE (Jet Engine) | 17
15 | SRP | 80 | Salt River Project | SRP | 150138 | 18 | 18 | [16 empty] | Missing PS |  |  | 0 | 50 | -24.216 | 30.987 | 80 | -50 | [6 empty] | Open | 0 | 0 | JE | 58.824 |  | NO | 0.002 | 0.144 | 0 |  |  |  | NAN | 13.8 |  | COE_U18_Q76 | JE (Jet Engine) | 18
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP | 151495 | S2 | S2 | [6 empty] | Limit Power Fact | [12 empty] | -153 | 157.75 | -123.46 | 123.46 | 80 | -157.75 |  |  | REGC_A |  |  | REEC_C | Closed | 20 | 1.3763 | BA | 205.76 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | CHR_Q27_T42_ES2 | BA (Energy Storage, Battery) | S2
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP | 151545 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | -153 | 157.75 | -123.46 | 123.46 | 80 | -157.75 |  |  | REGC_A |  |  | REEC_C | Closed | 20 | 1.3593 | BA | 205.76 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  | CHR_Q27_T41_ES1 | BA (Energy Storage, Battery) | S1
15 | SRP | 800 | NON SRP Owned - SRP Area | SRP | 151620 | S1 | S1 | [6 empty] | Limit Power Fact | [12 empty] | -86.5 | 90 | -71.15 | 71.15 | 80 | -90 |  |  | REGC_A |  |  | REEC_C | Closed | 8 | -10.3979 | BA | 114 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  | CHR_Q27_SP_BES_1 | BA (Energy Storage, Battery) | S1
15 | SRP | 801 | NON SRP Owned - other | SRP | 154727 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -89.2 | 89.2 | -44.73 | 44.73 | 80 | -89.2 |  |  | REGC_A |  |  | REEC_C | Closed | 44 | 13.8184 | BA | 101.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | FAE_SRP_Q55-BESS | BA (Energy Storage, Battery) | 1
15 | SRP | 801 | NON SRP Owned - other | SRP | 154828 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 50.8 | -16.943 | 16.943 | 80 | -50.8 |  |  | REGC_A |  |  | REEC_A | Closed | 25 | -7.2758 | P4 | 54 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | PVPC_Q07 PV1 | P4 (Photovoltaic, Tracking) | 1
15 | SRP | 137 | Sempra US Gas and Power | SRP [Bus] | 155010 | ES | ES | [17 empty] | Missing Sub R/X |  | -61.812 | 61.812 | -34.19 | 34.19 | 80 | -61.812 |  |  | REGC_A |  |  | REEC_C | Closed | 30 | -3.9689 | BA | 88 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | ANPP_Q23 Batt-5 | BA (Energy Storage, Battery) | ES
15 | SRP | 801 | NON SRP Owned - other | SRP | 155449 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 50.8 | -16.943 | 16.943 | 80 | -50.8 |  |  | REGC_A |  |  | REEC_A | Closed | 25 | -1.4454 | P4 | 54 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | PVPC_Q07 PV2 | P4 (Photovoltaic, Tracking) | 2
15 | SRP | 801 | NON SRP Owned - other | SRP | 156330 | P1 | P1 | [17 empty] | Missing Sub R/X |  | 0 | 156.3 | -94 | 94 | 80 | -156.3 |  |  | REGC_A |  |  | REEC_A | Closed | 75 | -3.3355 | PV | 172.4801 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | PVPCQ13_PV1 | PV (Photovoltaic) | P1
15 | SRP | 801 | NON SRP Owned - other | SRP | 156333 | E1 | E1 | [17 empty] | Missing Sub R/X |  | -156 | 156.3 | -73 | 73 | 80 | -156.3 |  |  | REGC_A |  |  | REEC_C | Closed | 75 | 7.2172 | BA | 172.872 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | PVPCQ13_ES1 | BA (Energy Storage, Battery) | E1
15 | SRP | 801 | NON SRP Owned - other | SRP | 156334 | P2 | P2 | [17 empty] | Missing Sub R/X |  | 0 | 156.3 | -94 | 94 | 80 | -156.3 |  |  | REGC_A |  |  | REEC_A | Closed | 75 | -5.5746 | PV | 182.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | PVPCQ13_PV2 | PV (Photovoltaic) | P2
15 | SRP | 801 | NON SRP Owned - other | SRP | 156335 | E2 | E2 | [17 empty] | Missing Sub R/X |  | -156 | 156.3 | -73 | 73 | 80 | -156.3 |  |  | REGC_A |  |  | REEC_C | Closed | 75 | 7.9707 | BA | 182.4 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | PVPCQ13_ES2 | BA (Energy Storage, Battery) | E2
15 | SRP | 80 | Salt River Project | SRP | 156395 | 1 | 1 | [9 empty] | Unreas H | [9 empty] | 0 | 46.4 | -11.3 | 17.5 | 80 | 11.835 | 58.235 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 58.235 |  | NO | 0.043 | 0.148 | 1.18 | 0.68717 | 0.11 | 0.49 | 4.4545 | 13.8 |  | CCG_SRPQ98_G1 | JE (Jet Engine) | 1
15 | SRP | 80 | Salt River Project | SRP | 156396 | 2 | 2 | [9 empty] | Unreas H | [9 empty] | 0 | 49.3 | -10.6 | 17.4 | 80 | 8.935 | 58.235 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Open | 0 | 0 | JE | 58.235 |  | NO | 0.043 | 0.148 | 1.18 | 0.68717 | 0.11 | 0.49 | 4.4545 | 13.8 |  | CCG_SRPQ98_G2 | JE (Jet Engine) | 2
15 | SRP | 137 | Sempra US Gas and Power | SRP [Bus] | 159013 | S1 | S1 | [17 empty] | Missing Sub R/X |  | 0 | 167.95 | -41.74 | 41.74 | 80 | -167.95 |  |  | REGC_A |  |  | REEC_A | Closed | 159 | 4.2445 | PV | 173.06 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | ANPP_Q02-1 | PV (Photovoltaic) | S1
15 | SRP | 137 | Sempra US Gas and Power | SRP [Bus] | 159014 | S1 | S1 | [17 empty] | Missing Sub R/X |  | 0 | 101.3 | -32.87 | 34.35 | 80 | -101.3 |  |  | REGC_A |  |  | REEC_A | Closed | 94 | 8.7585 | PV | 110 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | ANPP_Q02-2 | PV (Photovoltaic) | S1
15 | SRP | 137 | Sempra US Gas and Power | SRP [Bus] | 159015 | S1 | S1 | [17 empty] | Missing Sub R/X |  | 0 | 154 | -49.63 | 49.63 | 80 | -154 |  |  | REGC_A |  |  | REEC_A | Closed | 147 | 10.9796 | PV | 168 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.42 |  | ANPP_Q02-3 | PV (Photovoltaic) | S1
15 | SRP | 79 | Tucson Electric Power | SRP [Bus] | 159980 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 30 | 225.8 | -4.5 | 4.5 | 80 | -225.8 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 204 | 4.5 | CA | 319 |  | YES | 0 | 0.25 | 4.48 | 14.2912 | 0.085 | 0.3 | 3.5294 | 18 |  | GILRVTEP_18_2C | CA (Combined Cycle Steam Part) | 1
15 | SRP | 79 | Tucson Electric Power | SRP [Bus] | 159981 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 30 | 225.8 | -4.5 | 4.5 | 80 | -225.8 |  |  | GENTPJ | PSS2A |  | ESST4B | Closed | 204 | 4.5 | CA | 319 |  | YES | 0 | 0.25 | 4.48 | 14.2912 | 0.085 | 0.3 | 3.5294 | 18 |  | GILRVTEP_18_3C | CA (Combined Cycle Steam Part) | 1
16 | TEP | 150 | Unisource Energy Services |  | 161901 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | 5 | 20 | -25 | 15 | 79 | 1 | 21 |  | GENROU | PSS2B | GGOV1 | ESAC8B_GE | Open | 0 | 0 | JE | 67.5 | PF<0.8 | NO | 0.004 | 0.16 | 1.3 | 0.8775 | 0.136 | 0.481 | 3.5368 | 13.2 |  | VALENTEP_13.2_GEN4 | JE (Jet Engine) | 4
16 | TEP | 150 | Unisource Energy Services |  | 162902 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 55 | -19.6 | 19.6 | 79 | -55 |  |  | REGC_A |  |  | REEC_A | Closed | 33.4 | -10.0455 | PV | 55 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | GREYHAWK_0.6_SG | PV (Photovoltaic) | 1 |  | PSS Exempt
16 | TEP | 150 | Unisource Energy Services |  | 162903 | 1 | 1 | [12 empty] | Gen on HV | [6 empty] | 0 | 10.5 | -0.1 | 0.1 | 79 | -10.5 | [6 empty] | Open | 0 | 0 | W1 | 53.7 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  | GRIFFITH_69_WG | W1 (Wind Turbine, Type 1) | 1 |  | PSS Exempt
16 | TEP | 150 | Unisource Energy Services |  | 162904 | 1 | 1 | [16 empty] | Missing PS |  |  | 15 | 65.4 | -25 | 32.5 | 79 | -65.4 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN1 | JE (Jet Engine) | 1
16 | TEP | 150 | Unisource Energy Services |  | 162905 | 2 | 2 | [16 empty] | Missing PS |  |  | 15 | 65.4 | -25 | 32.5 | 79 | -65.4 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN1 | JE (Jet Engine) | 2
16 | TEP | 150 | Unisource Energy Services |  | 162906 | 3 | 3 | [16 empty] | Missing PS |  |  | 15 | 65.4 | -25 | 32.5 | 79 | -65.4 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN2 | JE (Jet Engine) | 3
16 | TEP | 150 | Unisource Energy Services |  | 162907 | 4 | 4 | [16 empty] | Missing PS |  |  | 15 | 65.4 | -25 | 32.5 | 79 | -65.4 | [6 empty] | Open | 0 | 0 | JE | 76.941 |  | NO | 0 | 0.223 | 0 |  |  |  | NAN | 13.8 |  | BLKMTN1_13.8_GEN2 | JE (Jet Engine) | 4
16 | TEP | 79 | Tucson Electric Power |  | 165050 | Q5 | Q5 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 80 | -32.87 | 33 | 79 | -80 | [6 empty] | Closed | 71 | 3.1692 | P4 | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q50_Q70_34.5_PV | P4 (Photovoltaic, Tracking) | Q5
16 | TEP | 79 | Tucson Electric Power |  | 165050 | Q7 | Q7 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 80 | -32.87 | 33 | 79 | -80 | [6 empty] | Closed | 71 | 3.1692 | P4 | 100 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q50_Q70_34.5_PV | P4 (Photovoltaic, Tracking) | Q7
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 170000 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 20 | 0 | 0 | 4 | -20 |  |  | REGC_A |  |  | REEC_A | Closed | 10 | 0 | P3 | 20 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | APACHE_34.5_SOLAR | P3 (Photovoltaic, Fixed) | PV
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 170001 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 4 | 40.8 | -12.4587 | 29.487 | 4 | 7.6e-07 | 40.8 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 40 | -8.0193 | JE | 71 |  | YES | 0 | 1e-05 | 1.27 | 0.9017 | 0.116 | 0.311 | 2.681 | 13.8 |  | APACHE_GT5_13.8 | JE (Jet Engine) | 1
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 170002 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 4 | 40.8 | -12.4587 | 29.487 | 4 | 7.6e-07 | 40.8 |  | GENTPJ | PSS2A | GGOV1 | ESAC8B_GE | Closed | 40 | -8.0193 | JE | 71 |  | YES | 0 | 1e-05 | 1.27 | 0.9017 | 0.116 | 0.311 | 2.681 | 13.8 |  | APACHE_GT6_13.8 | JE (Jet Engine) | 1
17 | AEPCO | 3 | Arizona Electric Power Co-Op |  | 179999 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 32.5 | 0 | 0 | 4 | -32.5 |  |  | REGC_A |  |  | REEC_A | Closed | 21 | 0 | P3 | 32.5 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 230 | BES Exempt | CAP-AZ_230.0_SOLAR_1 | P3 (Photovoltaic, Fixed) | 1
18 | NEVADA | 18 | N3 Nevada |  | 180655 | 3 | 3 | [9 empty] | Unreas H | [9 empty] | 65 | 226.9 | -92.14 | 140.28 | 24 | 1.025 | 227.925 |  | GENQEC | PSS2B | GGOV3 | ESST4B | Closed | 224.5 | 44.1527 | GT | 253.25 |  | YES | 0.003 | 0.205 | 1.052 | 2.6642 |  |  | NAN | 18 |  | SILVERHAPKR_18_CT3 | GT (Gas Turbine) | 3
18 | NEVADA | 18 | N3 Nevada |  | 180656 | 4 | 4 | [9 empty] | Unreas H | [9 empty] | 65 | 226.9 | -92 | 140 | 24 | -1.507 | 225.393 |  | GENQEC | PSS2B | GGOV3 | ESST4B | Closed | 225 | 48.8146 | GT | 253.25 |  | YES | 0.003 | 0.205 | 1.052 | 2.6642 |  |  | NAN | 18 |  | SILVERHAPKR_18_CT4 | GT (Gas Turbine) | 4
18 | NEVADA | 18 | N3 Nevada |  | 181006 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 99 | -66 | 66 | 24 | -99 |  |  | REGC_A |  |  |  | Closed | 88.5 | -18.1497 | PV | 110 | PF<-0.85 | NO | 1 | 10 | 0 |  |  |  | NAN | 0.385 |  | NSO_34.5_SOLAR1 | PV (Photovoltaic) | 1
24 | SOCALIF | 74 | Southern California Edison |  | 240019 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -106.1 | 106.1 | -82.3527 | 82.3527 | 999 | -106.1 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 134.31 | PF<0.8 | NO | 0.01 | 0.2 | 0 |  |  |  | NAN | 34.5 |  | ETIWND_2_SEPBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240027 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -125.46 | 125.46 | -115.308 | 115.308 | 999 | -125.46 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 172.8 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | OBERON_5_O1BBX2 | BA (Energy Storage, Battery) | 3
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240034 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -125.46 | 125.46 | -115.308 | 115.308 | 999 | -125.46 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 170.4 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | OBERON_5_O1BBX2 | BA (Energy Storage, Battery) | 4
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240041 | 7 | 7 | [6 empty] | Limit Power Fact | [12 empty] | -127.229 | 127.229 | -116.93 | 116.93 | 999 | -127.229 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 172.8 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | OBERON_5_O2BBX2 | BA (Energy Storage, Battery) | 7
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240048 | 8 | 8 | [6 empty] | Limit Power Fact | [12 empty] | -127.523 | 127.523 | -116.93 | 116.93 | 999 | -127.523 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 170.4 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  | OBERON_5_O2BBX2 | BA (Energy Storage, Battery) | 8
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240054 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -67.59 | 67.59 | -62.6188 | 62.6188 | 999 | -67.59 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 72.306 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | LCKHT1_2_LH1BT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240057 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.3662 | -12.8889 | 12.8889 | 999 | -20.3662 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 24.102 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | LCKHT1_2_LH1SR1 | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240059 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -59.368 | 59.368 | -52.1824 | 52.1824 | 999 | -59.368 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 60.255 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  | LCKHT1_2_LH1BT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240065 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -91.5876 | 91.5876 | -83.4918 | 83.4918 | 999 | -91.5876 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 86.408 | PF<0.8 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240066 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 115.504 | -72.886 | 72.886 | 999 | -115.504 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 138.578 | PF<-0.85 | NO | 999999 | 999999 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240077 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -41.25 | 41.25 | -36.478 | 36.478 | 999 | -41.25 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 41.25 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  | CMBLND_2_DS2BT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240079 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -61.88 | 61.88 | -54.717 | 54.717 | 999 | -61.88 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 61.88 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  | CMBLND_2_DS2BT2 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240080 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -66 | 66 | -58.365 | 58.365 | 999 | -66 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 66 | PF<0.8 | NO | 9999 | 9999 | 0 |  |  |  | NAN | 34.5 |  | CMBLND_2_DS2BT3 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240092 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -305 | 305 | -191.2 | 191.2 | 999 | -305 |  |  | REGC_A |  |  | REEC_C | Closed | 50 | 14.3915 | BA | 360 | PF<-0.85 | NO | 0 | 999 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240196 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -15.84 | 15.84 | -11.37 | 11.37 | 999 | -15.84 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 19.5 | PF<-0.85 | NO | 9999 | 99999 | 0 |  |  |  | NAN | 34.5 |  | VICPAS_2_SLOBT1 | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240288 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -66 | 66 | -47 | 47 | 999 | -66 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 81 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.55 |  | ECASCO_2_SJGBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240289 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -21.3 | 21.33 | -13.4 | 13.4 | 999 | -21.33 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 25.2 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | JOANEC_2_STABT2 | BA (Energy Storage, Battery) | 2
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240324 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -63.635 | 63.635 | -46.16 | 46.16 | 999 | -63.635 | [6 empty] | Open | 0 | 0 | BA | 106.08 | PF<-0.85 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240327 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -117.48 | 117.48 | -85.2 | 85.2 | 999 | -117.48 | [6 empty] | Open | 0 | 0 | BA | 195.84 | PF<-0.85 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240329 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -118.46 | 118.46 | -86 | 86 | 999 | -118.46 | [6 empty] | Open | 0 | 0 | BA | 197.47 | PF<-0.85 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240332 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -23.49 | 23.49 | -18 | 18 | 999 | -23.49 | [6 empty] | Open | 0 | 0 | BA | 39.16 | PF<0.8 | NO | 99999 | 999999 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240336 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -12.7 | 12.73 | -9.3 | 9.3 | 999 | -12.73 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 15.75 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240338 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -12.7 | 12.7 | -9.3 | 9.3 | 999 | -12.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 15.75 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240343 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -198 | 202.02 | -133.3 | 133.3 | 999 | -202.02 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 242 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.48 |  | CONDOR_2_CDRBT1 | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240367 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -25 | 25.82 | -17.4 | 17.4 | 999 | -25.82 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 32 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240482 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -20 | 20.53 | -14.1 | 14.1 | 999 | -20.53 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 26 | PF<-0.85 | NO | 1000000 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 740 | NON SCE Owned - SCE Area |  | 240520 | PV | PV | [17 empty] | Missing Sub R/X |  | 0 | 11 | 0 | 0 | 999 | -11 |  |  | DER_A |  |  |  | Closed | 11 | 0 | PV | 11 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  |  | PV (Photovoltaic) | PV
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59721 | G1 | G1 |  |  |  | Unapproved Gen Model |  |  |  |  | RX Ratio | [10 empty] | 0 | 105 | -37.05 | 49.775 | 76 | -105 |  |  | WT4G |  |  | WT4E | Closed | 28.3 | -13.5987 | W4 | 127.8 |  | NO | 0.742 | 0.371 | 0 |  |  |  | NAN | 0.72 |  |  | W4 (Wind Turbine, Type 4) | G1 |  | PSS Exempt
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242012 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -348.9504 | 348.9504 | -216.2601 | 216.2601 | 999 | -348.9504 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 410.53 | PF<-0.85 | NO | 0 | 100000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242013 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -333.8079 | 333.8079 | -250.356 | 250.356 | 999 | -333.8079 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 417.26 | PF<0.8 | NO | 0 | 100000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242014 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -344.576 | 344.576 | -258.432 | 258.432 | 999 | -344.576 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 430.72 | PF<0.8 | NO | 0 | 100000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242026 | 1 | 1 | [6 empty] | Limit Power Fact |  | RX Ratio | [10 empty] | 0 | 361.8003 | -243.1313 | 243.1313 | 999 | -361.8003 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | P3 | 435.904 | PF<-0.85 | NO | 100000000 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P3 (Photovoltaic, Fixed) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242027 | 1 | 1 | [6 empty] | Limit Power Fact |  | RX Ratio | [10 empty] | 0 | 373.8265 | -231.6796 | 231.6796 | 999 | -373.8265 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | P3 | 439.797 | PF<-0.85 | NO | 100000000 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P3 (Photovoltaic, Fixed) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242028 | 1 | 1 | [6 empty] | Limit Power Fact |  | RX Ratio | [10 empty] | 0 | 373.8265 | -231.6796 | 231.6796 | 999 | -373.8265 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | P3 | 439.797 | PF<-0.85 | NO | 100000000 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P3 (Photovoltaic, Fixed) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242043 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 382.32 | -185.166 | 185.166 | 999 | -382.32 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | P3 | 424.8 |  | NO | 100000000 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242044 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -388.9939 | 388.9939 | -241.0768 | 241.0768 | 999 | -388.9939 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 457.64 | PF<-0.85 | NO | 0 | 100000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242045 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 382.32 | -185.166 | 185.166 | 999 | -382.32 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | P3 | 424.8 |  | NO | 100000000 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242046 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -388.9939 | 388.9939 | -241.0768 | 241.0768 | 999 | -388.9939 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 457.64 | PF<-0.85 | NO | 0 | 100000000 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242047 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 382.32 | -185.166 | 185.166 | 999 | -382.32 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | P3 | 424.8 |  | NO | 100000000 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242068 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -85.68 | 85.68 | -77.45 | 77.45 | 999 | -85.68 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 115.5 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242069 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -85.68 | 85.68 | -77.45 | 77.45 | 999 | -85.68 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 115.5 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
24 | SOCALIF | 210 | DCR Transmission L.L.C. |  | 242070 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -85.68 | 85.68 | -77.45 | 77.45 | 999 | -85.68 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 115.5 | PF<0.8 | NO | 0 | 1000000 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 300140 | 2 | 2 | [16 empty] | Missing PS |  |  | 0 | 20.8 | -11 | 14 | 999 | 4.2 | 25 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Closed | 20.8 | 8.1263 | JE | 34.92 |  | NO | 0 | 0.116 | 2.3788 | 0.83068 | 0.1224 | 0.4172 | 3.4085 | 13.8 |  | KERNRDGE32G2 | JE (Jet Engine) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 300141 | 3 | 3 | [16 empty] | Missing PS |  |  | 0 | 20.7 | -11 | 14 | 999 | 4.3 | 25 |  | GENTPF |  | GGOV1 | ESAC8B_GE | Closed | 20.7 | 8.1264 | JE | 34.92 |  | NO | 0 | 0.116 | 2.3788 | 0.83068 | 0.1224 | 0.4172 | 3.4085 | 13.8 |  | KERNRDG332G3 | JE (Jet Engine) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 318683 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 1.1 | 0 | 0 | 999 | -1.1 |  |  | GENTPJ |  |  | ESAC7B | Closed | 1.1 | 0 | HY | 1.1 |  | NO | 0 | 1e-05 | 3 | 0.033 | 0.08 | 0.25 | 3.125 | 4.16 |  | HATLOS_6_LSCRK unit 1 | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59740 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 34.5 | -20.4 | 20.4 | 76 | -34.5 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 1.5 | -6.2653 | W3 | 33.7 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 1 |  |  | W3 (Wind Turbine, Type 3) | G1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 346912 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -9998.9998 | 8.16 | -4 | 4 | 999 | -8.16 |  |  | REGC_A |  |  | REEC_A | Closed | 5.712 | 0.26933 | PV | 8.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | AVENAL_6_AVSLR1 0124-WD unit 1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 346914 | 2 | 2 | [17 empty] | Missing Sub R/X |  | -9998.9998 | 8.16 | -4 | 4 | 999 | -8.16 |  |  | REGC_A |  |  | REEC_A | Closed | 5.712 | 0.26933 | PV | 8.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.385 |  | AVENAL_6_AVSLR2 0124-WD unit 2 | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 349683 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 10 | -4.56 | 4.56 | 999 | -10 |  |  | REGC_A |  |  | REEC_A | Closed | 7 | -1.0426 | P4 | 10.998 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  | TWISSL_6_SOLAR1 0040-WD unit 1 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 349686 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 10 | -4.56 | 4.56 | 999 | -10 |  |  | REGC_A |  |  | REEC_A | Closed | 7 | -0.4233 | P4 | 10.998 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  | TWISSL_6_SOLAR1 0040-WD unit 2 | P4 (Photovoltaic, Tracking) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 364362 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 25.41 | -8.87 | 8.87 | 999 | -25.41 |  |  | REGC_A |  |  | REEC_A | Closed | 17.787 | 8.87 | PV | 28.08 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit A3 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 364363 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 169.4 | -59.18 | 59.18 | 999 | -169.4 |  |  | REGC_A |  |  | REEC_A | Closed | 118.58 | 9.711 | PV | 187.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | TOPAZ_2_SOLAR unit B3 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365141 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | -133.67 | 133.67 | -46.28 | 46.28 | 999 | -133.67 |  |  | REGC_A |  |  | REEC_C | Closed | 53.468 | -46.28 | BA | 154 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1109 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365157 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -9.7 | 10.3 | -8.324 | 8.324 | 999 | -10.3 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 12.5 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | Q1143 bess c8 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365170 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 12.276 | -0.2 | 0.2 | 999 | -12.276 |  |  | REGC_A |  |  | REEC_A | Closed | 8.5932 | 0 | PV | 13.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | 0023-WD BLCKWL_6_SOLAR1 | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365180 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 20.4 | -9.349 | 9.349 | 999 | -20.4 |  |  | REGC_A |  |  |  | Closed | 14.28 | 9.349 | P4 | 22.44 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | WAUKNA_1_SOLAR spv Q0478 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365209 | 2 | 2 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -68.367 | 68.367 | -58.53 | 58.53 | 999 | -68.367 |  |  | REGC_A |  |  | REEC_C | Closed | 27.3468 | 30.5882 | BA | 90 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365211 | 4 | 4 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -68.367 | 68.367 | -58.53 | 58.53 | 999 | -68.367 |  |  | REGC_A |  |  | REEC_C | Closed | 27.3468 | 30.5882 | BA | 90 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365219 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 127.3 | -50 | 50 | 999 | -127.3 |  |  | REGC_A |  |  | REEC_A | Closed | 89.11 | 8.1263 | P4 | 136.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365220 | 2 | 2 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -114.45 | 114.45 | -100.6 | 100.6 | 999 | -114.45 |  |  | REGC_A |  |  | REEC_C | Closed | 45.78 | 8.1263 | BA | 150 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365221 | 3 | 3 | [17 empty] | Missing Sub R/X |  | 0 | 127.3 | -50 | 50 | 999 | -127.3 |  |  | REGC_A |  |  | REEC_A | Closed | 89.11 | 8.1263 | P4 | 136.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | P4 (Photovoltaic, Tracking) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365222 | 4 | 4 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -114.45 | 114.45 | -100.6 | 100.6 | 999 | -114.45 |  |  | REGC_A |  |  | REEC_C | Closed | 45.78 | 8.1264 | BA | 150 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365225 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -35 | 40.6 | -29.9 | 29.9 | 999 | -40.6 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 50.4 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1135 BESS1 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365226 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 205.5 | -72.16 | 72.16 | 999 | -205.5 |  |  | REGC_A |  |  | REEC_A | Closed | 143.85 | 63.5274 | P4 | 217.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1135 SPV1 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365230 | 2 | 2 | [17 empty] | Missing Sub R/X |  | 0 | 206.6 | -73.4 | 73.4 | 999 | -206.6 |  |  | REGC_A |  |  | REEC_A | Closed | 144.62 | 63.5267 | P4 | 219.249 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q1135 SPV2 | P4 (Photovoltaic, Tracking) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365240 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -206.4 | 215.6 | -192 | 192 | 999 | -215.6 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 288.8 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q1135 BESS3 | BA (Energy Storage, Battery) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365318 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -114.18 | 114.18 | -100.9 | 100.9 | 999 | -114.18 | [6 empty] | Open | 0 | 0 | BA | 152.4 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q1243 bess1 C09 CAISO-RPS | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365323 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -114.18 | 114.18 | -100.9 | 100.9 | 999 | -114.18 | [6 empty] | Open | 0 | 0 | BA | 152.4 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  | Q1243 bess2 C09 CAISO-RPS | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365330 | 2 | 2 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 96.02 | -42.4 | 42.4 | 999 | -96.02 |  |  | REGC_A |  |  | REEC_A | Closed | 67.214 | 42.4 | PV | 106 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.418 |  | TRNQLT_2_SOLAR spv2 Q0643X | PV (Photovoltaic) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365336 | 3 | 3 | [6 empty] | Limit Power Fact | [12 empty] | -51.7 | 51.7 | -32.71 | 32.71 | 999 | -51.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 62.1 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | HENRTA_6_UNITA1 bess1 | BA (Energy Storage, Battery) | 3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365337 | 4 | 4 | [6 empty] | Limit Power Fact | [12 empty] | -51.7 | 51.7 | -32.71 | 32.71 | 999 | -51.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 62.1 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | HENRTA_6_UNITA1 bess2 | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365343 | RN | RN | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 12.415 | 0 | 0 | 999 | -12.415 | [6 empty] | Open | 0 | 0 | UN | 12.415 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  | 1515-RD 2740-RD | UN (Unknown) | RN
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59835 | G1 | G1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 75.6 | 0 | 0 | 76 | -75.6 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 79.8 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G1 |  | PSS Exempt
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59901 | 2 | 2 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0 | 21.78 | -1.3066 | -1.3066 | 76 | -21.78 |  |  | WT2G | WT2P | WT2T | WT2E | Closed | 13 | -1.307 | W1 | 24.2 |  | NO | 0 | 0.302 | 0 |  |  |  | NAN | 25 |  |  | W1 (Wind Turbine, Type 1) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365504 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 18.9 | -5.9 | 5.9 | 999 | -18.9 |  |  | REGC_A |  |  | REEC_A | Closed | 1.89 | 1.36 | PV | 19.8 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | SUMWHT_6_SWSSR1 spv Q0632B | PV (Photovoltaic) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365540 | 1 | 1 | [5 empty] | At Mvar Limit |  | PSS No Ex | [11 empty] | 0 | 17.85 | -5 | 10 | 999 | -17.85 |  |  | GENTPJ | PSS2A |  |  | Closed | 17.85 | 10 | ST | 21 |  | NO | 0 | 0.23 | 3 | 0.63 | 0.05 | 0.25 | 5 | 12.47 |  | Q1016 | ST (Steam Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 59935 | G2 | G2 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 73.8 | 0 | 0 | 76 | -73.8 |  |  | WT3G | WT3P | WT3T | WT3E | Open | 0 | 0 | W3 | 77.9 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | G2 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365556 | RN | RN | [17 empty] | Missing Sub R/X |  | 0 | 2 | 0 | 0 | 999 | -2 |  |  | DER_A |  |  |  | Closed | 0.76 | 0 | W3 | 2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | r21 no queue # | W3 (Wind Turbine, Type 3) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365557 | RE | RE | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 5 | 0 | 0 | 999 | -5 | [6 empty] | Open | 0 | 0 | UN | 6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1277-RD 1990-RD unit 1 | UN (Unknown) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365558 | RN | RN | [15 empty] | Missing Model |  | Missing Sub R/X |  | -2 | 2 | 0 | 0 | 999 | -2 | [6 empty] | Closed | 0.8 | 0 | BA | 2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1249-RD | BA (Energy Storage, Battery) | RN
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365563 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 10 | -4.5 | 4.5 | 999 | -10 |  |  | REGC_A |  |  | REEC_A | Closed | 7 | -3.7521 | P4 | 10.98 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.357 |  | SKERN_6_SOLAR2 Q0885 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365564 | RE | RE | [14 empty] | Miss Turbine Type |  |  |  |  | 0 | 5 | 0 | 0 | 999 | -5 | [6 empty] | Open | 0 | 0 | UN | 6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | 1277-RD 1990-RD unit 2 | UN (Unknown) | RE
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365566 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 15.337 | -8.258 | -8.258 | 999 | -15.337 |  |  | WT2G |  | WT2T | WT2E | Closed | 15.337 | -8.258 | W2 | 15.49 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWNDR_2_SMUD | W2 (Wind Turbine, Type 2) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365593 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 46.2 | -22.8 | 22.8 | 999 | -46.2 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 16.13 | -1.9349 | W3 | 52.77 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q1010 | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365604 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 40.8 | -25.2 | 25.2 | 999 | -40.8 |  |  | REGC_A |  |  | REEC_A | Closed | 40.8 | 25.2 | P4 | 48.51 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  | LTBERA_1_LB1SR1 spv Q1028 Q1029 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365608 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 10 | -4.84 | 4.84 | 999 | -10 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 10 | -0.075463 | W3 | 11.11 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | USWPFK_6_FRICK | W3 (Wind Turbine, Type 3) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 550003 | G1 | G1 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0.686 | 13.72 | -3.254 | -3.254 | 76 | -13.72 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 9.9 | -3.254 | XC | 15.248 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | XC (Cross Compound Steam) | G1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365629 | FW | FW | [17 empty] | Missing Sub R/X |  | 0 | 101 | -45 | 45 | 999 | -101 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 39.29 | -24.1682 | W4 | 113.85 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12 |  | STRAUS_1_STRWD1 | W4 (Wind Turbine, Type 4) | FW
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365648 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | -25.3 | 25.3 | -14.25 | 14.25 | 999 | -25.3 |  |  | REGC_A |  |  | REEC_C | Closed | 10.12 | -14.25 | BA | 29.04 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1272 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365649 | 2 | 2 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | -20.25 | 20.25 | -8.01 | 8.01 | 999 | -20.25 |  |  | REGC_A |  |  | REEC_C | Closed | 8.1 | -8.01 | BA | 21.78 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1835 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365659 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [12 empty] | Missing Sub R/X |  | 0 | 20.709 | -6.869 | 6.869 | 999 | -20.709 |  |  | REGC_A |  |  | REEC_A | Closed | 20.709 | 0.86577 | PV | 22 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.36 |  | ADOBEE_1_SOLAR Q0622B | PV (Photovoltaic) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 550004 | G2 | G2 |  |  |  | Unapproved Gen Model | Exceed Gen Limit | [14 empty] | 0.772 | 15.435 | -3.7141 | -3.7141 | 76 | -15.435 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 11.3 | -3.714 | XC | 17.154 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | XC (Cross Compound Steam) | G2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365666 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | -80 | 84.8 | -32.2 | 32.2 | 999 | -84.8 | [6 empty] | Closed | 33.92 | -13.7878 | BA | 90.75 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365669 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 17.6 | -11.5 | 11.5 | 999 | -17.6 | [6 empty] | Open | 0 | 0 | W3 | 21.24 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 640063 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 50 | -36.67 | 36.67 | 24 | -50 |  |  | REGC_A |  |  | REEC_B | Closed | 39.4 | -1.3069 | PV | 51.7 | PF<-0.85 | YES | 1.754 | 2.355 | 0 |  |  |  | NAN | 0.55 |  | LUNING_0.48_SOLAR | PV (Photovoltaic) | 1
65 | PACE | 8 | UAMPS |  | 66550 | Z4 | Z4 |  |  |  | Unapproved Gen Model |  |  | Limit Power Fact | [12 empty] | 0 | 57.6 | -49.7 | 33.7 | 7 | -57.6 |  |  | WT4G |  | WT4T | WT4E | Closed | 25.9 | -10.8865 | W1 | 165 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.6 |  |  | W1 (Wind Turbine, Type 1) | Z4 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365695 | 2 | 2 | [17 empty] | Missing Sub R/X |  | -152.13 | 152.13 | -77.2 | 77.2 | 999 | -152.13 |  |  | REGC_A |  |  | REEC_C | Closed | 60.852 | 50.7788 | BA | 170.61 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1158 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365699 | 4 | 4 | [17 empty] | Missing Sub R/X |  | -152.13 | 152.13 | -77.2 | 77.2 | 999 | -152.13 |  |  | REGC_A |  |  | REEC_C | Closed | 60.852 | 50.7785 | BA | 170.61 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1158 | BA (Energy Storage, Battery) | 4
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365726 | 2 | 2 | [17 empty] | Missing Sub R/X |  | -93.7 | 93.7 | -55.22 | 55.22 | 999 | -93.7 |  |  | REGC_A |  |  | REEC_C | Closed | 37.48 | -19.9556 | BA | 108.76 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.52 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365729 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 9 | -4.36 | 4.36 | 999 | -9 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 9 | -0.95765 | W3 | 10.02 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365749 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 153 | 0 | 0 | 999 | -153 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 153 | 0 | W3 | 178.2 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.575 |  |  | W3 (Wind Turbine, Type 3) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365769 | 2 | 2 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | -10 | 10.28 | -3.9 | 3.9 | 999 | -10.28 |  |  | REGC_A |  |  | REEC_C | Closed | 4.112 | 3.9 | BA | 11 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.55 |  |  | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365773 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -208 | 208 | -115 | 115 | 999 | -208 |  |  | REGC_A |  |  | REEC_C | Closed | 83.2 | 17.9823 | BA | 237.762 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  |  | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365831 | 4 | 4 | [17 empty] | Missing Sub R/X |  | -60 | 60.59 | -33.33 | 33.33 | 999 | -60.59 |  |  | REGC_A |  |  | REEC_C | Closed | 24.236 | -0.62915 | BA | 69.159 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.505 |  | Q0877 | BA (Energy Storage, Battery) | 4
65 | PACE | 7 | PacifiCorp - East |  | 69102 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 19.5 | -9.438 | 9.438 | 7 | -19.5 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 9.4 | 1.9561 | W1 | 23 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | W1 (Wind Turbine, Type 1) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365938 | 3 | 3 | [17 empty] | Missing Sub R/X |  | -12.1 | 10.89 | -5.27 | 5.27 | 999 | -10.89 |  |  | REGC_A |  |  | REEC_C | Closed | 4.356 | 2.3444 | BA | 12.1 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 3
65 | PACE | 7 | PacifiCorp - East |  | 69523 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 43.2 | -13.5 | 18.8 | 7 | -43.2 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 19.4 | 9.7651 | W1 | 47.08 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.7 |  |  | W1 (Wind Turbine, Type 1) | 1 |  | PSS Exempt
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365994 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -53.85 | 82.8 | -38.93 | 38.93 | 999 | -82.8 |  |  | REGC_A |  |  | REEC_C | Closed | 82.8 | 30.1594 | BA | 91.512 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q0946-Q1259 spvbess1 | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365998 | 2 | 2 | [17 empty] | Missing Sub R/X |  | -38.14 | 58.57 | -27.77 | 27.77 | 999 | -58.57 |  |  | REGC_A |  |  | REEC_C | Closed | 58.57 | 21.289 | BA | 64.821 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q0946-Q1259 spvbess2 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 365999 | 3 | 3 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | 0 | 12.51 | -9.64 | 9.64 | 999 | -12.51 |  |  | REGC_A |  |  | REEC_A | Closed | 8.757 | 7.6876 | P3 | 15.798 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.69 |  | Q0946-Q1259 spv3 | P3 (Photovoltaic, Fixed) | 3
30 | PG AND E | 390 | Pacific Gas and Electric |  | 366107 | M1 | M1 | [6 empty] | Limit Power Fact | [12 empty] | -63.9 | 63.9 | -47.18 | 47.18 | 999 | -63.9 | [6 empty] | Open | 0 | 0 | BA | 79.43 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.505 |  | ELKHRN_1_EESX3 | BA (Energy Storage, Battery) | M1
30 | PG AND E | 390 | Pacific Gas and Electric |  | 366108 | M2 | M2 | [6 empty] | Limit Power Fact | [12 empty] | -60.85 | 60.85 | -45.23 | 45.23 | 999 | -60.85 | [6 empty] | Open | 0 | 0 | BA | 75.82 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.505 |  | ELKHRN_1_EESX3 | BA (Energy Storage, Battery) | M2
30 | PG AND E | 390 | Pacific Gas and Electric |  | 366109 | M3 | M3 | [6 empty] | Limit Power Fact | [12 empty] | -60.85 | 60.85 | -45.23 | 45.23 | 999 | -60.85 | [6 empty] | Open | 0 | 0 | BA | 75.82 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.505 |  | ELKHRN_1_EESX3 | BA (Energy Storage, Battery) | M3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366130 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 6.011 | -2.08 | 2.08 | 999 | -6.011 |  |  | REGC_A |  |  | REEC_A | Closed | 4.2077 | -2.08 | P3 | 6.54 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | P3 (Photovoltaic, Fixed) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366131 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 14.339 | -4.93 | 4.93 | 999 | -14.339 |  |  | REGC_A |  |  | REEC_A | Closed | 10.0373 | -4.93 | P3 | 15.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | P3 (Photovoltaic, Fixed) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366241 | M1 | M1 | [6 empty] | Limit Power Fact | [12 empty] | -77.46 | 77.46 | -73.43 | 73.43 | 999 | -77.46 | [6 empty] | Open | 0 | 0 | BA | 106.73 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS1 | BA (Energy Storage, Battery) | M1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366242 | M2 | M2 | [6 empty] | Limit Power Fact | [12 empty] | -77.46 | 77.46 | -73.43 | 73.43 | 999 | -77.46 | [6 empty] | Open | 0 | 0 | BA | 106.73 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS2 | BA (Energy Storage, Battery) | M2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366243 | M3 | M3 | [6 empty] | Limit Power Fact | [12 empty] | -104.27 | 104.27 | -98.85 | 98.85 | 999 | -104.27 | [6 empty] | Open | 0 | 0 | BA | 143.675 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS3 | BA (Energy Storage, Battery) | M3
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366244 | M4 | M4 | [6 empty] | Limit Power Fact | [12 empty] | -104.27 | 104.27 | -98.85 | 98.85 | 999 | -104.27 | [6 empty] | Open | 0 | 0 | BA | 143.675 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1540-BESS4 | BA (Energy Storage, Battery) | M4
30 | PG AND E | 470 | Calpine Corp. |  | 366344 | 1 | 1 | [5 empty] | At Mvar Limit | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -25.27 | 25.27 | -17.6 | 17.6 | 999 | -25.27 |  |  | REGC_A |  |  | REEC_C | Closed | 10.108 | -17.6 | BA | 30.8 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | 1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71009 | W1 | W1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 28.8 | -13.92 | 9.44 | 65 | -28.8 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 7.2 | -0.9711 | W3 | 32 |  | NO | 0 | 0.173 | 0 |  |  |  | NAN | 0.7 |  |  | W3 (Wind Turbine, Type 3) | W1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366416 | 1 | 1 | [17 empty] | Missing Sub R/X |  | -309.32 | 306.3 | -101.7 | 101.7 | 999 | -306.3 |  |  | REGC_A |  |  | REEC_C | Closed | 306.3 | -14.2688 | BA | 325.6 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  | Q1479 be | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366608 | 1 | 1 | [6 empty] | Limit Power Fact | [10 empty] | Missing Sub R/X |  | -105.92 | 105.92 | -73.1 | 73.1 | 999 | -105.92 |  |  | REGC_A |  |  | REEC_C | Closed | 42.368 | 1.4935 | BA | 128.7 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.66 |  | Q1470 BESS | BA (Energy Storage, Battery) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366708 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | -73.3 | 70.9 | -24 | 24 | 999 | -70.9 | [6 empty] | Closed | 28.36 | -20.1211 | BA | 77.165 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1499-CAISO-RPS | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366744 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 61.18 | -25.06 | 25.06 | 999 | -61.18 |  |  | REGC_A |  |  | REEC_A | Closed | 42.826 | -20.8762 | P4 | 66.15 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.6 |  | Q1493 spv c14 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366745 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -39.45 | 39.45 | -34.26 | 34.26 | 999 | -39.45 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 52.25 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.95 |  | Q1493 bess c14 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366806 | 2 | 2 | [6 empty] | Limit Power Fact | [12 empty] | -20.6 | 20.6 | -14.7 | 14.7 | 999 | -20.6 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 29.4 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  | Q1443 bess c11 | BA (Energy Storage, Battery) | 2
30 | PG AND E | 360 | PG&E customer owned facilities |  | 366808 | 1 | 1 | [5 empty] | At Mvar Limit | [11 empty] | Missing Sub R/X |  | 0 | 41.08 | -15.76 | 15.76 | 999 | -41.08 |  |  | REGC_A |  |  | REEC_A | Closed | 28.756 | -15.76 | P4 | 44 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.645 |  | Q1443 spv c11 | P4 (Photovoltaic, Tracking) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 367338 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 61.12 | -32.84 | 32.84 | 999 | -61.12 | [6 empty] | Open | 0 | 0 | ST | 62.35 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 12.47 |  | Q1859 geothermal CAISO-RPS | ST (Steam Turbine) | 1
30 | PG AND E | 360 | PG&E customer owned facilities |  | 399997 | EW | EW | [12 empty] | Gen on HV | [6 empty] | 0 | 17.3 | 0 | 0 | 999 | -17.3 | [6 empty] | Open | 0 | 0 | BA | 17.3 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 60 |  | CAISO-RPS | BA (Energy Storage, Battery) | EW
40 | NORTHWEST | 493 | Power Resources Cooperative | Bonneville Power Admin | 400151 | 1 | 1 | [12 empty] | Gen on HV |  |  | Missing Model | Missing PS |  |  | 0 | 5.66 | 0 | 0 | 14 | -5.66 | [6 empty] | Closed | 5.6 | 0 | GT | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 69 |  |  | GT (Gas Turbine) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 403441 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 70 | -31.9 | 27.2671 | 14 | -70 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Closed | 51.8 | 16.2876 | HY | 63.9 |  | YES | 0 | 0.2 | 4.4 | 2.8116 | 0.2 | 0.47 | 2.35 | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 987 | USACE-Portland District | Bonneville Power Admin | 403442 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 70 | -33.5 | 36.5 | 14 | -70 |  |  | GENTPJ | PSS2A | H6E | EXST1_GE | Open | 0 | 0 | HY | 63.9 |  | YES | 0 | 0.2 | 4.4 | 2.8116 | 0.2 | 0.47 | 2.35 | 13.8 |  |  | HY (Hydro) | 2
40 | NORTHWEST | 929 | Columbia Basin Hydro | Bonneville Power Admin | 404670 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 2.4 | 0 | 0 | 14 | -2.4 | [6 empty] | Closed | 2 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 405144 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 405145 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 405184 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 405185 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 406365 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 406366 | 2 | 2 | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 9 | 0 | PV | 10 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 406374 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 406375 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 497 | Middlefork Irrigation | Bonneville Power Admin | 408130 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 2 | 0 | 0 | 14 | -2 | [6 empty] | Closed | 2 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 497 | Middlefork Irrigation | Bonneville Power Admin | 408130 | 2 | 2 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 0.5 | 0 | 0 | 14 | -0.5 | [6 empty] | Closed | 0.5 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | HY (Hydro) | 2
40 | NORTHWEST | 497 | Middlefork Irrigation | Bonneville Power Admin | 408130 | 3 | 3 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 0.8 | 0 | 0 | 14 | -0.8 | [6 empty] | Closed | 0.8 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 12.5 |  |  | HY (Hydro) | 3
40 | NORTHWEST | 1473 | Mckinley Paper Company | Bonneville Power Admin | 408412 | 1 | 1 | [10 empty] | Unreas Sat | [6 empty] | Missing Sub R/X |  | 0 | 12.6 | -12.7 | 17.8 | 14 | -12.6 |  |  | GENTPJ | PSS2B |  | ESAC8B_GE | Closed | 12 | 4.2066 | ST | 25 | PF<0.8 | YES | 0 | 1e-05 | 3.2 | 0.8 | 0.043 | 0.405 | 9.4186 | 13.8 |  |  | ST (Steam Turbine) | 1
40 | NORTHWEST | 1478 | Goose Prairie Solar LLC | Bonneville Power Admin | 408665 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 48.4 | -29 | 29 | 14 | -48.4 | [6 empty] | Closed | 36 | 2.7735 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.645 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1478 | Goose Prairie Solar LLC | Bonneville Power Admin | 408666 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 48.4 | -29 | 29 | 14 | -48.4 | [6 empty] | Closed | 36 | -3.2343 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.645 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 1480 | OWNER1480 |  | 408683 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  | No Owner | 0 | 81.7 | -50.99 | 50.99 | 14 | -81.7 | [6 empty] | Closed | 75 | -7.47 | PV | 100 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.645 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 929 | Columbia Basin Hydro | Bonneville Power Admin | 408870 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 2.4 | 0.3 | 0.3 | 14 | -2.4 | [6 empty] | Closed | 2 | 0.3 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 929 | Columbia Basin Hydro | Bonneville Power Admin | 409591 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 6 | 0 | 0 | 14 | -6 | [6 empty] | Closed | 6 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 34.5 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 106 | Northern Lights Electric Co-op | Bonneville Power Admin | 410970 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 3 | 0 | 0 | 14 | -3 | [6 empty] | Closed | 3 | 0 | HY | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 412684 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 412685 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 10 | -0.8 | 0.8 | 14 | -10 | [6 empty] | Closed | 10 | 0 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 35 | Grant PUD |  | 461098 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20 | -35.2 | 35.2 | 35 | -20 | [6 empty] | Open | 0 | 0 | P3 | 20 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | P3 (Photovoltaic, Fixed) | 1
40 | NORTHWEST | 1458 | Energy Northwest Packwood | Bonneville Power Admin | 470473 | 1 | 1 | [12 empty] | Gen on HV |  |  |  | Missing PS |  |  | 0 | 26 | -8 | 23 | 14 | -26 | [6 empty] | Open | 0 | 0 | HY | 100 | PF<0.8 | YES | 0 | 0.2 | 0 |  |  |  | NAN | 69 |  |  | HY (Hydro) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 473782 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 81.3 | -53.4 | 53.4 | 937 | -81.3 | [6 empty] | Closed | 67.5 | -19.3254 | PV | 100 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.7 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 473851 | 1 | 1 | [17 empty] | Missing Sub R/X |  | 0 | 152.5 | -58.5 | 58.5 | 937 | -152.5 |  |  | REGC_A |  |  | REEC_A | Closed | 135 | 2.2304 | PV | 166.95 |  | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 34.5 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 473913 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 44.4 | -14.6 | 14.6 | 937 | -44.4 | [6 empty] | Closed | 44.4 | -3.1594 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | 2
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol | Bonneville Power Admin | 473962 | Z1 | Z1 | [15 empty] | Missing Model |  |  |  | 0 | 100.4 | -33 | 33 | 937 | -100.4 | [6 empty] | Closed | 100.4 | -13.9083 | W3 | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | Z1
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474412 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 6.8 | 2.8 | 2.8 | 14 | 2.2 | 9 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 6.8 | 0 | ST | 9 |  | NO | 0 | 1 | 3 | 0.27 | 0 | 0 | NAN | 13.8 |  | CHEM_WE4_13.8_G01 | ST (Steam Turbine) | 1
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474414 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 6.3 | 1.8 | 1.8 | 14 | -0.3 | 6 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 4.9 | 0 | ST | 6 |  | NO | 0 | 1 | 3 | 0.18 | 0 | 0 | NAN | 13.8 |  | CHEM_WE4_13.8_G02 | ST (Steam Turbine) | 1
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474415 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 39.2 | 13.5 | 13.5 | 14 | 0.8 | 40 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 37.2 | 0 | ST | 40 |  | NO | 0 | 1 | 3 | 1.2 | 0 | 0 | NAN | 13.8 |  | CHEM_WE4_13.8_G05 | ST (Steam Turbine) | 1 |  | PSS Exempt
40 | NORTHWEST | 47 | Cowlitz PUD | Bonneville Power Admin | 474422 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 18.8 | -5.43 | 7.18 | 14 | -2.8 | 16 |  | GENTPF |  | GGOV1 | EXST4B | Closed | 14.7 | 0 | ST | 16 |  | YES | 0 | 1 | 3 | 0.48 | 0 | 0 | NAN | 13.8 |  | COFFINRK_13.8_G04 | ST (Steam Turbine) | 1
40 | NORTHWEST | 451 | NextEra Energy | Bonneville Power Admin | 476104 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 200.2 | -96.9 | 96.9 | 14 | -200.2 | [6 empty] | Closed | 195 | -50.9314 | W3 | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 476157 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 200.2 | -96.9 | 96.9 | 14 | -200.2 | [6 empty] | Closed | 185 | 3.6293 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 476158 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 200.2 | -96.9 | 96.9 | 14 | -200.2 | [6 empty] | Closed | 185 | 3.6293 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 1474 | NewSun Energy Transmission LLC | Bonneville Power Admin | 476159 | 1 | 1 | [11 empty] | Gen at 0.0 |  |  |  | Missing Model |  |  |  | 0 | 200.2 | -96.9 | 96.9 | 14 | -200.2 | [6 empty] | Closed | 0 | 6.296 | PV | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | 1
40 | NORTHWEST | 937 | Avangrid Renewables LLC Iberdrol |  | 478060 | Z1 | Z1 | [15 empty] | Missing Model |  |  |  | 0 | 90 | 0 | 0 | 937 | -90 | [6 empty] | Closed | 84.1 | 0 | W3 | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | Z1
40 | NORTHWEST | 29 | Avista Corp. | Avista | 481871 | PV | PV | [15 empty] | Missing Model |  |  |  | 0 | 19.2 | -6.54 | 6.54 | 29 | -19.2 | [6 empty] | Closed | 8 | 3.2125 | PV | 19.2 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  | LIND SOLAR UN1 | PV (Photovoltaic) | PV
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 542867 | 12 | 12 | [10 empty] | Unreas Sat | [8 empty] | 0 | 407.5 | -132.5 | 195 | 76 | -4.3 | 403.2 |  | GENROU | PSS2B | GGOV1 | ESST1A_GE | Closed | 303.4 | 64.0778 | ST | 497 |  | NO | 0.003 | 0.243 | 4.66 | 23.1602 | 0.19 | 0.84 | 4.4211 | 15.5 |  |  | ST (Steam Turbine) | 12
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 542868 | 13 | 13 | [10 empty] | Unreas Sat | [8 empty] | 0 | 407.5 | -132.5 | 195 | 76 | -4.3 | 403.2 |  | GENROU | PSS2B | GGOV1 | ESST1A_GE | Closed | 303.4 | 74.7225 | ST | 497 |  | NO | 0.003 | 0.243 | 4.66 | 23.1602 | 0.19 | 0.84 | 4.4211 | 15.5 |  |  | ST (Steam Turbine) | 13
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 549110 | FD | FD | [15 empty] | Missing Model | Missing PS | Missing Sub R/X |  | 0 | 0 | -50 | 50 | 76 | 0 | [6 empty] | Closed | 0 | 0.93744 | SC | 50 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 21 |  |  | SC (Synchronous Condenser) | FD
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 549756 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 16.5 | -2.9582 | -2.9582 | 76 | -16.5 | [6 empty] | Closed | 9 | -2.958 | WT | 18.34 |  | NO | 0 | 0.144 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | G1
70 | PSCOLORADO | 66 | West Plains G&T |  | 71016 | W1 | W1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 60 | -27.2 | 27.2 | 65 | -60 |  |  | WT3G | WT3P | WT3T | WT3E | Closed | 15.6 | -5.7645 | W3 | 64.2 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.7 |  |  | W3 (Wind Turbine, Type 3) | W1
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79164 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 12.1 | -3.1352 | 4.0003 | 26 | -0.4 | 11.7 |  | GENTPJ | PFQRG | HYG3 | ESST4B | Closed | 11 | -0.89187 | HY | 12.1 |  | YES | 0.004 | 0.22 | 1.6 | 0.1936 | 0.07 | 0.31 | 4.4286 | 6.9 |  |  | HY (Hydro) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 551587 | G3 | G3 | [15 empty] | Missing Model |  |  |  | 0 | 4.8 | -1.2 | 1.2 | 76 | -4.8 | [6 empty] | Closed | 3.1 | 0.22122 | OT | 6 |  | NO | 0.02 | 0.15 | 0 |  |  |  | NAN | 4.16 |  |  | OT (Other) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552260 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 20.8 | -6.837 | 6.837 | 76 | -20.8 | [6 empty] | Closed | 0.9 | -2.9535 | WT | 21.9 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552378 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 2.925 | 0 | 0 | 76 | -2.925 | [6 empty] | Closed | 2.5 | 0 | WT | 3.656 |  | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 4.16 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552378 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 2.925 | 0 | 0 | 76 | -2.925 | [6 empty] | Closed | 2.5 | 0 | WT | 3.656 |  | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 4.16 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552418 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 96 | -46.02 | 46.02 | 76 | -96 | [6 empty] | Closed | 16.5 | -27.0165 | WT | 104 |  | NO | 0.008 | 0.2 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | 2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552433 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 25 | -2.8498 | 2.8498 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | -2.8498 | PV | 25 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552447 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 26.66 | -4.6867 | -4.6867 | 76 | -26.66 | [6 empty] | Closed | 18.7 | -4.687 | WT | 26.4 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552449 | G3 | G3 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 26.66 | -4.837 | -4.837 | 76 | -26.66 | [6 empty] | Closed | 19.3 | -4.837 | WT | 26.4 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552587 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 4.6 | -3.45 | 3.45 | 76 | -4.6 | [6 empty] | Closed | 2.9 | -0.17581 | OT | 5.75 | PF<-0.85 | NO | 0.006 | 0.301 | 0 |  |  |  | NAN | 4.2 |  |  | OT (Other) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 552587 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 0.663 | -0.36 | 0 | 76 | -0.663 | [6 empty] | Closed | 0.4 | -0.17581 | OT | 0.786 |  | NO | 0.018 | 0.218 | 0 |  |  |  | NAN | 4.2 |  |  | OT (Other) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553246 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 22 | -1.0356 | -1.0356 | 76 | -22 | [6 empty] | Closed | 5.1 | -1.036 | WT | 100 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553256 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 12.5 | -8.25 | 8.25 | 76 | -12.5 |  |  | REGC_A |  |  | REEC_A | Closed | 8.4 | -5.6792 | WT | 14.4 | PF<-0.85 | NO | 0 | 0.405 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553291 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 18 | -3.0053 | -3.0053 | 76 | -18 |  |  | REGC_A |  |  | REEC_A | Closed | 14.8 | -3.005 | PV | 22.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553314 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 2.925 | 0 | 0 | 76 | -2.925 | [6 empty] | Closed | 2.5 | 0 | WT | 3.656 |  | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 4.16 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553314 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 2.925 | 0 | 0 | 76 | -2.925 | [6 empty] | Closed | 2.5 | 0 | WT | 3.656 |  | NO | 0.005 | 0.155 | 0 |  |  |  | NAN | 4.16 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 553447 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 26.66 | -4.6867 | -4.6867 | 76 | -26.66 | [6 empty] | Closed | 18.7 | -4.687 | WT | 26.4 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 25 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554241 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 2.28 | 7 | -3.051 | 4.2 | 76 | -7 | [6 empty] | Closed | 5.747 | -2.5988 | GT | 15.75 |  | NO | 0.006 | 0.156 | 0 |  |  |  | NAN | 4.16 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554242 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 2.07 | 3 | -1.8 | 2.7 | 76 | -3 | [6 empty] | Closed | 2.463 | -1.0258 | GT | 4.45 | PF<0.8 | NO | 0.007 | 0.1 | 0 |  |  |  | NAN | 0.6 |  |  | GT (Gas Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554244 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 25.2 | 0 | 0 | 76 | -25.2 | [6 empty] | Closed | 18.4 | 0 | WT | 25.2 |  | NO | 0.016 | 0.53 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554246 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 7.5 | -1.2793 | -1.2793 | 76 | -7.5 | [6 empty] | Closed | 6.3 | -1.279 | WT | 10.8 |  | NO | 0 | 0.943 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554254 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 13.3 | -1.2592 | -1.2592 | 76 | -13.3 | [6 empty] | Closed | 2.6 | -1.259 | WT | 17.6 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.8 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554257 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 14 | -9.9 | 9.9 | 76 | -14 |  |  | REGC_A |  |  | REEC_A | Closed | 9 | -5.1939 | PV | 18 | PF<-0.85 | NO | 0 | 0.405 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554291 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 23.4 | -3.8378 | -3.8378 | 76 | -23.4 |  |  | REGC_A |  |  | REEC_A | Closed | 18.9 | -3.838 | PV | 29.25 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554400 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 25.2 | -3.7566 | -3.7566 | 76 | -25.2 |  |  | REGC_A |  |  | REEC_A | Closed | 18.5 | -3.757 | WT | 25.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554448 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 25 | -2.7501 | 2.7501 | 76 | -25 |  |  | REGC_A |  |  | REEC_A | Closed | 19.3 | -2.7501 | PV | 25 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554452 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.49952 | 0.49952 | 76 | -3.6 | [6 empty] | Closed | 2.46 | 0.5 | WT | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554452 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.49952 | 0.49952 | 76 | -3.6 | [6 empty] | Closed | 2.46 | 0.5 | WT | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554452 | G3 | G3 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.49952 | 0.49952 | 76 | -3.6 | [6 empty] | Closed | 2.46 | 0.5 | WT | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554452 | G4 | G4 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 3.6 | 0.49952 | 0.49952 | 76 | -3.6 | [6 empty] | Closed | 2.46 | 0.5 | WT | 3.6 |  | NO | 0.016 | 0.77 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554487 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 13 | -3.5206 | -3.5206 | 76 | -13 | [6 empty] | Closed | 9.7 | -3.521 | WT | 16 |  | NO | 0.12 | 0.74 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 554986 | G1 | G1 | [5 empty] | At Mvar Limit | [13 empty] | -28.35 | 28.35 | -17.01 | 17.01 | 76 | -28.35 |  |  | REGC_A |  |  | REEC_A | Closed | 17.4 | 17.01 | PV | 25.56 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 555214 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 6.8 | -0.97743 | -0.97743 | 76 | -6.8 | [6 empty] | Closed | 3.9 | -0.977 | WT | 7.01 |  | NO | 999 | 999 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 555216 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | -2 | 2 | -0.27569 | -0.27569 | 76 | -2 | [6 empty] | Closed | 1.1 | -0.276 | WT | 2.06 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 555220 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 6.8 | -0.97743 | -0.97743 | 76 | -6.8 | [6 empty] | Closed | 3.9 | -0.977 | WT | 7.01 |  | NO | 999 | 999 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 555222 | 1 | 1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | -2 | 2 | -0.27569 | -0.27569 | 76 | -2 | [6 empty] | Closed | 1.1 | -0.276 | WT | 2.06 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557004 | 16 | 16 | [9 empty] | Unreas H | [9 empty] | 17 | 41.5 | -15 | 22 | 76 | 35.441 | 76.941 |  | GENROU | PSS2B | GGOV1 | ESAC7B | Closed | 39.5 | 17.0803 | JE | 76.94 |  | NO | 0.005 | 0.181 | 1.088 | 0.83711 | 0.109 | 0.501 | 4.5963 | 13.8 |  |  | JE (Jet Engine) | 16
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557066 | G1 | G1 | [9 empty] | Unreas H | [9 empty] | 10 | 46 | -15.12 | 22.28 | 76 | 0.843 | 46.843 |  | GENROU | PSS2B | GGOV1 | REXS | Closed | 46 | -4.8995 | JE | 71.2 |  | NO | 0 | 0.156 | 1.341 | 0.95479 | 0.11 | 0.49 | 4.4545 | 13.8 |  |  | JE (Jet Engine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557109 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 14.7 | -4.3058 | -4.3058 | 76 | -14.7 | [6 empty] | Closed | 13.1 | -4.306 | WT | 16.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557113 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 3.1 | -1.412 | -1.412 | 76 | -3.1 | [6 empty] | Closed | 2.2 | -1.412 | IC | 3.874 |  | NO | 0 | 0.102 | 0 |  |  |  | NAN | 0.48 |  |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557113 | G3 | G3 | [15 empty] | Missing Model |  |  |  | 0 | 2.95 | -1.344 | -1.344 | 76 | -2.95 | [6 empty] | Closed | 2.2 | -1.344 | IC | 3.686 |  | NO | 0 | 0.095 | 0 |  |  |  | NAN | 0.48 |  |  | IC (Internal Combustion) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G1 | G1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 2.67 | -0.379 | -0.379 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.379 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G2 | G2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 2.67 | -0.379 | -0.379 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.379 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G3 | G3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 2.67 | -0.379 | -0.379 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.379 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557116 | G4 | G4 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 2.67 | -0.379 | -0.379 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.379 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557120 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 22 | -2.3796 | -2.3796 | 76 | -22 |  |  | REGC_A |  |  | REEC_A | Closed | 16.7 | -2.38 | PV | 23 |  | NO | 0 | 999 | 0 |  |  |  | NAN | 0.69 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557216 | G5 | G5 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 1.8 | 2.67 | -0.38024 | -0.38024 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.38 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557216 | G6 | G6 |  |  |  |  | Exceed Gen Limit |  |  |  |  | Unreas H | Unreas Sat | [8 empty] | 1.8 | 2.67 | -0.38024 | -0.38024 | 76 | -2.67 |  |  | GENTPJ |  |  |  | Closed | 2.1 | -0.38 | IC | 3.63 |  | NO | 0 | 0.159 | 0.415 | 0.015064 | 0.2 | 0.8 | 4 | 4.16 |  |  | IC (Internal Combustion) | G6
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557221 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 22.5 | 0 | 0 | 76 | -22.5 | [6 empty] | Closed | 18.2 | 0 | WT | 22.5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.36 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557259 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 18 | -1.198 | -1.198 | 76 | -18 |  |  | REGC_A |  |  |  | Closed | 5.9 | -1.198 | WT | 17.5 |  | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557270 | 1 | 1 | [6 empty] | Limit Power Fact | [8 empty] | Missing Model |  |  |  | 0 | 23 | -17.25 | 17.25 | 76 | -23 | [6 empty] | Closed | 21.2 | -9.004 | WT | 27.5 | PF<-0.85 | NO | 0 | 999 | 0 |  |  |  | NAN | 0.55 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557277 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 19 | -2.7074 | -2.7074 | 76 | -19 |  |  | REGC_A |  |  |  | Closed | 19 | -2.707 | PV | 22.05 |  | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557342 | G1 | G1 | [9 empty] | Unreas H | [9 empty] | 0 | 21.15 | -6.95 | 10.25 | 76 | 50.026 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 14.8 | 5.6261 | OT | 23.5 |  | NO | 0.001 | 0.19 | 1.25 | 0.29375 | 0.136 | 0.4 | 2.9412 | 13.8 |  |  | OT (Other) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557352 | D1 | D1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | -4.2 | 19.8 | -1.8951 | -1.8951 | 76 | -19.8 | [6 empty] | Closed | 13.3 | -1.895 | WT | 22 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.55 |  |  | WT (Wind Turbine) | D1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557435 | FD | FD | [15 empty] | Missing Model |  | Missing Sub R/X |  | 0 | 0 | -24 | 24 | 76 | 0 | [6 empty] | Closed | 0 | -1.9367 | SC | 24 | PF<0.8 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.48 |  |  | SC (Synchronous Condenser) | FD
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557442 | G2 | G2 | [9 empty] | Unreas H | [9 empty] | 0 | 21.15 | -6.95 | 10.25 | 76 | 50.026 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 14.8 | 5.6261 | OT | 23.5 |  | NO | 0.001 | 0.19 | 1.25 | 0.29375 | 0.136 | 0.4 | 2.9412 | 13.8 |  |  | OT (Other) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557481 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 230 | -69.4 | 102.3 | 76 | -230 | [6 empty] | Closed | 125.4 | 90.5113 | WT | 234.6 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557482 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 230 | -69.4 | 102.3 | 76 | -230 | [6 empty] | Closed | 125.4 | 90.5113 | WT | 234.6 |  | NO | 0 | 0.2 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557494 | G3 | G3 | [15 empty] | Missing Model |  |  |  | 0 | 3.2 | -1.55 | 1.55 | 76 | -3.2 | [6 empty] | Closed | 1.8 | -0.063257 | GT | 3.55 |  | NO | 0 | 0.29 | 0 |  |  |  | NAN | 13.8 |  |  | GT (Gas Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557495 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 3.1 | -1.5 | 1.5 | 76 | -3.1 | [6 empty] | Closed | 2.5 | -0.12765 | OT | 3.477 |  | NO | 0 | 0.253 | 0 |  |  |  | NAN | 12.47 |  |  | OT (Other) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557495 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 3.1 | -1.5 | 1.5 | 76 | -3.1 | [6 empty] | Closed | 2.5 | -0.12765 | OT | 3.477 |  | NO | 0 | 0.253 | 0 |  |  |  | NAN | 12.47 |  |  | OT (Other) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557495 | G4 | G4 | [15 empty] | Missing Model |  |  |  | 0 | 9.5 | -4.6 | 4.6 | 76 | -9.5 | [6 empty] | Closed | 8.8 | -0.12765 | OT | 10.549 |  | NO | 0 | 0.22 | 0 |  |  |  | NAN | 12.47 |  |  | OT (Other) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557542 | G3 | G3 | [9 empty] | Unreas H | [9 empty] | 0 | 21.15 | -6.95 | 10.25 | 76 | 50.026 | 71.176 |  | GENTPJ | PSS2B | GGOV1 | ESAC7B | Closed | 14.8 | 5.6261 | OT | 23.5 |  | NO | 0.001 | 0.19 | 1.25 | 0.29375 | 0.136 | 0.4 | 2.9412 | 13.8 |  |  | OT (Other) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557642 | G4 | G4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 29.7 | -9.8 | 14.4 | 76 | -29.7 |  |  | GENTPJ | PSS2A |  | ESAC8B_GE | Closed | 14.8 | 8.9261 | OT | 33 |  | NO | 0.003 | 0.25 | 5.51 | 1.8183 | 0.207 | 0.48 | 2.3188 | 13.8 |  |  | OT (Other) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557690 | G5 | G5 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 5.28 | 1.3588 | 1.3588 | 76 | -5.28 | [6 empty] | Closed | 5 | 1.359 | IC | 7.5 |  | NO | 0 | 0.13 | 0 |  |  |  | NAN | 0.6 |  |  | IC (Internal Combustion) | G5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557709 | 17 | 17 | [9 empty] | Unreas H | [9 empty] | 17 | 44 | -15 | 22 | 76 | 4.2 | 48.2 |  | GENQEC | PSS2C | GGOV1 | ESAC7B | Closed | 42.8 | 17.2441 | JE | 76.941 |  | NO | 0.006 | 0.181 | 1.117 | 0.85943 |  |  | NAN | 13.8 |  |  | JE (Jet Engine) | 17
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557742 | M1 | M1 | [15 empty] | Missing Model |  |  |  | -17.9 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -16.1 | 0 | MP | 17.9 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | MP (Motor/Pump) | M1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557742 | M2 | M2 | [15 empty] | Missing Model |  |  |  | -11.6 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -10.4 | 0 | MP | 11.6 |  | NO | 0.005 | 0.25 | 0 |  |  |  | NAN | 13.8 |  |  | MP (Motor/Pump) | M2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557842 | M3 | M3 | [15 empty] | Missing Model |  |  |  | -8.6 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -8 | 0 | MP | 8.6 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | MP (Motor/Pump) | M3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557942 | M4 | M4 | [15 empty] | Missing Model |  |  |  | -8.2 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -7.6 | 0 | MP | 8.2 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | MP (Motor/Pump) | M4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 557942 | M5 | M5 | [15 empty] | Missing Model |  |  |  | -5.6 | 0 | 0 | 0 | 76 | 0 | [6 empty] | Closed | -5.2 | 0 | MP | 5.6 |  | NO | 0 | 0.16 | 0 |  |  |  | NAN | 13.8 |  |  | MP (Motor/Pump) | M5
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558088 | D1 | D1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 22 | -4.2828 | -4.2828 | 76 | -22 | [6 empty] | Closed | 11.8 | -4.283 | WT | 24.44 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | D1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558130 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 9.2 | -1.1833 | -1.1833 | 76 | -9.2 | [6 empty] | Closed | 3.6 | -1.183 | WT | 9.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558230 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 9.2 | -1.05 | -1.05 | 76 | -9.2 | [6 empty] | Closed | 3.6 | -1.05 | WT | 9.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558248 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 15 | -4.93 | 7.26 | 76 | -15 | [6 empty] | Closed | 10.5 | 2.7399 | WT | 16.67 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558259 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [14 empty] | 0 | 22.5 | -1.5229 | -1.5229 | 76 | -22.5 |  |  | REGC_A |  |  |  | Closed | 7.5 | -1.523 | WT | 22.5 |  | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558266 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 4.5 | -0.85285 | -0.85285 | 76 | -4.5 | [6 empty] | Closed | 4.2 | -0.853 | WT | 9.375 |  | NO | 0 | 0.211 | 0 |  |  |  | NAN | 13.8 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558267 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 12.6 | -7.56 | 7.56 | 76 | -12.6 | [6 empty] | Closed | 8.6 | 0.28333 | WT | 13 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558269 | G1 | G1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 20 | -2.5506 | -2.5506 | 76 | -20 | [6 empty] | Closed | 17.9 | -2.551 | PV | 22.05 |  | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.6 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558277 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 24.444 | -6.126 | 6.126 | 76 | -24.444 | [6 empty] | Closed | 17.6 | -0.88006 | WT | 25.2 |  | NO | 1000 | 1000 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558321 | G1 | G1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 19.35 | -6.73 | 9.39 | 76 | 10.179 | 29.529 |  | GENROU | PSS2A | GGOV1 | ESAC8B_GE | Closed | 15.2 | 0.73912 | GT | 21.56 |  | NO | 0.004 | 0.17 | 5.116 | 1.103 | 0.282 | 0.906 | 3.2128 | 13.8 |  |  | GT (Gas Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 558366 | G2 | G2 |  |  |  |  | Exceed Gen Limit | [5 empty] | Unreas Sat | [8 empty] | 0 | 15.1 | -2.8022 | -2.8022 | 76 | -15.1 |  |  | GENTPJ |  |  |  | Closed | 13.8 | -2.802 | WT | 17.5 |  | NO | 0 | 0.211 | 1.52 | 0.266 | 0.2 | 0.8 | 4 | 6.9 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560026 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 155 | -98.407 | 98.407 | 76 | -155 |  |  | REGC_A |  |  | REEC_A | Closed | 145.5 | 80.9998 | PV | 183.6 | PF<-0.85 | NO | 0 | 10 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560058 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 457 | -150.209 | 221.335 | 76 | -457 | [6 empty] | Closed | 388.5 | 8.9347 | WT | 507.778 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560088 | G1 | G1 | [8 empty] | RX Ratio | [6 empty] | Missing Model |  |  |  | 0 | 11.122 | -3.65 | 5.387 | 76 | -11.122 | [6 empty] | Closed | 0.6 | -0.36762 | WT | 12.4 |  | NO | 2.25 | 1.09 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560111 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 103.5 | -34.019 | 50.127 | 76 | -103.5 | [6 empty] | Closed | 92.1 | -20.1102 | WT | 115 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.7 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560441 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 60 | -19.72 | 29.06 | 76 | -60 | [6 empty] | Closed | 43.6 | 8.8744 | WT | 64.8 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.63 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560503 | G4 | G4 | [6 empty] | Limit Power Fact | [12 empty] | -8.7 | 8.7 | -8 | 5.6 | 76 | -8.7 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | WT | 11.18 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.48 |  |  | WT (Wind Turbine) | G4
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 560894 | G1 | G1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 57.75 | -38.307 | 38.307 | 76 | -57.75 |  |  | REGC_A |  |  |  | Closed | 38.4 | -7.1618 | PV | 157.5 | PF<-0.85 | NO | 0 | 0.523 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561026 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 155 | -98.407 | 98.407 | 76 | -155 |  |  | REGC_A |  |  | REEC_A | Closed | 141.2 | 39.4902 | PV | 183.6 | PF<-0.85 | NO | 0 | 10 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561336 | B1 | B1 | [6 empty] | Limit Power Fact | [12 empty] | -10 | 9.999 | -10 | 10 | 76 | -9.999 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 11.6 | PF<0.8 | NO | 0 | 99 | 0 |  |  |  | NAN | 0.48 |  |  | BA (Energy Storage, Battery) | B1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561450 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 23.3 | -6.212 | 9.154 | 76 | -23.3 | [6 empty] | Closed | 17.7 | 0.30252 | WT | 25.9 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561477 | D1 | D1 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 4.75 | -0.19721 | -0.19721 | 76 | -4.75 | [6 empty] | Closed | 0.6 | -0.197 | WT | 5 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.8 |  |  | WT (Wind Turbine) | D1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561478 | D2 | D2 |  |  |  |  | Exceed Gen Limit | [10 empty] | Missing Model |  |  |  | 0 | 25.25 | -0.98605 | -0.98605 | 76 | -25.25 | [6 empty] | Closed | 3 | -0.986 | WT | 32.6 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.72 |  |  | WT (Wind Turbine) | D2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561894 | G2 | G2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 74.25 | -47.604 | 47.604 | 76 | -74.25 |  |  | REGC_A |  |  | REEC_A | Closed | 49.6 | -5.9251 | PV | 88.2 | PF<-0.85 | NO | 0 | 0.523 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 561990 | G2 | G2 | [8 empty] | RX Ratio | [10 empty] | 0 | 151.2 | -52.164 | 71.988 | 76 | -151.2 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | W4 | 168 |  | NO | 0.3 | 0.17 | 0 |  |  |  | NAN | 0.65 |  |  | W4 (Wind Turbine, Type 4) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 562026 | G3 | G3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 155 | -98.407 | 98.407 | 76 | -155 |  |  | REGC_A |  |  | REEC_A | Closed | 141.2 | 45.0953 | PV | 183.6 | PF<-0.85 | NO | 0 | 10 | 0 |  |  |  | NAN | 0.63 |  |  | PV (Photovoltaic) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 563308 | G3 | G3 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 54 | -33.6 | 33.6 | 76 | -54 |  |  | REGC_A |  |  | REEC_A | Closed | 7.3 | 14.0695 | WT | 63.6 | PF<-0.85 | NO | 0.3 | 1.2 | 0 |  |  |  | NAN | 0.72 |  |  | WT (Wind Turbine) | G3
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 565994 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 250 | -80 | 121 | 76 | -250 | [6 empty] | Closed | 177.1 | 116.2535 | WT | 280 |  | NO | 0 | 0.55 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | 1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 568006 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 9.2 | 0 | 0 | 76 | -9.2 | [6 empty] | Closed | 6.9 | 0 | WT | 9.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 568007 | G2 | G2 | [15 empty] | Missing Model |  |  |  | 0 | 9.2 | 0 | 0 | 76 | -9.2 | [6 empty] | Closed | 6.9 | 0 | WT | 9.2 |  | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G2
54 | ALBERTA | 76 | Alberta Int. Electric System |  | 569049 | G1 | G1 | [15 empty] | Missing Model |  |  |  | 0 | 80 | -26.3 | 38.75 | 76 | -80 | [6 empty] | Closed | 62.6 | 0.8782 | WT | 89 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | G1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 1 | 1 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 2 | 2 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 2
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 3 | 3 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 3
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 4 | 4 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 4
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 5 | 5 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 5
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 6 | 6 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 6
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 7 | 7 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 7
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 8 | 8 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 8
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 621521 | 9 | 9 | [9 empty] | Unreas H | Unreas Sat | [8 empty] | 0 | 5.9 | -3.7625 | 4.3875 | 78 | -5.9 |  |  | GENTPJ |  |  |  | Open | 0 | 0 | IC | 7.37 | PF<-0.85 | YES | 0 | 0.176 | 0.94 | 0.069278 | 1.035 | 1.281 | 1.2377 | 13.8 |  |  | IC (Internal Combustion) | 9
62 | MONTANA | 78 | NorthWestern Energy |  | 622521 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 3.4 | 7 | -2.8778 | 2.8778 | 78 | 2 | 9 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 6.3 | 2.8778 | HY | 7 |  | YES | 0.012 | 0.2 | 1.59 | 0.1113 | 0.174 | 0.408 | 2.3448 | 6.6 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 622521 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 3.4 | 7 | -2.8778 | 2.8778 | 78 | 2 | 9 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 6.3 | 2.8778 | HY | 7 |  | YES | 0.012 | 0.2 | 1.59 | 0.1113 | 0.174 | 0.408 | 2.3448 | 6.6 |  |  | HY (Hydro) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 622521 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 3.4 | 7 | -2.6889 | 2.6889 | 78 | 2 | 9 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 6.4 | 2.6889 | HY | 7 |  | YES | 0.012 | 0.2 | 1.59 | 0.1113 | 0.174 | 0.408 | 2.3448 | 6.6 |  |  | HY (Hydro) | 3
62 | MONTANA | 78 | NorthWestern Energy |  | 622531 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 11.5 | -3.225 | 3.9 | 78 | 2.01 | 13.51 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 10.7 | 3.9 | HY | 10 |  | YES | 0 | 0.204 | 4.055 | 0.4055 | 0.165 | 0.397 | 2.4061 | 6.6 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622531 | 2 | 2 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 11.5 | -3.225 | 3.9 | 78 | 2.01 | 13.51 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 10.7 | 3.9 | HY | 11.5 |  | YES | 0 | 0.204 | 4.055 | 0.46632 | 0.165 | 0.397 | 2.4061 | 6.6 |  |  | HY (Hydro) | 2 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622531 | 3 | 3 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 11.5 | -3.225 | 3.9 | 78 | 2.01 | 13.51 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 10.7 | 3.9 | HY | 10 |  | YES | 0 | 0.204 | 4.055 | 0.4055 | 0.165 | 0.397 | 2.4061 | 6.6 |  |  | HY (Hydro) | 3 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622532 | 4 | 4 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 11.5 | -3.225 | 3.9 | 78 | 2.01 | 13.51 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 10.7 | 3.9 | HY | 11.5 |  | YES | 0 | 0.204 | 4.055 | 0.46632 | 0.165 | 0.397 | 2.4061 | 6.6 |  |  | HY (Hydro) | 4 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622532 | 5 | 5 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 11.5 | -3.225 | 3.9 | 78 | 2.01 | 13.51 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 10.7 | 3.9 | HY | 10 |  | YES | 0 | 0.204 | 4.055 | 0.4055 | 0.165 | 0.397 | 2.4061 | 6.6 |  |  | HY (Hydro) | 5 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622532 | 6 | 6 | [5 empty] | At Mvar Limit | [13 empty] | 5 | 11.5 | -3.375 | 4.5 | 78 | 2.01 | 13.51 |  | GENTPJ |  | HYG3 | ESST4B | Closed | 10.5 | 4.5 | HY | 10 |  | YES | 0 | 0.204 | 4.055 | 0.4055 | 0.165 | 0.397 | 2.4061 | 6.6 |  |  | HY (Hydro) | 6 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622541 | 1 | 1 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 11 | 31 | -17 | 17 | 78 | 0.32 | 31.32 |  | (GENTPJ) |  | (HYGOV4) | (ESDC1A) | Closed | 31 | 17 | HY | 35.5 |  | YES | 0.002 | 0.345 | 0 |  | 0.3017 | 0.6096 | 2.0206 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622541 | 2 | 2 | [5 empty] | At Mvar Limit |  |  |  |  | Unreas Sat | [8 empty] | 11 | 31 | -17 | 17 | 78 | 0.32 | 31.32 |  | (GENTPJ) |  | (HYGOV4) | (ESDC1A) | Closed | 31 | 17 | HY | 35.5 |  | YES | 0.002 | 0.42 | 0 |  | 0.3017 | 0.6096 | 2.0206 | 13.8 |  |  | HY (Hydro) | 2 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 622551 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 9 | 24.5 | -11.6071 | 19.25 | 78 | 0.9 | 25.4 |  | GENTPJ | PSS2A | HYG3 | ESST4B | Closed | 23.5 | 12.8558 | HY | 35 | PF<0.8 | YES | 0.006 | 0.51 | 1.68 | 0.588 | 0.29 | 0.472 | 1.6276 | 13.8 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 622591 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 7.8 | -3.58 | 3.58 | 78 | -7.8 | [6 empty] | Closed | 7.8 | -3.2714 | HY | 8.22 |  | NO | 0 | 0.194 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 622591 | 2 | 2 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 5.4 | -2.57 | 2.57 | 78 | -5.4 | [6 empty] | Closed | 5.4 | -2.57 | HY | 5.89 |  | NO | 0 | 0.213 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 623511 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 1 | 6 | -0.75806 | 1.0887 | 78 | -6 | [6 empty] | Closed | 6 | 0.60536 | HY | 7.5 |  | YES | 0 | 0.203 | 0 |  |  |  | NAN | 6.6 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 623511 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 1 | 6 | -0.75806 | 1.0887 | 78 | -6 | [6 empty] | Closed | 6 | 0.60536 | HY | 7.5 |  | YES | 0 | 0.203 | 0 |  |  |  | NAN | 6.6 |  |  | HY (Hydro) | 2
62 | MONTANA | 32 | Portland General Elec |  | 623527 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 8.883 | 177.66 | -93.018 | 93.018 | 78 | -177.66 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 53.5 | -93.018 | WT | 200.619 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | 1
62 | MONTANA | 32 | Portland General Elec |  | 623528 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 1.512 | 30.24 | -14.64 | 14.64 | 78 | -30.24 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 9.1 | -14.64 | WT | 33.6 |  | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 623531 | 1 | 1 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 623531 | 2 | 2 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 623531 | 3 | 3 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 3
62 | MONTANA | 78 | NorthWestern Energy |  | 623531 | 4 | 4 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 4
62 | MONTANA | 78 | NorthWestern Energy |  | 623531 | 5 | 5 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 5
62 | MONTANA | 78 | NorthWestern Energy |  | 623531 | 6 | 6 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 6
62 | MONTANA | 78 | NorthWestern Energy |  | 623532 | 10 | 10 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 10
62 | MONTANA | 78 | NorthWestern Energy |  | 623532 | 11 | 11 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 11
62 | MONTANA | 78 | NorthWestern Energy |  | 623532 | 12 | 12 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 12
62 | MONTANA | 78 | NorthWestern Energy |  | 623532 | 7 | 7 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 7
62 | MONTANA | 78 | NorthWestern Energy |  | 623532 | 8 | 8 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 8
62 | MONTANA | 78 | NorthWestern Energy |  | 623532 | 9 | 9 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 9
62 | MONTANA | 78 | NorthWestern Energy |  | 623533 | 13 | 13 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 13
62 | MONTANA | 78 | NorthWestern Energy |  | 623533 | 14 | 14 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 14
62 | MONTANA | 78 | NorthWestern Energy |  | 623533 | 15 | 15 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 15
62 | MONTANA | 78 | NorthWestern Energy |  | 623533 | 16 | 16 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 16
62 | MONTANA | 78 | NorthWestern Energy |  | 623533 | 17 | 17 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 17
62 | MONTANA | 78 | NorthWestern Energy |  | 623533 | 18 | 18 | [7 empty] | PSS No Ex | [11 empty] | 2.5 | 9.738 | -4.715 | 6.035 | 78 | -0.00099974 | 9.737 |  | GENQEC | PSS2C | GGOV1 |  | Closed | 9.738 | 0.44362 | IC | 11.457 |  | NO | 0 | 0.182 | 1.24 | 0.14207 |  |  | NAN | 13.8 |  |  | IC (Internal Combustion) | 18
62 | MONTANA | 30 | Puget Sound Energy |  | 623546 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 126.9 | -71.92 | 71.92 | 78 | -126.9 | [6 empty] | Closed | 38 | -8.0526 | WT | 145.8 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | 1
62 | MONTANA | 30 | Puget Sound Energy |  | 623547 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 121.26 | -68.72 | 68.72 | 78 | -121.26 | [6 empty] | Closed | 36 | -7.0395 | WT | 139.32 |  | NO | 0 | 1 | 0 |  |  |  | NAN | 0.69 |  |  | WT (Wind Turbine) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 623566 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 20.2 | -15.067 | 15.067 | 78 | -20.2 |  |  | REGC_A |  |  | REEC_A | Closed | 20 | -3.2151 | WT | 25.2 | PF<-0.85 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.6 |  |  | WT (Wind Turbine) | 1
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 624541 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 20 | -1.9714 | 1.9714 | 78 | -20 |  |  | REGC_A | WTGPT_A | WTGT_A | REEC_A | Closed | 6 | 1.9714 | W3 | 30 |  | YES | 0 | 0.8 | 0 |  |  |  | NAN | 0.69 |  |  | W3 (Wind Turbine, Type 3) | 1 |  | PSS Exempt
62 | MONTANA | 50 | US Bur Reclam |  | 625521 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 18.5 | -2.2 | 5.5 | 78 | -2.4e-07 | 18.5 |  | GENTPJ | PSS2B | HYGOV4 | ESST4B | Closed | 10 | 5.5 | HY | 16.67 |  | YES | 0.007 | 0.26 | 3.24 | 0.54011 | 0.11 | 0.55 | 5 | 6.9 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 50 | US Bur Reclam |  | 625522 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 18.5 | -5.3 | 7.1 | 78 | -2.4e-07 | 18.5 |  | GENTPJ | PSS2B | HYGOV4 | ESST4B | Closed | 10 | 7.1 | HY | 16.67 |  | YES | 0.007 | 0.26 | 3.24 | 0.54011 | 0.11 | 0.55 | 5 | 6.9 |  |  | HY (Hydro) | 1
62 | MONTANA | 50 | US Bur Reclam |  | 625523 | 1 | 1 | [5 empty] | At Mvar Limit | [13 empty] | 0 | 15.5 | -5.3 | 7.1 | 78 | 3 | 18.5 |  | GENTPJ | PSS2B | HYGOV4 | ESST4B | Closed | 10 | 7.1 | HY | 16.67 |  | YES | 0.007 | 0.26 | 3.24 | 0.54011 | 0.11 | 0.55 | 5 | 6.9 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 627521 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 1.7 | 2.8 | -3 | 3 | 78 | -2.8 | [6 empty] | Closed | 2.2 | -0.68989 | HY | 2.8 | PF<0.8 | YES | 0 | 0.108 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 627521 | 2 | 2 | [15 empty] | Missing Model |  |  |  | 0 | 3.79 | -1.935 | 2.82 | 78 | -3.79 | [6 empty] | Closed | 2.9 | -0.68989 | HY | 4.4 |  | YES | 0.003 | 0.235 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 2
62 | MONTANA | 78 | NorthWestern Energy |  | 627521 | 3 | 3 | [15 empty] | Missing Model |  |  |  | 1.7 | 2.8 | -3 | 3 | 78 | -2.8 | [6 empty] | Closed | 2.2 | -0.68989 | HY | 2.8 | PF<0.8 | YES | 0 | 0.108 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 3
62 | MONTANA | 78 | NorthWestern Energy |  | 627522 | 4 | 4 | [15 empty] | Missing Model |  |  |  | 0 | 3.79 | -1.935 | 2.82 | 78 | -3.79 | [6 empty] | Closed | 2.9 | -0.68989 | HY | 4.4 |  | YES | 0.003 | 0.235 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 4
62 | MONTANA | 78 | NorthWestern Energy |  | 627522 | 5 | 5 | [15 empty] | Missing Model |  |  |  | 0 | 3.79 | -1.935 | 2.82 | 78 | -3.79 | [6 empty] | Closed | 2.9 | -0.68989 | HY | 4.4 |  | YES | 0.003 | 0.235 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 5
62 | MONTANA | 78 | NorthWestern Energy |  | 627522 | 6 | 6 | [15 empty] | Missing Model |  |  |  | 2.5 | 3.75 | -3 | 3 | 78 | -3.75 | [6 empty] | Closed | 2.9 | -0.68989 | HY | 3.75 | PF<0.8 | YES | 0 | 0.14 | 0 |  |  |  | NAN | 2.4 |  |  | HY (Hydro) | 6
62 | MONTANA | 622 | Montana IPP (Ind. Power Prods) |  | 627531 | 1 | 1 | [5 empty] | At Mvar Limit | [9 empty] | Missing Model |  |  |  | 0 | 9.66 | -4.21 | 4.21 | 78 | -9.66 | [6 empty] | Closed | 9 | 4.21 | HY | 9.66 |  | NO | 0 | 0.22 | 0 |  |  |  | NAN | 4.16 |  |  | HY (Hydro) | 1
62 | MONTANA | 78 | NorthWestern Energy |  | 629521 | 1 | 1 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7.6 | -5 | 5.26 | 78 | -0.6 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 6.8 | 1.0117 | HY | 8.75 | PF<-0.85 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 1 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629521 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -5 | 5.41 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 6.3 | 1.0117 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 2 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629521 | 3 | 3 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7.6 | -5 | 5.26 | 78 | -0.6 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 6.8 | 1.0117 | HY | 8.75 | PF<-0.85 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 3 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629522 | 4 | 4 | [10 empty] | Unreas Sat | [8 empty] | 0 | 6.33 | -4.875 | 4.575 | 78 | 0.67 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 5.7 | 1.0117 | HY | 8.75 | PF<-0.85 | YES | 0.007 | 0.192 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 4 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629522 | 5 | 5 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -5 | 5.41 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 6.3 | 1.0117 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 5 |  | PSS Exempt
62 | MONTANA | 78 | NorthWestern Energy |  | 629522 | 6 | 6 | [10 empty] | Unreas Sat | [8 empty] | 0 | 7 | -5 | 5.47 | 78 | -3e-08 | 7 |  | GENTPJ |  | HYGOV | ESST4B | Closed | 6.1 | 1.0117 | HY | 8.75 | PF<0.8 | YES | 0.008 | 0.224 | 2.59 | 0.22662 | 0.185 | 0.394 | 2.1297 | 6.6 |  |  | HY (Hydro) | 6 |  | PSS Exempt
63 | WAPA U.W. | 43 | US Army Corps of Engrs |  | 631002 | 2 | 2 | [10 empty] | Unreas Sat | [8 empty] | 0 | 18 | -9 | 11 | 77 | 1.21 | 19.21 |  | GENTPJ | PSS2A | HYGOV4 | ESST1A_GE | Closed | 18 | 10.8096 | HY | 19.21 |  | NO | 0.004 | 0.25 | 2.03 | 0.38996 | 0.17 | 0.33 | 1.9412 | 13.8 |  |  | HY (Hydro) | 2
73 | WAPA R.M. | 50 | US Bur Reclam |  | 79176 | 1 | 1 |  |  |  | Unapproved Gen Model | [15 empty] | 0 | 1.3 | 0 | 0 | 26 | -1.3 |  |  | GENTPJ | PFQRG |  | ESST6B | Closed | 1 | 0 | HY | 1.35 |  | NO | 0.009 | 0.23 | 0.9 | 0.01215 | 0.05 | 0.39 | 7.8 | 2.4 |  |  | HY (Hydro) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 640076 | CL | CL | [16 empty] | Missing PS |  |  | -1.5 | -1.5 | -0.5 | -0.5 | 24 | 1.5 | [6 empty] | Open | 0 | 0 | GT | 183 | PF<0.8 | YES | 0.002 | 0.156 | 0 |  |  |  | NAN | 34.5 |  | TSLACHLR | GT (Gas Turbine) | CL
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 640080 | 1 | 1 | [15 empty] | Missing Model |  |  |  | 0 | 10.1 | -2.6952 | 2.6952 | 24 | -10.1 | [6 empty] | Closed | 8.2 | 0.084051 | PV | 10 |  | NO | 0 | 0.179 | 0 |  |  |  | NAN | 0.38 |  | PATUA_PV | PV (Photovoltaic) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640252 | 1 | 1 | [8 empty] | RX Ratio | [10 empty] | 0 | 8 | -2.63 | 2.63 | 24 | -8 |  |  | REGC_A |  |  | REEC_A | Closed | 5 | -0.049499 | PV | 8 |  | NO | 0.297 | 0.005 | 0 |  |  |  | NAN | 0.69 |  | TUNGSTEN | PV (Photovoltaic) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640252 | 2 | 2 | [8 empty] | RX Ratio | [10 empty] | 0 | 8 | -2.63 | 2.63 | 24 | -8 |  |  | REGC_A |  |  | REEC_A | Closed | 5 | -0.049499 | PV | 8 |  | NO | 0.297 | 0.005 | 0 |  |  |  | NAN | 0.69 |  | TUNGSTEN | PV (Photovoltaic) | 2
64 | SIERRA | 186 | Ormat Nevada INC. |  | 640920 | 1 | 1 | [16 empty] | Missing PS |  |  | 0 | 37 | -12.1613 | 22.9305 | 24 | 1 | 38 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 32 | -5.8293 | BT | 30 |  | NO | 0.03 | 0.191 | 1.65 | 0.495 | 0.05 | 0.4 | 8 | 12.47 |  | BEOWAWE_RPWR_12.47_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 641041 | 1 | 1 | [10 empty] | Unreas Sat | [5 empty] | Missing PS |  |  | 0 | 25 | -10 | 27.1819 | 24 | 1.85 | 26.85 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 19.4348 | 11.2347 | BT | 43.53 | PF<0.8 | YES | 0.003 | 0.25 | 1.76 | 0.76613 | 0.08 | 0.16 | 2 | 12.47 |  | N_VALLEY_GEO_12.47_1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 641048 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 18.5 | -17.25 | 17.25 | 24 | 4.9 | 23.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 10.4 | -0.36637 | BT | 28.75 | PF<0.8 | NO | 0 | 100000 | 1.68 | 0.483 | 0.08 | 0.16 | 2 | 13.7998 |  | N_VALLEY2_13.8_G1 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 186 | Ormat Nevada INC. |  | 641048 | 2 | 2 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 18.5 | -17.25 | 17.25 | 24 | 4.9 | 23.4 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 12.4 | -0.36637 | BT | 28.75 | PF<0.8 | NO | 0 | 100000 | 1.68 | 0.483 | 0.08 | 0.16 | 2 | 13.7998 |  | N_VALLEY2_13.8_G2 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 2
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 641110 | 1 | 1 | [6 empty] | Limit Power Fact |  |  |  | Unreas Sat | [8 empty] | 0 | 24.8 | -22.93 | 22.93 | 24 | 4.1e-07 | 24.8 |  | GENTPJ |  | GGOV1 | ESAC8B_GE | Closed | 24.2 | 0.14893 | BT | 29.17 | PF<0.8 | NO | 0 | 100000 | 1.76 | 0.51339 | 0.08 | 0.16 | 2 | 12.47 |  | FRONTIRS_12.5_GEO9 | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 641253 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 410 | -368 | 368 | 24 | -410 |  |  | REGC_A |  |  | REEC_A | Closed | 360 | 40.9673 | P4 | 546 | PF<0.8 | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.6 |  | SIERRA1_0.66_LANTERN_345_PV | P4 (Photovoltaic, Tracking) | 1
64 | SIERRA | 59 | Sierra Pacific Power Co. |  | 641254 | 1 | 1 | [6 empty] | Limit Power Fact | [12 empty] | -405 | 405 | -368 | 368 | 24 | -405 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 546 | PF<0.8 | NO | 0 | 0.8 | 0 |  |  |  | NAN | 0.6 |  | SIERRA1_0.66_LANTERN_345_ES | BA (Energy Storage, Battery) | 1
64 | SIERRA | 57 | Harney Elec Co-Op |  | 668161 | 1 | 1 | [15 empty] | Missing Model | Missing PS |  |  | 0 | 45 | -23.6091 | 39.1942 | 24 | -45 | [6 empty] | Closed | 45 | 29.2722 | BT | 62.325 | PF<0.8 | YES | 0 | 1 | 0 |  |  |  | NAN | 13.8 |  | BPA_LITHIUM MINES | BT (Turbines Used in a Binary Cycle, including those used for geothermal applications) | 1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700100 | B1 | B1 | [6 empty] | Limit Power Fact | [12 empty] | -205.6336 | 205.6336 | -173.1134 | 173.1134 | 65 | -205.6336 | [6 empty] | Open | 0 | 0 | BA | 268.8 | PF<0.8 | NO | 0 | 1 | 0 |  |  |  | NAN | 0.66 |  | Not_in_WSM | BA (Energy Storage, Battery) | B1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700122 | B1 | B1 | [11 empty] | Gen at 0.0 | [7 empty] | -76.608 | 76.608 | -40.035 | 40.035 | 65 | -76.608 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 5.0456 | BA | 80.64 |  | NO | 9999 | 9999 | 0 |  |  |  | NAN | 0.69 |  | Not_in_WSM | BA (Energy Storage, Battery) | B1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700123 | B2 | B2 | [11 empty] | Gen at 0.0 | [7 empty] | -76.608 | 76.608 | -40.035 | 40.035 | 65 | -76.608 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 5.0456 | BA | 80.64 |  | NO | 9999 | 9999 | 0 |  |  |  | NAN | 0.69 |  | Not_in_WSM | BA (Energy Storage, Battery) | B2
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700124 | B3 | B3 | [11 empty] | Gen at 0.0 | [7 empty] | -76.608 | 76.608 | -40.035 | 40.035 | 65 | -76.608 |  |  | REGC_A |  |  | REEC_C | Closed | 0 | 5.6352 | BA | 80.64 |  | NO | 9999 | 9999 | 0 |  |  |  | NAN | 0.69 |  | Not_in_WSM | BA (Energy Storage, Battery) | B3
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700144 | B1 | B1 | [6 empty] | Limit Power Fact | [12 empty] | -118.25 | 118.25 | -74.95 | 74.95 | 65 | -118.25 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 140 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.9 |  | Not_in_WSM | BA (Energy Storage, Battery) | B1
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700146 | S2 | S2 | [6 empty] | Limit Power Fact | [12 empty] | 0 | 84.05 | -93.19 | 93.19 | 65 | -84.05 |  |  | REGC_A |  |  | REEC_A | Open | 0 | 0 | PV | 180 | PF<0.8 | NO | 0 | 999 | 0 |  |  |  | NAN | 0.63 |  | Not_in_WSM | PV (Photovoltaic) | S2
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700147 | B2 | B2 | [6 empty] | Limit Power Fact | [12 empty] | -118.25 | 118.25 | -74.95 | 74.95 | 65 | -118.25 |  |  | REGC_A |  |  | REEC_C | Open | 0 | 0 | BA | 140 | PF<-0.85 | NO | 0 | 1e-05 | 0 |  |  |  | NAN | 0.9 |  | Not_in_WSM | BA (Energy Storage, Battery) | B2
70 | PSCOLORADO | 700 | Non Utility Owned - PSCO Area |  | 700191 | B1 | B1 | [6 empty] | Limit Power Fact | [12 empty] | -14.25 | 14.25 | -9.865 | 9.865 | 65 | -14.25 | [6 empty] | Open | 0 | 0 | BA | 15 | PF<-0.85 | NO | 0 | 9999 | 0 |  |  |  | NAN | 0.6 |  | Not_in_WSM | BA (Energy Storage, Battery) | B1