## Sheet1
Project Name | Description | Evolving Grid Phase | Expected in-service date | Limit Changes for Interfaces Modeled in 2034 ADS PCM Case | Put In Case or Change File | Aux File | Notes | Aux File Provided
Rock Creek - John Day | Upgrade existing John Day - Rock Ck 500kV line | 1.0 | January, 2030 | none | Case | None |  | No
Big Eddy - Chemawa 230/500kV Line upgrade | Reconfigures the existing Big Eddy – Chemawa 230kV line into Big Eddy – Ostrander – Pearl 500kV line and Pearl-Chemawa 230kV line | 1.0 | 2032 | WOCS Path (The North of Marion #1 and #2 projects were included in the study for this path) 9,200 MW (Winter) 8,200 MW (Summer) | Case | EG1_BPA_BigEddy_Ostrander_Pearl_Chemawa_500 |  | Yes
Cross Cascades North Upgrades | 1. Upgrade Schultz-Raver #3 and #4 500kV lines to higher capacity. 2. Add new capacitor at Paul 500kV sub 3. Add new svcat Olympia 230kV sub | 1.0 | 2031 | WOCN Path 11,100 MW (Winter) | Case | EG1_BPA_Schultz – Raver #3 and 4 Upgrade *No aux files for capacitor and svc |  | Yes
Ross - Rivergate 230kV Line Upgrade | Upgrade existing Ross-Rivergate #1 230kV line to higher capacity. | 1.0 | 2029 | none | Case | EG1_BPA_Ross-Rvrg230_rebuild |  | Yes
Chehalis-Covington 230kV Line Upgrades | Replace conductor between Chehalis sub and Cowlitz Tap 230kV line | 1.0 | 2028 | Raver-Paul Path 1,655 MW (Summer/Spring) | Case | EG1_BPA_Chehalis-Covington-1_230kV_Reconductor |  | Yes
Portland Area Upgrades | 1. Keeler-Horizon 230kV Line #2: Completed and energized in 2024 2. Pearl-Sherwood-Mcloughlin 230kV Line Upgrade: Reconfigure and re-terminate the Pearl-Sherwood-Mclaughlin 230kV line 3. Keeler 230/500kV xfmr addition | 1.0 | 1. Completed 2. Summer 2026 3. 2029 | North Of Pearl Path (The North of Marion #1 and #2 projects were included in the study for this path) 2,100 MW | Case | 1. EG1_BPA Pearl_Sherwood_Upgrade 2. EG1_BPA_Keeler_Tx5 |  | Yes
Bonanza 230/500kV Substation | New 115/230/500kV substation near Ponderosa Substation | 1.0 | 2028 | none | Case | EG1_BPA_Bonanza_500 |  | Yes
La Pine-Bonanza 230kV Line | New 53 mile 230kV line between existing La Pine sub and new Bonanza Sub | 1.0 | Late 2029 | none | Case | EG1_BPA_Bonanza_500 |  | Yes
Six Mile Canyon 230/500kV Substation | New 230/500kV sub called Six Mile Canyon near Boardman, OR | 1.0 | Late 2027/early 2028 | WOCS definition update: Six Mile - Marion #2 | Case | EG1_BPA_Six_Mile500 |  | Yes
Grand Coulee-Columbia-Schultz 500kV Line Upgrade | Rebuild existing Grand Coulee-Olympia 286kV to 500kV. New Columbia 500kV sub yard with 500/230kV xfmr | 2.0 | 2035 | WOCN Path 13,000 MW (Winter) | Change File | EG2_BPA WOCN_Grand_Coulee_Schultz_Olympia |  | Yes
Schultz-Olympia 500kV Rebuild | Rebuildt the Schultz-Olympia portion of the Coulee-Olympia 287kV to 500kV. Expand the Olympia yard to include a 500/230kV xfmr and (3) 500kV shunt caps | 2.0 | End of 2035 | WOCN Path 13,000 MW (Winter) | Change File | EG2_BPA WOCN_Grand_Coulee_Schultz_Olympia |  | Yes
Salem Area Upgrades | A. North Marion Upgrade 1 1. New 500kV yard and Chemawa, including 500/230kV xfmr. 2. Rebuild Pearl-Chemawa from 230 to 500kV 3. Rebuild Chemawa-Santiam #1 from 230 to 500kV B. North of Marion Upgrade 2 1. Rebuild Pearl-Marion #1 500kV to upgrade line 2. REbuild Oregon City-Chemawa 115kV 3. Add a second 230/115kV xfmr at Chemawa | 2.0 | End of 2035 | North of Marion interface is not modeled in the 2034 ADS | Change File | A. EG2_BPA North_Marion_1_Pearl_Chemawa_Marion_500 B. EG2_BPA North_Marion_2 |  | Yes
North of Pearl | 1. Reconductor existing Pearl-Keeler #1 500kV and add a second 500kV line between the two subs. 2. Existing Pearl-Sherwood #1 and #2 230kV lines to be relocated and rebuilt to accommodate the Pearl-Keeler 500kV lines. 3. Existing Keeler-Oregon City #2 115kV to be repurposed as the new Keeler-Sherwood(PGE) 115kV line | 2.0 | End of 2035 | North Of Pearl Path (The North of Marion #1 and #2 projects were included in the TTC study for this path) 2,400 MW | Change File | EG2_BPA North_Of_Pearl_Pearl_Keeler #2 500 |  | Yes
Ostrander-Pearl #1 500kV Line Upgrade | Upgrade existing Ostrander-Pearl 500kV line | 2.0 | End of 2035 | WOCS Path (The North of Marion #1 and #2 projects were included in the TTC study for this path) 9200 MW (Winter) 8,200 MW (Summer) | Change File | EG2_Ostrander-Pearl-1-500-reconductor |  | Yes
Lower Columbia to NOB | 1. Lower Columbia to Bonanza: Proposed project to build a new 500kV line between a sub in lower Columbia area and the planned Bonanza sub in Central Oregon. 2. Bonanza to NOB: Proposed project to build a new 500kV line from Bonanza Sub toward NOB 3. NOB Sub: Proposed project would build a new 500kV sub at NOB | 2.0 | End of 2035 | Rating increases and changes to be determined | Change File | None |  | Will provide Bonanza-NOB All other files are still being worked on.