## Responses to Questions
Path Rating Draft with Flowgate Method Incorporated: Questions Received on First Draft and Associated Responses
Question | Response
What is "Established Flowgate Generator Deliverability" or "Established Flowgate Entities?" | "Established Flowgate Generator Deliverability," refers to a group of resources that have been studied and determined to not exceed flowgate limitations under stressed system conditions. The term "Established Flowgate Entities" has been removed and replaced with "Established Flowgate Generator Deliverability." "Established Flowgate Generator Deliverability" is now defined in Appendix A.
When must new/proposed Flowgate Generator Deliverability be considered? | Flowgate Generator Deliverability Studies are done as needed (i.e. when a new resource is proposed), and/or annually depending on the WECC member. After a Flowgate Generator Deliverability Study is completed, those resources will need to be considered in the WECC Path Rating Process. After the Phase 2B study plan has been completed, no additional Flowgate Generator Deliverability Studies will need to be considered.
How can one identify when Established Flowgate Generator Deliverability is impacted? Is there a way of determining which Flowgate Generator Deliverabilities are Similarly Situated and when path/flow gate deliverability may have simultaneous interactions? How can entities determine their impact on a Flowgate? | Those that use Flowgate Planning Method will participate in Project Review Groups (PRG) to identify Established Flowgate Generator Deliverabilities pertinent to a proposed path. They have agreed to perform the necessary Flowgate Generator Deliverability Studies to determine if a proposed path negatively impacts generator deliverability. The term Flowgate Generator Deliverability Study has been added in Appendix A. Flowgate Planners may also provide information to help mitigate said impact.
Will Flowgate Generator Deliverability be subject to a process like Path Ratings? | Flowgate Generator Deliverability Studies do not impact path ratings. The studies only confirm that capacity for a specific generator, or fleet of generators, can be reliably transferred through one or more identified flowgates to serve load or count toward capacity obligations without creating thermal, voltage, or stability violations. As per NAESB WEQ Modeling Business Practice Standard (WEQ-023) Sections 1.1.1.3, 1.1.1.3.1, and 1.1.1.3.3, if a project sponsor requests the inclusion of a path as a constraint in Flowgate Generator Deliverability Studies, and an impact test performed by the requestee shows generator to load transfers affect a path's transfer capability by 5% or greater, than the requested path will be accounted for as a constraint in Flowgate Generator Deliverability Studies. If the impact to the path is less than 5%, the requested path may still be included if agreed upon by the project sponsor and entity performing the Flowgate Generator Deliverability Studies.
Is there a technical reference for Generator Deliverability analysis? If not, should we add a section that discusses key methods, assumptions, concerns, and that has examples of Flowgate Generator Deliverability analysis? | We have included an overview of Flowgate Generator Deliverability Studies in Section 5 of the Draft Path Rating Process. However, additional technical references that may be found useful have been provided below. Entities in the West leverage much of their Flowgate Planning Methods from CAISO's Methodology: CAISO's Methodology: https://stakeholdercenter.caiso.com/InitiativeDocuments/Final-Proposal-Generation-Deliverability-Methodology-Review-Jan-04-2024.pdf PJM's Methodology: https://www.pjm.com/-/media/DotCom/documents/manuals/m14b.ashx SRP's Methodology: https://www.oasis.oati.com/woa/docs/SRP/SRPdocs/SRP_Generator_Deliverability_Study_Business_Practice.pdf AZPS FAQ: https://www.oasis.oati.com/woa/docs/AZPS/AZPSdocs/Generator_Deliverability_FAQ_v1.pdf
Does each Planning Coordinator have their own Generation Deliverability methodology, and if so, how can “established” Flowgates be comparable if different methodologies are used? | Those that use flowgates for transmission planning purposes follow the WEQ-023 NAESB Business Practice which can be found here: WEQ-023 NAESB Business Practice: https://www.naesb.org/weq/weq_standards.asp (Please note the above link requires membership to NAESB) These business practices are not too different than the retired NERC MOD 30 standard, which may be found here (I can't seem to find retired standards on NERC's actual website): Retired NERC MOD 30: https://nercipedia.com/active-standards/mod-030-3-flowgate-methodology/ In addition, entities post their ATCID on OASIS which can be reviewed. For items not defined by the WEQ-023 NAESB Business Practices, WECC members may use their technical expertise to tailor their respective Flowgate Planning Method to their area and processes. Neither Path Planners nor Flowgate Planners all use synonymous planning methods.
In addition to Remedial Action Schemes, should transmission upgrades be considered in generator deliverability studies to achieve post outage performance requirements? | The purpose of Flowgate Generator Deliverability Studies is to confirm generators are deliverable without transmission constraints for severe dispatch scenarios while meeting existing transmission commitments. Incorporating RAS would be counterintuitive to the goal of the studies. As such, the language regarding RAS has been removed from the document.
What does "Considered relevant Rated Path constraints" mean? | "Considered relevant Rated Path constraints" refers to WECC Path Ratings. Flowgate planners must account for accepted WECC path ratings in Flowgate Generator Deliverability Studies if a project sponsor requests the inclusion of a path as a constraint in Flowgate Generator Deliverability Studies, and an impact test performed shows generator to load transfers affect a path's transfer capability by 5% or greater. If the impact to the path is less than 5%, the requested path may still be included if agreed upon by the project sponsor and entity performing the Flowgate Generator Deliverability Studies.
Could there be differences between FGD realism and what folks have considered to be “realistic” in Path Rating assumptions, and is this a concern? | The purpose of Flowgate Generator Deliverability Studies is to confirm generators are deliverable without transmission constraints for severe dispatch scenarios while meeting existing transmission commitments. As such, numerous operating conditions are tested in a single Flowgate Generator Deliverability Study to determine if there is a scenario under which a resource cannot maintain generator deliverability. If this scenario is encountered due to a proposed path, then the project sponsor and flowgate planners should work together to determine how to mitigate the issue.
Do we need a discussion on counterflow? If so, what purpose does it serve? | A discussion on counterflow is required. Thermal or joint ownership counterflow adjusts the AFC. Therefore it must be considered in Flowgate Generator Deliverability Studies. AFC has also now been added to Appendix A.
Is there a criteria for how many Flowgate Generator Deliverability studies/cases must be completed to prove a path does not adversely impact generator deliverability? | One Flowgate Generator Deliverability Study per topology year will be sufficient. If the proposed path was studied in year 2029, and only year 2029, then the Flowgate Generator Deliverability Study would examine the same year. If multiple years are studied for a proposed path, matching years and topology would be used for the Flowgate Generator Deliverability Studies.
Are we expecting to need to rerate paths based on the changes associated with flowgates? | Paths will not be rerated based on Flowgate Generator Deliverability Studies.
Is it expected that Flowgate planners be a part of the PRG? If a Flowgate Method utility decided to not join the PRG, is it assumed their Generator Deliverability is not impacted by the project? | Those that use a flowgate based methodology for planning purposes will participate in Project Review Groups (PRG) to identify Established Flowgate Generator Deliverabilities pertinent to a proposed path. Through PRG participation, Flowgate Planners will be required to support performing the necessary Flowgate Generator Deliverability Studies. Flowgate planners may also provide information to help mitigate said impact.
Note on A2: Zapotocky, Matt: Reference the "wFeedback" version to see in text responses

## Responses to Comments
Path Rating Draft with Flowgate Method Incorporated: Comments Received on First Draft and Associated Responses/Actions
Section | Page | Comments | Response and/or Actions
2.1 | 21 | Suggestion to use the word "Established" instead of "existing" for item 4 of Section 2.1 on "Objectives" | Agree, replaced the word “Existing” with “Established.” Protection is only for “Established Flowgate Generator Deliverability,” which is now defined in Appendix A.
2.1 | 21 | Suggestion to discuss and define the term "Established Flowgate Generator Deliverability" | Agree, “Established Flowgate Generator Deliverability”, “Flowgate Generator Deliverability Study”, and “Flowgate” are now all defined in Appendix A. SRP provided a presentation on the Flowgate Planning Method in October’s 2025 RAC meeting to provide additional background.
2.3 | 22 | Suggestion to remove SOL requirement in the following: "2. The limiting condition (e.g., thermal limit, stability, or voltage) in determining the Total Transfer Capability of the path or the System Operating Limit for transmission facilities that have the potential to adversely impact an established Flowgate Generator Deliverability and the affected entity of the Flowgate Generator Deliverability requests the path be rated ." Not practical to assess every System Operating Limit's potential impact to WECC Accepted Ratings for WECC Paths. SOLs are used, as well as RTCA (Realtime Contingency Analysis) to establish limits in operation. | Agree, the term "System Operating Limit" has been removed from these statements.
2.3 | 22 | Addition of the the words "and the affected entity of the Flowgate Generator Deliverability requests the path be rated " in item #2. | Agree. Those that use a flowgate based methodology for planning purposes will participate in Project Review Groups (PRG) to identify Established Flowgate Generator Deliverabilities pertinent to a proposed path.
5.1 | 48 | Disagreement on primary purpose of the Flowgate Method | Removed the words "primary focus of the" from Section 5.1.
5.1 | 48 | It is not possible/practical for Path Project Sponsors to consider every/any kind of generation deliverability results. What we are talking about in this document here, are a specific subset of FGDs, which are used by specific utilities in lieu of Paths for ATC and scheduling purposes. | Agree, no change to document. It is not practical to look at all Established Flowgate Generator Deliverabilities for all entities for a Path Rating change. Only Established Flowgate Generator Deliverabilities pertinent to the given Path.
5.2 | 48 | Request to clarify the following statement: "Generator Deliverability is determined such that, at the pre-outage facility ratings are below continuous ratings for screened flowgate and all screened ratings are below within post-outage performance requirements specified in the NERC Standards and WECC Criteria." | Agree that the original meaning of the statement was unclear. Wording of Section 5.2 has been updated in an attempt to clarify the meaning.
5.2 | 48 | Technically, the TO does not own generation. Request to alter the following statement "To determine Generator Deliverability, the Transmission Operator would examine their entire fleet of generation and existing committed transmission uses against facility ratings and joint ownership utilization during stressed system conditions." | Agree, changed the term to "Transmission Planner."
5.3.4 | 49 | Request to state that "the facilities and/or mitigation to resolve the constraint(s) must be implemented before the fleet of generation can be deemed fully Deliverable." | Agree on this. Wording in Section 5.3.4 has been updated to accommodate this language
5.3.5 | 49 | Conflicting opinions on whether to keep the following statement "Flowgate entities must include all relevant Rated Paths, as requested through the flowgate coordination process, in their Flowgate Generation Deliverability process to ensure no adverse impact." | Language has been updated to state "relevant Paths with Existing or Accepted Ratings" to be consistent with similar Phase 2 language.
5.3.7 | 50 | Request to define "ATCID" | Added "ATCID" to Appendix A.
5.3.8 | 50 | Objection to the use of joint ownership being applied as a flowgate rating. | Added the word "may" to the statement describing types of counterflow TSRs may include.
6.2.3 | 51 | Request to define the term "new Projects" in the following statement: "4. New Projects will ensure no adverse impact on established Flowgate Generator Deliverability" | Agree this is unclear, changed "New Projects" to "New path or increase to existing path"
6.4.2 | 54 | Request to clarify the following statement " iii. Identify all affected paths and Flowgates that pick up a 10% increment or more, based on that affected Path's rating, due to the outage. If the mon or con is a Flowgate entity , a, Flowgate generator Generator Deliverability analysis will may be required." | No change to the document, provided response: If a flowgate segment picks up 10% of the flow for an outage than a Flowgate Generator Deliverability Study is required, the goal was to ensure that the same established screening criteria for when other paths must be considered also existed for when a Flowgate Generator Deliverability Study is required.
Appendix A | 98 | Request to make the "Flowgate Generator Deliverability" definition more general and to match the NERC definition | "Established Flowgate Generator Deliverability," "Flowgate Generator Deliverability Study," and "Available Flowgate Capability (AFC)" have been added to Appendix A
Note on A2: Zapotocky, Matt: Reference the "wFeedback" version to see in text responses
Note on B2: Zapotocky, Matt: Reference the "wFeedback" version to see in text responses