## LMDT
Load Model Data for Hour 1800
BUTTON: PSS®E |  | PTI PSS®E File Name | load21_wecc1a.dyr
*Requires PSS®E Version 34.05
BUTTON: PSLF |  | GE PSLF File Name | Shoulder_hour17(24HSP1).dyd
*Requires GE PSLF Version 21.07
Min MW | 5 | *Minimum MW value for creating a load model record
PQmin | 1.4327 | *Minimum absolute value of P/Q ratio to create a load model record
Vmin | 0.93 | *Lowest bus voltage to create a load model record
kVThresh | 40 | *kV threshold for model to add a transformer
Versions:
0

## PowerFlow
#Type | Bus_Number | Bus_Name | LoadComp | Feeder | DER_Model | MVA_base | Base_kV | Load_ID | Area | Zone | Owner | Bus Voltage | Pload | Qload | Pder | Qder | Report
LoadType | -11 | NWC_RES | NWC_RES | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -12 | NWC_COM | NWC_COM | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -13 | NWC_MIX | NWC_MIX | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -14 | NWC_RAG | NWC_RAG | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -15 | NWV_RES | NWV_RES | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9
LoadType | -16 | NWV_COM | NWV_COM | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9
LoadType | -17 | NWV_MIX | NWV_MIX | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9
LoadType | -18 | NWV_RAG | NWV_RAG | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9
LoadType | -19 | NWI_RES | NWI_RES | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -20 | NWI_COM | NWI_COM | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -21 | NWI_MIX | NWI_MIX | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -22 | NWI_RAG | NWI_RAG | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -23 | RMN_RES | RMN_RES | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -24 | RMN_COM | RMN_COM | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -25 | RMN_MIX | RMN_MIX | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -26 | RMN_RAG | RMN_RAG | FDR_01 | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -27 | NCC_RES | NCC_RES | FDR_01_noLTC | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -28 | NCC_COM | NCC_COM | FDR_01_noLTC | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -29 | NCC_MIX | NCC_MIX | FDR_01_noLTC | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -30 | NCC_RAG | NCC_RAG | FDR_01_noLTC | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -31 | NCV_RES | NCV_RES | FDR_01_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -32 | NCV_COM | NCV_COM | FDR_01_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -33 | NCV_MIX | NCV_MIX | FDR_01_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -34 | NCV_RAG | NCV_RAG | FDR_01_noLTC | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -35 | NCI_RES | NCI_RES | FDR_01_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -36 | NCI_COM | NCI_COM | FDR_01_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -37 | NCI_MIX | NCI_MIX | FDR_01_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -38 | NCI_RAG | NCI_RAG | FDR_01_noLTC | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -39 | SCC_RES | SCC_RES | FDR_02_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -40 | SCC_COM | SCC_COM | FDR_02_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -41 | SCC_MIX | SCC_MIX | FDR_02_noLTC | -110 | -1.1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -42 | SCC_RAG | SCC_RAG | FDR_02_noLTC | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -43 | SCV_RES | SCV_RES | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -44 | SCV_COM | SCV_COM | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -45 | SCV_MIX | SCV_MIX | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -46 | SCV_RAG | SCV_RAG | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -47 | SCI_RES | SCI_RES | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -48 | SCI_COM | SCI_COM | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -49 | SCI_MIX | SCI_MIX | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -50 | SCI_RAG | SCI_RAG | FDR_02_noLTC | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -51 | DSW_RES | DSW_RES | FDR_01_noLTC | -110 | -1.25 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -52 | DSW_COM | DSW_COM | FDR_01_noLTC | -110 | -1.25 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -53 | DSW_MIX | DSW_MIX | FDR_01_noLTC | -110 | -1.25 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -54 | DSW_RAG | DSW_RAG | FDR_01_noLTC | -110 | -1.25 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -55 | HID_RES | HID_RES | FDR_01-HID | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -56 | HID_COM | HID_COM | FDR_01 | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -57 | HID_MIX | HID_MIX | FDR_01 | -110 | -1.2 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -58 | HID_RAG | HID_RAG | FDR_01-HID | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -101 | IND_PCH | IND_PCH | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -102 | IND_OIL | IND_OIL | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -103 | IND_SHG | IND_SHG | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -104 | IND_LNG | IND_LNG | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -105 | IND_PMK | IND_PMK | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -106 | IND_PMT | IND_PMT | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -107 | IND_LMB | IND_LMB | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -108 | IND_MIN | IND_MIN | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -109 | IND_ASM | IND_ASM | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -110 | IND_SML | IND_SML | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -111 | IND_CAR | IND_CAR | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -112 | IND_CEM | IND_CEM | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -113 | IND_SCD | IND_SCD | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -114 | IND_SRF | IND_SRF | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -115 | IND_OTH | IND_OTH | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -116 | IND_RAIL | IND_RAIL | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -117 | PPA_AUX | PPA_AUX | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -118 | AGR_IRR | AGR_IRR | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -119 | AGR_PMP | AGR_PMP | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
LoadType | -120 | AGR_PRO | AGR_PRO | FDR_IND | -110 | -1 | 100 | W | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1

## LoadComp
#AREA | ID_MotorA | ID_MotorB | ID_MotorC | ID_MotorD | ID_PwrElec | Lc_MotorA | Lc_MotorB | Lc_MotorC | Lc_MotorD | LC_PwrElec | Lc_StatPF | Lc_Zp | Lc_Ip | Lc_Zq | Lc_Iq | Lc_Pf | Lc_Qf
NWC_RES | MA | MB | MC | AC | PE | 0.040451 | 0.06964 | 0.038539 | 0.055949 | 0.16724 | -0.99961 | 0.51835 | 0.10983 | -0.5 | 1.5 | 0 | -1
NWC_COM | MA | MB | MC | AC | PE | 0.10609 | 0.12421 | 0.028943 | 0.022727 | 0.20694 | -0.99648 | 0.26158 | 0.24951 | -0.5 | 1.5 | 0 | -1
NWC_MIX | MA | MB | MC | AC | PE | 0.091281 | 0.12118 | 0.054192 | 0.031073 | 0.1766 | -0.99838 | 0.33123 | 0.19444 | -0.5 | 1.5 | 0 | -1
NWC_RAG | MA | MB | MC | AC | PE | 0.10325 | 0.09812 | 0.13497 | 0.032052 | 0.15219 | -0.99955 | 0.36141 | 0.11802 | -0.5 | 1.5 | 0 | -1
NWV_RES | MA | MB | MC | AC | PE | 0.043481 | 0.068426 | 0.038444 | 0.059608 | 0.17931 | -0.9996 | 0.50172 | 0.10901 | -0.5 | 1.5 | 0 | -1
NWV_COM | MA | MB | MC | AC | PE | 0.11325 | 0.12125 | 0.025723 | 0.024145 | 0.22084 | -0.99633 | 0.24801 | 0.24678 | -0.5 | 1.5 | 0 | -1
NWV_MIX | MA | MB | MC | AC | PE | 0.096352 | 0.11914 | 0.052326 | 0.033048 | 0.18842 | -0.99831 | 0.318 | 0.19271 | -0.5 | 1.5 | 0 | -1
NWV_RAG | MA | MB | MC | AC | PE | 0.10576 | 0.097145 | 0.13457 | 0.034119 | 0.16021 | -0.99953 | 0.35091 | 0.11728 | -0.5 | 1.5 | 0 | -1
NWI_RES | MA | MB | MC | AC | PE | 0.051143 | 0.076511 | 0.034304 | 0.11532 | 0.15875 | -0.9995 | 0.45228 | 0.11169 | -0.5 | 1.5 | 0 | -1
NWI_COM | MA | MB | MC | AC | PE | 0.13474 | 0.10875 | 0.023972 | 0.047663 | 0.20813 | -0.99561 | 0.21818 | 0.25856 | -0.5 | 1.5 | 0 | -1
NWI_MIX | MA | MB | MC | AC | PE | 0.11072 | 0.11472 | 0.050229 | 0.064686 | 0.1742 | -0.99796 | 0.28585 | 0.1996 | -0.5 | 1.5 | 0 | -1
NWI_RAG | MA | MB | MC | AC | PE | 0.11229 | 0.099764 | 0.13228 | 0.066239 | 0.14778 | -0.99944 | 0.32181 | 0.11983 | -0.5 | 1.5 | 0 | -1
RMN_RES | MA | MB | MC | AC | PE | 0.04021 | 0.0575 | 0.038965 | 0.063601 | 0.22525 | -0.99975 | 0.49146 | 0.083016 | -0.5 | 1.5 | 0 | -1
RMN_COM | MA | MB | MC | AC | PE | 0.11493 | 0.1071 | 0.025752 | 0.028382 | 0.23225 | -0.99755 | 0.28842 | 0.20316 | -0.5 | 1.5 | 0 | -1
RMN_MIX | MA | MB | MC | AC | PE | 0.094279 | 0.10551 | 0.051582 | 0.037675 | 0.21065 | -0.99891 | 0.34276 | 0.15754 | -0.5 | 1.5 | 0 | -1
RMN_RAG | MA | MB | MC | AC | PE | 0.10024 | 0.087689 | 0.12844 | 0.0384 | 0.18824 | -0.9997 | 0.35924 | 0.097745 | -0.5 | 1.5 | 0 | -1
NCC_RES | MA | MB | MC | AC | PE | 0.064534 | 0.065979 | 0.047657 | 0.072814 | 0.19628 | -0.99962 | 0.45398 | 0.09876 | -0.5 | 1.5 | 0 | -1
NCC_COM | MA | MB | MC | AC | PE | 0.16552 | 0.11645 | 0.037789 | 0.029575 | 0.20861 | -0.99644 | 0.22015 | 0.2219 | -0.5 | 1.5 | 0 | -1
NCC_MIX | MA | MB | MC | AC | PE | 0.13278 | 0.11583 | 0.062434 | 0.040374 | 0.18678 | -0.99841 | 0.28659 | 0.17521 | -0.5 | 1.5 | 0 | -1
NCC_RAG | MA | MB | MC | AC | PE | 0.12356 | 0.095433 | 0.14173 | 0.041498 | 0.16728 | -0.99958 | 0.32182 | 0.10869 | -0.5 | 1.5 | 0 | -1
NCV_RES | MA | MB | MC | AC | PE | 0.08097 | 0.056865 | 0.04725 | 0.073777 | 0.1952 | -0.99966 | 0.45222 | 0.093715 | -0.5 | 1.5 | 0 | -1
NCV_COM | MA | MB | MC | AC | PE | 0.21017 | 0.095228 | 0.036439 | 0.030558 | 0.2063 | -0.99646 | 0.20798 | 0.21332 | -0.5 | 1.5 | 0 | -1
NCV_MIX | MA | MB | MC | AC | PE | 0.16282 | 0.10119 | 0.062067 | 0.041299 | 0.18469 | -0.99851 | 0.27972 | 0.16822 | -0.5 | 1.5 | 0 | -1
NCV_RAG | MA | MB | MC | AC | PE | 0.1377 | 0.088267 | 0.14241 | 0.041949 | 0.16607 | -0.99962 | 0.31895 | 0.10465 | -0.5 | 1.5 | 0 | -1
NCI_RES | MA | MB | MC | AC | PE | 0.070061 | 0.064132 | 0.04683 | 0.072952 | 0.19989 | -0.99966 | 0.45391 | 0.092224 | -0.5 | 1.5 | 0 | -1
NCI_COM | MA | MB | MC | AC | PE | 0.17965 | 0.11212 | 0.035701 | 0.029714 | 0.2176 | -0.9966 | 0.21888 | 0.20633 | -0.5 | 1.5 | 0 | -1
NCI_MIX | MA | MB | MC | AC | PE | 0.1425 | 0.11282 | 0.061061 | 0.040505 | 0.19296 | -0.99853 | 0.28592 | 0.16422 | -0.5 | 1.5 | 0 | -1
NCI_RAG | MA | MB | MC | AC | PE | 0.1282 | 0.093959 | 0.14119 | 0.041563 | 0.1702 | -0.99962 | 0.32156 | 0.10333 | -0.5 | 1.5 | 0 | -1
SCC_RES | MA | MB | MC | AC | PE | 0.041944 | 0.054757 | 0.041356 | 0.064673 | 0.21926 | -0.99971 | 0.48146 | 0.09655 | -0.5 | 1.5 | 0 | -1
SCC_COM | MA | MB | MC | AC | PE | 0.12327 | 0.10179 | 0.031796 | 0.029716 | 0.21589 | -0.99693 | 0.251 | 0.24654 | -0.5 | 1.5 | 0 | -1
SCC_MIX | MA | MB | MC | AC | PE | 0.099199 | 0.10191 | 0.056424 | 0.038857 | 0.19906 | -0.99867 | 0.3195 | 0.18505 | -0.5 | 1.5 | 0 | -1
SCC_RAG | MA | MB | MC | AC | PE | 0.10263 | 0.085745 | 0.13183 | 0.038964 | 0.18249 | -0.99965 | 0.3486 | 0.10974 | -0.5 | 1.5 | 0 | -1
SCV_RES | MA | MB | MC | AC | PE | 0.050276 | 0.059739 | 0.040807 | 0.094828 | 0.2099 | -0.99976 | 0.4609 | 0.083557 | -0.5 | 1.5 | 0 | -1
SCV_COM | MA | MB | MC | AC | PE | 0.15103 | 0.098407 | 0.034702 | 0.044998 | 0.20768 | -0.99723 | 0.24504 | 0.21813 | -0.5 | 1.5 | 0 | -1
SCV_MIX | MA | MB | MC | AC | PE | 0.11634 | 0.10122 | 0.057453 | 0.058221 | 0.19166 | -0.99885 | 0.31093 | 0.16418 | -0.5 | 1.5 | 0 | -1
SCV_RAG | MA | MB | MC | AC | PE | 0.1091 | 0.087471 | 0.12973 | 0.058122 | 0.17718 | -0.99971 | 0.3393 | 0.099093 | -0.5 | 1.5 | 0 | -1
SCI_RES | MA | MB | MC | AC | PE | 0.046224 | 0.054711 | 0.041686 | 0.068696 | 0.21754 | -0.99973 | 0.47902 | 0.092123 | -0.5 | 1.5 | 0 | -1
SCI_COM | MA | MB | MC | AC | PE | 0.13607 | 0.099583 | 0.033257 | 0.031773 | 0.21345 | -0.99705 | 0.25004 | 0.23583 | -0.5 | 1.5 | 0 | -1
SCI_MIX | MA | MB | MC | AC | PE | 0.1075 | 0.10065 | 0.057345 | 0.041438 | 0.19713 | -0.99875 | 0.31844 | 0.1775 | -0.5 | 1.5 | 0 | -1
SCI_RAG | MA | MB | MC | AC | PE | 0.10632 | 0.085397 | 0.13202 | 0.041473 | 0.18133 | -0.99967 | 0.34746 | 0.106 | -0.5 | 1.5 | 0 | -1
DSW_RES | MA | MB | MC | AC | PE | 0.060465 | 0.13556 | 0.030261 | 0.34592 | 0.12764 | -0.99907 | 0.20337 | 0.096775 | -0.5 | 1.5 | 0 | -1
DSW_COM | MA | MB | MC | AC | PE | 0.16858 | 0.13363 | 0.032967 | 0.15257 | 0.16306 | -0.99511 | 0.11443 | 0.23476 | -0.5 | 1.5 | 0 | -1
DSW_MIX | MA | MB | MC | AC | PE | 0.13149 | 0.14861 | 0.054808 | 0.20084 | 0.13768 | -0.99747 | 0.14676 | 0.17983 | -0.5 | 1.5 | 0 | -1
DSW_RAG | MA | MB | MC | AC | PE | 0.12109 | 0.13372 | 0.13238 | 0.19978 | 0.12567 | -0.99929 | 0.17917 | 0.1082 | -0.5 | 1.5 | 0 | -1
HID_RES | MA | MB | MC | AC | PE | 0.037324 | 0.056775 | 0.04209 | 0.068276 | 0.2168 | -0.99966 | 0.47693 | 0.10181 | -0.5 | 1.5 | 0 | -1
HID_COM | MA | MB | MC | AC | PE | 0.10984 | 0.10455 | 0.034521 | 0.031233 | 0.21144 | -0.99665 | 0.24815 | 0.26026 | -0.5 | 1.5 | 0 | -1
HID_MIX | MA | MB | MC | AC | PE | 0.090277 | 0.10396 | 0.057916 | 0.040966 | 0.19598 | -0.99851 | 0.3164 | 0.19451 | -0.5 | 1.5 | 0 | -1
HID_RAG | MA | MB | MC | AC | PE | 0.098231 | 0.087034 | 0.13189 | 0.041251 | 0.18087 | -0.99959 | 0.34634 | 0.11438 | -0.5 | 1.5 | 0 | -1
IND_PCH | IA | IB | IC | AC | PI | 0.15 | 0.25 | 0.4 | 0 | 0.15 | 1 | 0.02 | 0.05 | 1 | 0 | 0 | -1
IND_OIL | IA | IB | IC | AC | PI | 0.3 | 0 | 0.4 | 0 | 0.3 | 1 | 0 | 0 | 1 | 0 | 0 | -1
IND_SHG | IA | IB | IC | AC | PI | 0 | 0.2 | 0.4 | 0 | 0.4 | 1 | 0 | 0 | 1 | 0 | 0 | -1
IND_LNG | IA | IB | IC | AC | PI | 0 | 0.3 | 0.2 | 0 | 0.5 | 1 | 0 | 0 | 1 | 0 | 0 | -1
IND_PMK | IA | IB | IC | AC | PI | 0.1 | 0.25 | 0.4 | 0 | 0.2 | 1 | 0 | 0.05 | 1 | 0 | 0 | -1
IND_PMT | IA | IB | IC | AC | PI | 0.05 | 0.55 | 0.25 | 0 | 0.12 | 1 | 0 | 0.03 | 1 | 0 | 0 | -1
IND_LMB | IA | IB | IC | AC | PI | 0.4 | 0.2 | 0.3 | 0 | 0 | 1 | 0.05 | 0.05 | 1 | 0 | 0 | -1
IND_MIN | IA | IB | IC | AC | PI | 0.2 | 0.35 | 0.35 | 0 | 0.05 | 1 | 0 | 0.05 | 1 | 0 | 0 | -1
IND_ASM | IA | IB | IC | AC | PI | 0 | 0 | 0.1 | 0 | 0.05 | 1 | 0.9 | 0 | 1 | 0 | 0 | -1
IND_SML | IA | IB | IC | AC | PI | 0.2 | 0.25 | 0.3 | 0 | 0.2 | 1 | 0 | 0.05 | 1 | 0 | 0 | -1
IND_CAR | IA | IB | IC | AC | PI | 0.15 | 0 | 0.3 | 0 | 0.3 | 1 | 0.1 | 0.15 | 1 | 0 | 0 | -1
IND_CEM | IA | IB | IC | AC | PI | 0.1 | 0.1 | 0.1 | 0 | 0.6 | 1 | 0.1 | 0 | 1 | 0 | 0 | -1
IND_SCD | IA | IB | IC | AC | PI | 0.1 | 0.35 | 0.1 | 0 | 0.4 | 1 | 0 | 0.05 | 1 | 0 | 0 | -1
IND_SRF | IA | IB | IC | AC | PI | 0.25 | 0.1 | 0.05 | 0 | 0.65 | 1 | 0 | 0.05 | 1 | 0 | 0 | -1
IND_OTH | IA | IB | IC | AC | PI | 0.2 | 0.25 | 0.3 | 0 | 0.2 | 1 | 0 | 0.05 | 1 | 0 | 0 | -1
IND_RAIL | IA | IB | IC | AC | PI | 0 | 0 | 0.05 | 0 | 0.95 | 1 | 0 | 0 | 1 | 0 | 0 | -1
AGR_IRR | IA | IB | IC | AC | PI | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | -1
AGR_PMP | IA | IB | IC | AC | PI | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | -1
PPA_AUX | IA | IB | IC | AC | PI | 0.05 | 0.5 | 0.25 | 0 | 0.15 | 1 | 0 | 0.05 | 1 | 0 | 0 | -1
AGR_PRO | IA | IB | IC | AC | PI | 0.6 | 0 | 0.25 | 0 | 0.05 | 1 | 0.05 | 0.05 | 1 | 0 | 0 | -1

## Feeder
#FEEDER | Bss | Rfdr | Xfdr | Fb | Xxf | TfixHS | TfixLS | LTC | Tmin | Tmax | step | Vmin | Vmax | Tdel | Ttap | Rcomp | Xcomp
FDR_01 | 0 | 0.04 | 0.04 | 0.75 | 0.08 | 1 | 1 | 1 | 0.9 | 1.1 | 0.00625 | 1.025 | 1.04 | 30 | 5 | 0 | 0
FDR_01-HID | 0 | 0.04 | 0.04 | 0.75 | 0.06 | 1 | 1 | 1 | 0.9 | 1.1 | 0.00625 | 1.025 | 1.04 | 30 | 5 | 0 | 0
FDR_01_noLTC | 0 | 0.04 | 0.04 | 0.75 | 0.08 | 1 | 1 | 1 | 0.9 | 1.1 | 0.00625 | 1.025 | 1.04 | 999 | 5 | 0 | 0
FDR_02_CVR | 0 | 0.04 | 0.04 | 0.75 | 0.08 | 1 | 1 | 1 | 0.9 | 1.1 | 0.00625 | 1 | 1.02 | 30 | 5 | 0 | 0
FDR_02_noLTC | 0 | 0.04 | 0.04 | 0.75 | 0.08 | 1 | 1 | 1 | 0.9 | 1.1 | 0.00625 | 1 | 1.02 | 999 | 5 | 0 | 0
FDR_IND | 0 | 0 | 0.01 | 1 | 0.08 | 1 | 1 | 1 | 0.9 | 1.1 | 0.00625 | 1 | 1.02 | 999 | 5 | 0 | 0

## Motors
| MA | MB | MC | IA | IB | IC |  | AC
TYPE | M3 | M3 | M3 | M3 | M3 | M3 | TYPE | AC
LF | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | LFm | 1
Ra | 0.04 | 0.03 | 0.03 | 0.01 | 0.01 | 0.01 | CompPF | 0.98
Ls | 1.8 | 1.8 | 1.8 | 3.1 | 3.1 | 3.1 | Vstall | 0.45
Lps | 0.12 | 0.19 | 0.19 | 0.2 | 0.2 | 0.2 | Rstall | 0.1
Lpps | 0.104 | 0.14 | 0.14 | 0.165 | 0.165 | 0.165 | Xstall | 0.1
Tpo | 0.095 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | Tstall | 0.032
Tppo | 0.0021 | 0.0026 | 0.0026 | 0.0026 | 0.0026 | 0.0026 | Frst | 0.2 | AC re-start fraction | 0 to 0.5
H | 0.1 | 0.5 | 0.1 | 0.15 | 1 | 0.2 | Vrst | 0.95 | Restart voltage | 0.8 to 0.9
Etrq | 0 | 2 | 2 | 0 | 2 | 2 | Trst | 0.3
Vtr1 | 0.7 | 0.6 | 0.65 | 0.7 | 0.7 | 0.7 | Fuvr | 0.1 | AC trip fraction | 0 to 0.5
Ttr1 | 0.1 | 0.02 | 0.02 | 0.05 | 0.05 | 0.05 | vtr1 | 0.6 | Trip Voltage 1 | 0.45 to 0.55
Ftr1 | 0.2 | 0.2 | 0.2 | 1 | 0.3 | 0.3 | ttr1 | 0.02 | Trip Timer 1 | 0.03 to 0.1
Vrc1 | 1 | 0.75 | 1 | 1 | 1 | 1 | vtr2 | 0 | Trip Voltage 2 | 0.5 to 0.6
Trc1 | 99999 | 0.05 | 9999 | 9999 | 9999 | 9999 | ttr2 | 9999 | Trip Timer 2 | .05 to 0.15 | 999 = disabled
Vtr2 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | Vc1off | 0.5
Ttr2 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | Vc2off | 0.4
Ftr2 | 0.7 | 0.3 | 0.3 | 0 | 0.5 | 0.5 | VC1on | 0.6
Vrc2 | 0.7 | 0.65 | 0.65 | 1 | 0.75 | 0.75 | VC2on | 0.5
Trc2 | 0.1 | 0.05 | 0.1 | 99999 | 0.25 | 0.25 | Tth | 15
[7 empty] | Th1t | 0.7
[7 empty] | Th2t | 1.9
[7 empty] | Tv | 0.025
[7 empty] | Tf | 0.05
[7 empty] | LFadj | 0
[7 empty] | Kp1 | 0
[7 empty] | Np1 | 1
[7 empty] | Kq1 | 6
[7 empty] | Nq1 | 2
[7 empty] | Kp2 | 12
[7 empty] | Np2 | 3.2
[7 empty] | Kq2 | 11
[7 empty] | Nq2 | 2.5
[7 empty] | Vbrk | 0.86
[7 empty] | CmpKpf | 1
[7 empty] | CmpKqf | -3.3

## PwrEl
| PE | PI | PD
PFel | 1 | 1 | 1
Vd1 | 0.7 | 0.72 | 0.72
Vd2 | 0.5 | 0.52 | 0.52
Frcel | 1 | 1 | 0.5

## DER
#DER | -110 | -100
trv | 0.02 | 0
dbd1 | -99 | -0.1
dbd2 | 99 | 0.1
kqv | 0 | 1
vref0 | 0 | 0
tp | 0.02 | 0.025
pfflag | 1 | 1
tiq | 0.02 | 0.02
ddn | 20 | 0
dup | 20 | 0
fdbd1 | -0.0006 | 0
fdbd2 | 0.0006 | 0
femax | 99 | 999
femin | -99 | -999
pmax | 1 | 1.1
pmin | 0 | 0
frqflg | 0 | 0
dPmax | 99 | 9
dPmin | -99 | -9
tpord | 5 | 0.1
imax | 1.2 | 1.2
pqflag | 0 | 0
vl0 | 0.49 | 0.5
vl1 | 0.54 | 0.52
vh0 | 1.2 | 1.21
vh1 | 1.15 | 1.19
tvl0 | 0.16 | 200
tvl1 | 1.5 | 0
tvh0 | 0.16 | 200
tvh1 | 1.5 | 0
vrfrac | 0.5 | 0.5
fltrp | 58.5 | 59
fhtrp | 61.2 | 61
tf1 | 300 | 1
tfh | 300 | 1
tg | 0.02 | 0.02
rrpwr | 2 | 5
tv | 0.02 | 0.2
kpg | 0.1 | 0.1
kig | 10 | 0.05
xe | 0.25 | 0.5
typeflag | 1 | 1
vfth | 0.3 | 0.8
Iqhl | 1
Iqll | -1