## Entity Contact Tab
X
Attachment A
2025 Reporting Form
PRC-006-WECC-CRT-3.1
WECC Underfrequency Load Shedding Criterion
UFLS Entity Data Submittals Requirements
Compliance with the WECC Coordinated Plan,
Western Power Pool (WPP) Sub-area Coordinated Plan, &
Southern Island Load Tripping Plan (SILTP)
|  |  | Entity NCR #: | NCRID |  |  |  | *Select from dropdown |  | Entity Name:
|  |  | Entity Name: | Entity |  |  |  | *Prepopulates unless manual entry selected |  | Entity Acroynm:
|  |  | Entity Acroynm: | Acronym |  |  |  | *Prepopulates unless manual entry selected
|  | Respondent's Name: | [5 empty] | *Required Field
|  |  | E-mail: |  |  |  |  | *Required Field
|  |  | Phone Number: |  |  |  |  | *Required Field
|  |  | Entity Functions: | GO | TO | TOP | DP-UFLS
| Please select all applicable functions: | [6 empty] | *Should prepopulate
Are you an applicable entity per section 4 of PRC-006? | [6 empty] | (YES, NO) | *Required Field | YES
Do you own or operate generators that meet the modeling requirements of PRC-006-5 D.B.4.? | [6 empty] | (YES, NO) | *Required Field | NO
Are you submitting data for more than one registered entity? | [6 empty] | *Required Field | Name of Entity
If so which entities? | [5 empty] | NCRID |  | Entity
[6 empty] | NCRID |  | Entity
[6 empty] | NCRID |  | Entity
[6 empty] | NCRID |  | Entity
Is another entity submitting data for you? | [6 empty] | *Required Field | Name of Entity
If so which entity? | [5 empty] | NCRID |  | Entity
Notes:
v.2025PRC006

## EntityList (hidden)
Entity | Functions | Acronym | NCRID | Jurisdiction | Item Type | Path
Manual Entry
Calpine Corporation | GO, GOP | CPN | NCR00006 | US | Item | Lists/EntityList
Plains End II, LLC | GO | PEII | NCR00082 | US | Item | Lists/EntityList
Boise-Kuna Irrigation District | GO | BKID | NCR00086 | US | Item | Lists/EntityList
DGC Operations, LLC | GOP | DGCO | NCR00125 | US | Item | Lists/EntityList
Vistra Corp. | GO | VST | NCR00200 | US | Item | Lists/EntityList
Energy Northwest - Columbia | GO, GOP | ENWC | NCR00209 | US | Item | Lists/EntityList
Energy Northwest - Energy/Business Services | GO, GOP | ENWB | NCR00250 | US | Item | Lists/EntityList
BHE Glacier Wind, LLC | GO, GOP | NGW | NCR00257 | US | Item | Lists/EntityList
Colorado Energy Management - RMP | GOP | CRMP | NCR00339 | US | Item | Lists/EntityList
Nevada Gold Energy LLC | GO, GOP, TO | NNEI | NCR00377 | US | Item | Lists/EntityList
NAES Corporation - White Creek Wind 1 | GO, GOP | NAES-WC | NCR00418 | US | Item | Lists/EntityList
Montana-Dakota Utilities Company | DP, RP, TO | MDUCO | NCR01015 | US | Item | Lists/EntityList
Southwest Power Pool, Inc. | RC, TSP | SPP | NCR01143 | US | Item | Lists/EntityList
Grays Harbor Energy LLC | GO, GOP | GHE | NCR02551 | US | Item | Lists/EntityList
New Harquahala Generating Company, LLC - HGBA | BA | HGBA | NCR02552 | US | Item | Lists/EntityList
Trans Bay Cable LLC | TO, TOP, TP | TBAY | NCR03036 | US | Item | Lists/EntityList
Arlington Valley, LLC - AVBA | BA | AVBA | NCR03049 | US | Item | Lists/EntityList
Arlington Valley, LLC | GO, GOP | AVGO | NCR03051 | US | Item | Lists/EntityList
AES Alamitos, LLC | GO, GOP | ALGS | NCR05002 | US | Item | Lists/EntityList
AES Huntington Beach, LLC | GO, GOP | AESH | NCR05004 | US | Item | Lists/EntityList
Aragonne Wind LLC | GO, GOP | AGW | NCR05014 | US | Item | Lists/EntityList
Arizona Electric Power Cooperative, Inc. | GO, GOP, RP, TO, TOP, TP, TSP | AEPC | NCR05015 | US | Item | Lists/EntityList
Arizona Public Service Company | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | AZPS | NCR05016 | US | Item | Lists/EntityList
Avista Corporation | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | AVA | NCR05020 | US | Item | Lists/EntityList
Basin Electric Power Cooperative | DP, GO, GOP, RP, TO, TP, TSP | BEPC | NCR05023 | US | Item | Lists/EntityList
SWG Arapahoe, LLC | GO, GOP | BHC | NCR05029 | US | Item | Lists/EntityList
Black Hills Corporation | DP, GO, GOP, RP, TO, TOP, TP, TSP | BHP | NCR05030 | US | Item | Lists/EntityList
Bonneville Power Administration | BA, RP, TO, TOP, TP, TSP | BPA | NCR05032 | US | Item | Lists/EntityList
Bountiful City Light & Power | DP | BCLP | NCR05033 | US | Item | Lists/EntityList
Burney Forest Products, A Joint Venture | GO, GOP | BFP | NCR05039 | US | Item | Lists/EntityList
Terra-Gen Dixie Valley, LLC | GO, GOP | CADV | NCR05043 | US | Item | Lists/EntityList
California Department of Water Resources | GO, GOP, RP, TO, TP | CDWR | NCR05047 | US | Item | Lists/EntityList
California Independent System Operator | BA, RC, TOP, TSP | CISO | NCR05048 | US | Item | Lists/EntityList
City of Anaheim | DP, RP | ANHM | NCR05067 | US | Item | Lists/EntityList
City of Azusa | RP | CYAZ | NCR05069 | US | Item | Lists/EntityList
City of Burbank | DP, RP | BURB | NCR05072 | US | Item | Lists/EntityList
City of Colton | RP | CYCL | NCR05074 | US | Item | Lists/EntityList
City of Fort Collins | DP | CYFC | NCR05079 | US | Item | Lists/EntityList
City of Glendale | DP | GLEN | NCR05081 | US | Item | Lists/EntityList
City of Idaho Falls Electric Light Division | DP, GO, GOP | CYIF | NCR05084 | US | Item | Lists/EntityList
City of Longmont | DP | CYLM | NCR05086 | US | Item | Lists/EntityList
City of Loveland, Colorado | DP | CYLV | NCR05087 | US | Item | Lists/EntityList
City of Palo Alto | DP | CYPL | NCR05089 | US | Item | Lists/EntityList
City of Pasadena Water and Power | DP, RP, TO, TP | CYPW | NCR05090 | US | Item | Lists/EntityList
City of Redding | DP, GO, GOP, RP, TO, TOP, TP | RDNG | NCR05091 | US | Item | Lists/EntityList
City of Riverside Public Utilities | DP, RP | CYRS | NCR05093 | US | Item | Lists/EntityList
City of Roseville | DP, RP | CYRO | NCR05094 | US | Item | Lists/EntityList
City of St George | DP, GO, GOP | CYSG | NCR05096 | US | Item | Lists/EntityList
City of Tacoma, Department of Public Utilities, Light Division | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | TPWR | NCR05097 | US | Item | Lists/EntityList
Colorado Springs Utilities | DP, GO, GOP, RP, TO, TOP, TP, TSP | CSU | NCR05106 | US | Item | Lists/EntityList
Colstrip Energy Limited Partnership | GO | CELP | NCR05107 | US | Item | Lists/EntityList
Continental Divide Electric Cooperative | DP | CDEC | NCR05115 | US | Item | Lists/EntityList
Coso Energy Developers | GO, GOP | COSE | NCR05119 | US | Item | Lists/EntityList
Coso Finance Partners | GO, GOP | COSF | NCR05120 | US | Item | Lists/EntityList
Coso Power Developers | GO, GOP | COSP | NCR05122 | US | Item | Lists/EntityList
Cowlitz County PUD No. 1 | DP, GO, TO, TP | COWPD | NCR05123 | US | Item | Lists/EntityList
Crockett Cogeneration, a California Limited Partnership | GO, GOP | CROC | NCR05124 | US | Item | Lists/EntityList
Deseret Generation & Transmission Co-operative | GO, GOP, RP, TO, TP, TSP | DGTII | NCR05126 | US | Item | Lists/EntityList
El Paso Electric Company | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | EPE | NCR05140 | US | Item | Lists/EntityList
NRG Energy Services, LLC â€“ El Segundo | GOP | ELSP | NCR05141 | US | Item | Lists/EntityList
Elk Hills Power, LLC | GO, GOP | EHP | NCR05143 | US | Item | Lists/EntityList
Eugene Water & Electric Board | DP, GO, GOP, TO, TP | EWEB | NCR05153 | US | Item | Lists/EntityList
Fall River Rural Electric/PNGC | DP | FRRE | NCR05154 | US | Item | Lists/EntityList
Farmington Electric Utility System | DP, GO, GOP, RP, TO, TOP, TP | FEUS | NCR05155 | US | Item | Lists/EntityList
Fountain Valley Power, LLC | GO, GOP | FVP | NCR05162 | US | Item | Lists/EntityList
Frederickson Power LP | GO, GOP | FPWR | NCR05164 | US | Item | Lists/EntityList
Glacier Electric Cooperative, Inc. | TO | GLEC | NCR05171 | US | Item | Lists/EntityList
Grays Harbor County PUD | DP, TO, TP | GHPD | NCR05172 | US | Item | Lists/EntityList
Harbor Cogeneration Company, LLC | GO, GOP | HCC | NCR05177 | US | Item | Lists/EntityList
Hermiston Generating Co., L.P. | GO, GOP | HERM | NCR05181 | US | Item | Lists/EntityList
Hetch Hetchy Water and Power | GO, GOP, TO, TOP, TP | HHWP | NCR05182 | US | Item | Lists/EntityList
High Desert Power Project, LLC | GO | HDPP | NCR05184 | US | Item | Lists/EntityList
Holy Cross Energy | DP, TO | HCE | NCR05190 | US | Item | Lists/EntityList
Idaho Power Company | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | IPCO | NCR05191 | US | Item | Lists/EntityList
Imperial Irrigation District | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | IID | NCR05195 | US | Item | Lists/EntityList
Indigo Generation, LLC | GO | INDG | NCR05197 | US | Item | Lists/EntityList
Klickitat County PUD | DP, TO, TP | KCPD | NCR05206 | US | Item | Lists/EntityList
Larkspur Energy, LLC | GO | LARK | NCR05213 | US | Item | Lists/EntityList
Lassen Municipal Utility District | DP | LMUD | NCR05216 | US | Item | Lists/EntityList
Los Angeles Department of Water and Power | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | LDWP | NCR05223 | US | Item | Lists/EntityList
Lower Valley Energy | DP, TO, TP | LVE | NCR05225 | US | Item | Lists/EntityList
Malacha Hydro Limited Partnership GOP | GO, GOP | MHGOP | NCR05229 | US | Item | Lists/EntityList
HF Sinclair Puget Sound Refining LLC | GO, GOP | MPCC | NCR05232 | US | Item | Lists/EntityList
Merced Irrigation District | DP, GO, GOP | MEID | NCR05234 | US | Item | Lists/EntityList
Mesquite Power LLC | GO | MPL | NCR05235 | US | Item | Lists/EntityList
Metropolitan Water District of Southern California | RP, TO, TP | MWDSC | NCR05236 | US | Item | Lists/EntityList
Modesto Irrigation District | DP, GO, GOP, RP, TO, TOP, TP | MID | NCR05244 | US | Item | Lists/EntityList
Mt. Poso Cogeneration Co. | GO, GOP | MTPO | NCR05254 | US | Item | Lists/EntityList
Municipal Energy Agency of Nebraska | RP | MEAN | NCR05256 | US | Item | Lists/EntityList
Murray City Corporation | DP | MUPD | NCR05257 | US | Item | Lists/EntityList
NV Energy | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | NEVP | NCR05261 | US | Item | Lists/EntityList
NV Energy | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | NEVP | NCR05261 | US | Item | Lists/EntityList
New Harquahala Generating Company, LLC | GO, GOP | HGMA | NCR05263 | US | Item | Lists/EntityList
Northern California Power Agency | GO, GOP | NCPA | NCR05278 | US | Item | Lists/EntityList
Northern Wasco County People's Utility District | DP, TO, TP | NWCP | NCR05280 | US | Item | Lists/EntityList
Northwest Power Pool Reserve Sharing Group | RSG | NWPP RSG | NCR05281 | US | Item | Lists/EntityList
NorthWestern Corporation | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | NWC | NCR05282 | US | Item | Lists/EntityList
Public Utility District No. 1 of Okanogan County | DP, TO | OCPD | NCR05286 | US | Item | Lists/EntityList
Oregon Trail Electric Consumers Cooperative | TO | OTEC | NCR05287 | US | Item | Lists/EntityList
Pacific Gas and Electric Company | DP, GO, GOP, RP, TO, TOP, TP | PGAE | NCR05299 | US | Item | Lists/EntityList
PacifiCorp | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | PAC | NCR05304 | US | Item | Lists/EntityList
Pend Oreille County Public Utility District No. 1 | DP, GO, GOP, TO, TP | POPD | NCR05315 | US | Item | Lists/EntityList
Plains End, LLC | GO | PEL | NCR05320 | US | Item | Lists/EntityList
Platte River Power Authority | GO, GOP, RP, TO, TOP, TP, TSP | PRPA | NCR05321 | US | Item | Lists/EntityList
Plumas-Sierra Rural Electric Cooperative | DP | PLUM | NCR05322 | US | Item | Lists/EntityList
Portland General Electric Company | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | PGE | NCR05325 | US | Item | Lists/EntityList
Talen Montana, LLC | GO, GOP | TALN | NCR05329 | US | Item | Lists/EntityList
Provo City Corporation | DP | PCYC | NCR05332 | US | Item | Lists/EntityList
Public Service Company of New Mexico | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | PNM | NCR05333 | US | Item | Lists/EntityList
Public Utility District No. 1 of Clark County | DP, GO, GOP, TO, TP | CKPD | NCR05334 | US | Item | Lists/EntityList
Public Utility District No. 1 of Snohomish County | DP, GO, GOP, TO, TOP, TP | SNPD | NCR05335 | US | Item | Lists/EntityList
Public Utility District No. 1 of Benton County | DP, GO | BCPD | NCR05337 | US | Item | Lists/EntityList
Public Utility District No. 1 of Chelan County | BA, DP, GO, GOP, RP, TO, TOP, TP | CHPD | NCR05338 | US | Item | Lists/EntityList
Public Utility District #1 of Lewis County | GO, GOP, TO, TP | LCPD | NCR05340 | US | Item | Lists/EntityList
Public Utility District No. 2 of Grant County, Washington | BA, DP, GO, GOP, RP, TO, TOP, TP | GCPD | NCR05342 | US | Item | Lists/EntityList
PUD No. 1 of Douglas County | BA, DP, GO, GOP, RP, TO, TOP, TP | DOPD | NCR05343 | US | Item | Lists/EntityList
Puget Sound Energy, Inc. | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | PSE | NCR05344 | US | Item | Lists/EntityList
Rathdrum Power, LLC | GO | RAPO | NCR05349 | US | Item | Lists/EntityList
AltaGas Ripon Energy Inc. | GO, GOP | RIPO | NCR05363 | US | Item | Lists/EntityList
Rosebud Operating Services, Inc. | GOP | ROSI | NCR05367 | US | Item | Lists/EntityList
Sacramento Municipal Utility District | DP, GO, GOP, RP, TO, TOP, TP, TSP | SMUD | NCR05368 | US | Item | Lists/EntityList
Saguaro Power Company, A Limited Partnership | GO, GOP | SPC | NCR05369 | US | Item | Lists/EntityList
Salt River Project Agricultural Improvement and Power District | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | SRP | NCR05372 | US | Item | Lists/EntityList
San Diego Gas & Electric | DP, GO, GOP, RP, TO, TOP, TP | SDGE | NCR05377 | US | Item | Lists/EntityList
Seattle City Light | BA, DP, GO, GOP, RP, TO, TOP, TP | SCL | NCR05382 | US | Item | Lists/EntityList
Sierra Pacific Industries | GO, GOP | SPI | NCR05389 | US | Item | Lists/EntityList
Silicon Valley Power | DP, GO, GOP, TO, TOP, TP | SNCL | NCR05392 | US | Item | Lists/EntityList
Southern California Edison Company | DP, GO, GOP, RP, TO, TOP, TP | SCEC | NCR05398 | US | Item | Lists/EntityList
Sunnyside Cogeneration Associates - GO | GO, GOP | SCAII | NCR05413 | US | Item | Lists/EntityList
Termoelectrica de Mexicali, S. de R.L. de C.V. | GO, GOP | MEXC | NCR05420 | US | Item | Lists/EntityList
Transmission Agency of Northern California | TO, TP, TSP | TANC | NCR05430 | US | Item | Lists/EntityList
Tri-Dam Project of the Oakdale and South San Joaquin Irrigation Districts | GO, GOP | OSJID | NCR05431 | US | Item | Lists/EntityList
Tucson Electric Power | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | TEPC | NCR05434 | US | Item | Lists/EntityList
Turlock Irrigation District | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | TID | NCR05435 | US | Item | Lists/EntityList
Umatilla Electric Cooperative Assoc. | DP, TO, TP | UMEC | NCR05436 | US | Item | Lists/EntityList
US Bureau of Reclamation | GO, GOP, TO | USBR | NCR05441 | US | Item | Lists/EntityList
U.S. Department of Energy, Hanford Field Office | TO | DOERL | NCR05442 | US | Item | Lists/EntityList
US Navy, Naval Base Kitsap | TO | USNK | NCR05444 | US | Item | Lists/EntityList
Utah Associated Municipal Power Systems | GO, GOP, RP | UAMP | NCR05445 | US | Item | Lists/EntityList
Utah Municipal Power Agency | GO, GOP | UMPA | NCR05446 | US | Item | Lists/EntityList
Valley Electric Association, Inc | DP, TO, TOP, TP | VEA | NCR05447 | US | Item | Lists/EntityList
Watson Cogeneration Company | GO, GOP | WCGN | NCR05454 | US | Item | Lists/EntityList
Wellhead Power Panoche, LLC | GO | WHPP | NCR05456 | US | Item | Lists/EntityList
Wellhead Services, Inc | GOP | WHSV | NCR05457 | US | Item | Lists/EntityList
Western Area Power Administration - Desert Southwest Region | BA, TO, TOP, TP, TSP | WALC | NCR05461 | US | Item | Lists/EntityList
Western Area Power Administration - Rocky Mountain Region | BA, TO, TOP, TP, TSP | WACM | NCR05464 | US | Item | Lists/EntityList
Western Area Power Administration - Sierra Nevada Region | RP, TO, TOP, TP, TSP | WASN | NCR05465 | US | Item | Lists/EntityList
Western Area Power Administration - Upper Great Plains Region | BA, RP, TO, TOP, TP | WAUW | NCR05467 | US | Item | Lists/EntityList
City of Gallup | DP | CYGA | NCR05489 | US | Item | Lists/EntityList
City of Ukiah | DP | CYUK | NCR05494 | US | Item | Lists/EntityList
Delta-Montrose Electric Association | DP | NA | NCR05498 | US | Item | Lists/EntityList
Judith Gap Energy LLC | GO, GOP | JUGE | NCR05503 | US | Item | Lists/EntityList
KES-Kingsburg, LP | GO, GOP | KESK | NCR05504 | US | Item | Lists/EntityList
Kings River Conservation District | GO, GOP | KRCD | NCR05505 | US | Item | Lists/EntityList
La Plata Electric Association, Inc. | DP, TO | LPEA | NCR05507 | US | Item | Lists/EntityList
Midway Sunset Cogeneration Company | GO, GOP | MSCC | NCR05510 | US | Item | Lists/EntityList
National Nuclear Security Administration - Los Alamos National Laboratory | DP, TO | NNSAL | NCR05515 | US | Item | Lists/EntityList
Public Service Company of Colorado | BA, DP, GO, GOP, RP, TO, TOP, TP, TSP | PSCO | NCR05521 | US | Item | Lists/EntityList
Public Utility District No. 1 of Whatcom County | TO, TP | WCPD | NCR05522 | US | Item | Lists/EntityList
San Luis Valley Rural Electric Cooperative, Inc. | DP | SLVR | NCR05524 | US | Item | Lists/EntityList
Spindle Hill Energy LLC | GO, GOP | SPHE | NCR05529 | US | Item | Lists/EntityList
TransAlta Centralia Generation, LLC | GO, GOP | TACG | NCR05533 | US | Item | Lists/EntityList
USACE - Omaha District | GO, GOP | UNWO | NCR05537 | US | Item | Lists/EntityList
USACE - Portland District | GO, GOP | UNWP | NCR05538 | US | Item | Lists/EntityList
USACE - Seattle District | GO, GOP | UNWS | NCR05539 | US | Item | Lists/EntityList
USACE - Walla Walla District | GO, GOP | UNWW | NCR05540 | US | Item | Lists/EntityList
NextEra Energy Resources, LLC | GO, GOP | NEER | NCR10019 | US | Item | Lists/EntityList
Tri-State Generation and Transmission Association, Inc. - Reliability | GO, GOP, RP, TO, TOP, TP, TSP | TSGT | NCR10030 | US | Item | Lists/EntityList
Alameda Municipal Power | DP | APAT | NCR10042 | US | Item | Lists/EntityList
Columbia Basin Hydropower | GO, GOP | CBHP | NCR10043 | US | Item | Lists/EntityList
Nevada Cogeneration Associates #1 | GO, GOP | NVI | NCR10044 | US | Item | Lists/EntityList
Woodland Biomass Power LLC | GO, GOP | WDBM | NCR10047 | US | Item | Lists/EntityList
Luminant Energy Company, LLC | GOP | LUMI | NCR10133 | US | Item | Lists/EntityList
Cedar Creek Wind Energy, LLC | GO, GOP | CCWE | NCR10165 | US | Item | Lists/EntityList
Brush Power | GO, GOP | COPP | NCR10195 | US | Item | Lists/EntityList
Rocky Mountain Power, LLC | GO | RMPS | NCR10197 | US | Item | Lists/EntityList
Valencia Power, LLC | GO, GOP | VALP | NCR10216 | US | Item | Lists/EntityList
Avangrid Renewables | BA, GO, GOP | PPME | NCR10259 | US | Item | Lists/EntityList
National Nuclear Security Administration and Sandia National Laboratories - | DP | NNSAA | NCR10260 | US | Item | Lists/EntityList
Deriva Energy Services, LLC | GOP | DEGS | NCR10264 | US | Item | Lists/EntityList
Shiloh Wind Project 2, LLC | GO, GOP | SWPII | NCR10292 | US | Item | Lists/EntityList
Three Buttes Windpower LLC | GO | TBWIN | NCR10345 | US | Item | Lists/EntityList
Panoche Energy Center LLC | GO | PENG | NCR10347 | US | Item | Lists/EntityList
Windy Flats Partners, LLC | GO, GOP | WFLA | NCR10350 | US | Item | Lists/EntityList
Milford Wind Corridor Phase I, LLC | GO, GOP | MILW | NCR10394 | US | Item | Lists/EntityList
BHE Power Watch, LLC | BA | NPGW | NCR10395 | US | Item | Lists/EntityList
Otay Mesa Energy Center, LLC | GO, GOP | OTAY | NCR10396 | US | Item | Lists/EntityList
City of Spokane Waste-to-Energy Facility | GO, GOP | SWTE | NCR11025 | US | Item | Lists/EntityList
South Feather Power Project | GO, GOP | SFPP | NCR11054 | US | Item | Lists/EntityList
Lone Star Transmission, LLC | TOP | NA | NCR11076 | US | Item | Lists/EntityList
Vantage Wind Energy LLC | GO, GOP | VWEL | NCR11078 | US | Item | Lists/EntityList
Goshen Phase II LLC | GO, GOP | GPL | NCR11089 | US | Item | Lists/EntityList
Top of the World | GO | TOPW | NCR11090 | US | Item | Lists/EntityList
Idaho Wind Partners 1, LLC | GO, GOP | IWPL | NCR11103 | US | Item | Lists/EntityList
NAES Corporation - Harvest Wind Project | GO, GOP | NAES-HW | NCR11104 | US | Item | Lists/EntityList
Balancing Authority of Northern California | BA | BANC | NCR11118 | US | Item | Lists/EntityList
NRG Energy Services, LLC - Walnut Creek | GOP | GCAI | NCR11148 | US | Item | Lists/EntityList
GenOn Energy Inc. | GO, GOP | GCAII | NCR11149 | US | Item | Lists/EntityList
NRG Energy Services, LLC â€“ Marsh Landing | GOP | GEND | NCR11150 | US | Item | Lists/EntityList
Cedar Creek II, LLC | GO, GOP | CCII | NCR11161 | US | Item | Lists/EntityList
Shepherds Flat Wind, LLC | GO, GOP | CAIT | NCR11170 | US | Item | Lists/EntityList
Agua Caliente Solar LLC | GO | AGCS | NCR11209 | US | Item | Lists/EntityList
Rockland Wind Farm LLC | GO, GOP | RWFL | NCR11214 | US | Item | Lists/EntityList
CORE Electric Cooperative | DP, TO, TOP | IREA | NCR11226 | US | Item | Lists/EntityList
Shiloh III Wind Project, LLC. | GO, GOP | SIIIW | NCR11232 | US | Item | Lists/EntityList
Mariposa Energy, LLC | GO | MARI | NCR11256 | US | Item | Lists/EntityList
Mustang Hills, LLC | GO, GOP | MHLL | NCR11261 | US | Item | Lists/EntityList
Cedar Point Wind, LLC | GO, GOP | CPWL | NCR11271 | US | Item | Lists/EntityList
BHE Rim Rock Wind, LLC | GO, GOP | NERR | NCR11272 | US | Item | Lists/EntityList
Mesquite Solar 1, LLC | GO, GOP | MSOL | NCR11273 | US | Item | Lists/EntityList
Rio Bravo Fresno | GO, GOP | RBFR | NCR11277 | US | Item | Lists/EntityList
Pacific-Ultrapower Chinese Station | GO, GOP | PUPCS | NCR11279 | US | Item | Lists/EntityList
Copper Mountain Solar 2, LLC | GO, GOP | CMSL | NCR11290 | US | Item | Lists/EntityList
Rio Bravo Rocklin | GO, GOP | RBROC | NCR11296 | US | Item | Lists/EntityList
Meadow Creek Project Company LLC | GO, GOP | MCREEK | NCR11303 | US | Item | Lists/EntityList
NAES Corporation - Ferndale | GOP | NAES-FD | NCR11306 | US | Item | Lists/EntityList
Sentinel Energy Center, LLC | GO, GOP | CPVSL | NCR11307 | US | Item | Lists/EntityList
Constellation Energy Generation, LLC â€“ Western Region | GO, GOP | EXEL | NCR11325 | US | Item | Lists/EntityList
Mountain Air Projects, LLC | GO, GOP | MAPL | NCR11328 | US | Item | Lists/EntityList
Topaz Solar Farms LLC | GO, GOP | TSFL | NCR11342 | US | Item | Lists/EntityList
Palouse Wind, LLC | GO | PWIND | NCR11344 | US | Item | Lists/EntityList
Pinyon Pines Wind I, LLC | GO, GOP | PPWI | NCR11347 | US | Item | Lists/EntityList
Pinyon Pines Wind II, LLC | GO, GOP | PPWII | NCR11350 | US | Item | Lists/EntityList
Orange Grove Energy, L.P. | GO, GOP | OGEL | NCR11352 | US | Item | Lists/EntityList
Russell City Energy Company, LLC | GO, GOP | RCEC | NCR11353 | US | Item | Lists/EntityList
CSolar IV South, LLC | GO | CSIV | NCR11359 | US | Item | Lists/EntityList
MATL LLP | TO, TOP, TP, TSP | MATL | NCR11360 | US | Item | Lists/EntityList
BHE Wind Watch, LLC | BA | NWIND | NCR11382 | US | Item | Lists/EntityList
Colorado Highlands Wind, LLC | GO, GOP | CHWL | NCR11389 | US | Item | Lists/EntityList
Gridforce Energy Management, LLC | BA, TOP | GRID | NCR11393 | US | Item | Lists/EntityList
Nevada Solar One, LLC | GO, GOP | NSONE | NCR11395 | US | Item | Lists/EntityList
Southern Power Company | GO, GOP | SPOW | NCR11396 | US | Item | Lists/EntityList
Barrick Goldstrike Mines Inc. | GO, GOP | BGMI | NCR11411 | US | Item | Lists/EntityList
ORNI 47 LLC | GO, GOP | ORNI | NCR11412 | US | Item | Lists/EntityList
Placer County Water Agency | GO, GOP | PCWA | NCR11420 | US | Item | Lists/EntityList
Ivanpah Master Holdings LLC | GO, GOP | IVAN | NCR11421 | US | Item | Lists/EntityList
Solar Star California XIX, LLC | GO, GOP | SSCA | NCR11424 | US | Item | Lists/EntityList
Arlington Valley Solar Energy II, LLC | GO, GOP | AVSE | NCR11426 | US | Item | Lists/EntityList
Imperial Valley Solar 1, LLC | GO | IVSO | NCR11427 | US | Item | Lists/EntityList
Yuba County Water Agency | GO, GOP | YUBA | NCR11428 | US | Item | Lists/EntityList
Centinela Solar Energy, LLC | GO, GOP | CSEL | NCR11431 | US | Item | Lists/EntityList
Solar Star California XX, LLC | GO, GOP | SSXX | NCR11432 | US | Item | Lists/EntityList
Blythe Energy Inc. | GO, GOP | BLYT | NCR11433 | US | Item | Lists/EntityList
CalPECo | DP | CPAC | NCR11439 | US | Item | Lists/EntityList
EDF Renewable Service | GOP | EDFR | NCR11441 | US | Item | Lists/EntityList
Pacific Wind | GO, GOP | PACWN | NCR11442 | US | Item | Lists/EntityList
Hudson Ranch Power I | GO, GOP | HUDS | NCR11443 | US | Item | Lists/EntityList
Western Power and Steam II LLC | GO, GOP | WPSI | NCR11445 | US | Item | Lists/EntityList
Shiloh IV Wind Project, LLC | GO, GOP | SWPIV | NCR11450 | US | Item | Lists/EntityList
ASI Operations Inc | GO, GOP | ASI | NCR11452 | US | Item | Lists/EntityList
TransAlta Wyoming Wind LLC | GO, GOP | TAWW | NCR11457 | US | Item | Lists/EntityList
Mojave 16/17/18, LLC | GO, GOP | MOJV | NCR11463 | US | Item | Lists/EntityList
Los Angeles Department of Water and Power - APEX | GO, GOP | APEX | NCR11467 | US | Item | Lists/EntityList
Nevada Irrigation District | GO, GOP | NID | NCR11469 | US | Item | Lists/EntityList
Sunrise Power Company, LLC | GO, GOP | SNRS | NCR11471 | US | Item | Lists/EntityList
Copper Mountain Solar 3, LLC | GO, GOP | CMSOL | NCR11476 | US | Item | Lists/EntityList
Catalina Solar, LLC | GO, GOP | CATA | NCR11484 | US | Item | Lists/EntityList
ACE O&M, LLC | GO, GOP | ACE | NCR11516 | US | Item | Lists/EntityList
NAES - Panoche | GOP | NAES-PN | NCR11518 | US | Item | Lists/EntityList
ORNI 39 LLC | GO, GOP | ORTN | NCR11521 | US | Item | Lists/EntityList
AltaGas Brush Energy Inc. | GO, GOP | AGBR | NCR11528 | US | Item | Lists/EntityList
Spring Canyon Energy LLC | GO, GOP | SPCE | NCR11529 | US | Item | Lists/EntityList
Energia Sierra Juarez, S. de R.L. de C.V. | GO, GOP | ENSJ | NCR11531 | US | Item | Lists/EntityList
Solar Star California XIII, LLC | GO | SXIII | NCR11549 | US | Item | Lists/EntityList
SPI Anderson 2 | GO, GOP | SPIA | NCR11557 | US | Item | Lists/EntityList
Energy Keepers Incorporated | GO, GOP | EKI | NCR11568 | US | Item | Lists/EntityList
CSolar IV West, LLC | GO | CSW | NCR11572 | US | Item | Lists/EntityList
Red Horse Wind 2, LLC | GO | RHWII | NCR11578 | US | Item | Lists/EntityList
NAES Corporation - Plains End | GOP | NAES-PE | NCR11589 | US | Item | Lists/EntityList
NAES Corporation - Rathdrum Power | GOP | NAES-RP | NCR11590 | US | Item | Lists/EntityList
Tonopah Solar Energy, LLC | GO, GOP | TSE | NCR11594 | US | Item | Lists/EntityList
RWE Clean Energy Asset Holdings, Inc. | GO, GOP | CEDI | NCR11605 | US | Item | Lists/EntityList
Red Horse III, LLC | GO | RHIII | NCR11630 | US | Item | Lists/EntityList
NAES Corporation - High Desert Power Project | GOP | NAES-HD | NCR11632 | US | Item | Lists/EntityList
62SK 8ME LLC | GO | SBKI | NCR11634 | US | Item | Lists/EntityList
63SU 8ME LLC | GO | SBKII | NCR11643 | US | Item | Lists/EntityList
AE Power Services LLC | GOP | AEPS | NCR11645 | US | Item | Lists/EntityList
Brookfield Power US Asset Management LLC | GOP | NA | NCR11647 | US | Item | Lists/EntityList
Pio Pico Energy Center, LLC | GO, GOP | PPEC | NCR11652 | US | Item | Lists/EntityList
Mojave 3/4/5 | GO, GOP | TGMV | NCR11653 | US | Item | Lists/EntityList
Mesquite Solar 3, LLC | GO, GOP | MSIII | NCR11661 | US | Item | Lists/EntityList
EDP Renewables North America LLC | GO, GOP | EDPR NA | NCR11662 | US | Item | Lists/EntityList
Comanche Solar PV, LLC | GO | CMCH | NCR11665 | US | Item | Lists/EntityList
Copper Mountain Solar 4, LLC | GO, GOP | CMSIV | NCR11666 | US | Item | Lists/EntityList
Mesquite Solar 2, LLC | GO, GOP | MSII | NCR11672 | US | Item | Lists/EntityList
AES US Renewables | GO, GOP | SPS | NCR11679 | US | Item | Lists/EntityList
Catalina Solar 2, LLC | GO | CSII | NCR11680 | US | Item | Lists/EntityList
SOLV Energy, LLC | GOP | SOLV | NCR11685 | US | Item | Lists/EntityList
Moapa Southern Paiute Solar, LLC | GO | FSEM | NCR11697 | US | Item | Lists/EntityList
Golden Fields Solar I, LLC | GO | GFSI | NCR11703 | US | Item | Lists/EntityList
Solar Star California XLI, LLC | GO | SXLI | NCR11704 | US | Item | Lists/EntityList
Western Interconnect LLC | TO, TSP | WITP | NCR11708 | US | Item | Lists/EntityList
Three Peaks Power LLC | GO | TPP | NCR11737 | US | Item | Lists/EntityList
Hill County Electric Cooperative, Inc. | DP, TO | HILL | NCR11744 | US | Item | Lists/EntityList
Powder River Energy Corporation | DP, TO | PREC | NCR11745 | US | Item | Lists/EntityList
EDF RAH - Playa Solar, LLC | GO | EDFPS | NCR11757 | US | Item | Lists/EntityList
CD Global Solar NC Sponsor, L.P. | GO | CDGS | NCR11775 | US | Item | Lists/EntityList
GridLiance Holdco, LLC | TO | GDLH | NCR11783 | US | Item | Lists/EntityList
Clearlight Energy (America) LLC | GO, GOP | NA | NCR11785 | US | Item | Lists/EntityList
California Flats Solar, LLC | GO | CFS | NCR11801 | US | Item | Lists/EntityList
Great Valley Solar Portfolio Holdings, LLC | GO, GOP | GVS | NCR11806 | US | Item | Lists/EntityList
Pattern Operators LP | GO, GOP | POLP | NCR11808 | US | Item | Lists/EntityList
Western Frequency Response Sharing Group | FRSG | WFRSG | NCR11825 | US | Item | Lists/EntityList
54KR 8ME LLC | GO | REDIV | NCR11826 | US | Item | Lists/EntityList
ORNI 43 LLC | GO, GOP | ORNI43 | NCR11839 | US | Item | Lists/EntityList
Luz Solar Partners Ltd. IX | GO, GOP | LUZIX | NCR11849 | US | Item | Lists/EntityList
NRG Energy Services, LLC - Carlsbad | GOP | CECL | NCR11854 | US | Item | Lists/EntityList
Imperial Valley Solar 3, LLC | GO | IVS3 | NCR11858 | US | Item | Lists/EntityList
ORNI 41 | GO, GOP | ORNI41 | NCR11881 | US | Item | Lists/EntityList
Clearway Energy Operating LLC - Fossil | GO | CEOF | NCR11883 | US | Item | Lists/EntityList
Techren Solar I LLC | GO | TECH | NCR11904 | US | Item | Lists/EntityList
Voyager II | GO, GOP | VOII | NCR11905 | US | Item | Lists/EntityList
Willow Springs, LLC | GO | WSLC | NCR11906 | US | Item | Lists/EntityList
MRP - San Joaquin Energy, LLC | GO | MRPS | NCR11912 | US | Item | Lists/EntityList
NAES San Joaquin | GOP | NAES-SJ | NCR11913 | US | Item | Lists/EntityList
64KT 8ME LLC | GO | KT8M | NCR11921 | US | Item | Lists/EntityList
CXA La Paloma, LLC | GO, GOP | NA | NCR11922 | US | Item | Lists/EntityList
Clearway Renewable Operation & Maintenance LLC | GO, GOP | NA | NCR11926 | US | Item | Lists/EntityList
North Rosamond Solar, LLC | GO | NA | NCR11927 | US | Item | Lists/EntityList
NAES Corporation - Sycamore | GO, GOP | NA | NCR11928 | US | Item | Lists/EntityList
NAES Corporation - Kern River | GO, GOP | NA | NCR11929 | US | Item | Lists/EntityList
NAES CalPeak Panoche | GOP | NA | NCR11936 | US | Item | Lists/EntityList
NAES CalPeak Power Vaca-Dixon | GOP | NA | NCR11937 | US | Item | Lists/EntityList
NAES Malaga Power | GOP | NA | NCR11938 | US | Item | Lists/EntityList
NAES Midway Peaking | GOP | NA | NCR11939 | US | Item | Lists/EntityList
Calpeak Power Panoche LLC | GO | NA | NCR11940 | US | Item | Lists/EntityList
CalPeak Power Vaca-Dixon, LLC | GO | NA | NCR11941 | US | Item | Lists/EntityList
Malaga Power, LLC | GO | NA | NCR11942 | US | Item | Lists/EntityList
Midway Peaking, LLC | GO | NA | NCR11943 | US | Item | Lists/EntityList
RE Mustang Holdings LLC | GO | NA | NCR11951 | US | Item | Lists/EntityList
RE Astoria LLC | GO | NA | NCR11955 | US | Item | Lists/EntityList
RE Astoria 2 LLC | GO | NA | NCR11956 | US | Item | Lists/EntityList
Valentine Solar, LLC | GO, GOP | NA | NCR11959 | US | Item | Lists/EntityList
Imperial Valley Solar 2, LLC | GO | NA | NCR11961 | US | Item | Lists/EntityList
AES Alamitos Energy LLC | GO, GOP | NA | NCR11966 | US | Item | Lists/EntityList
AES Huntington Beach Energy LLC | GO, GOP | NA | NCR11967 | US | Item | Lists/EntityList
Voyager Wind I, LLC | GO, GOP | NA | NCR11989 | US | Item | Lists/EntityList
Miller Bros. Solar, LLC | GOP | NA | NCR11990 | US | Item | Lists/EntityList
Wright Solar Park LLC | GO | WSPK | NCR12001 | US | Item | Lists/EntityList
Horizon West Transmission, LLC | TO, TP | NA | NCR12006 | US | Item | Lists/EntityList
Willow Creek Energy LLC | GO, GOP | NA | NCR12013 | US | Item | Lists/EntityList
DesertLink, LLC | TO, TP | NA | NCR12025 | US | Item | Lists/EntityList
Steamboat Hills, LLC | GO, GOP | NA | NCR12028 | US | Item | Lists/EntityList
Gateway Energy Storage, LLC | GO, GOP | NA | NCR12035 | US | Item | Lists/EntityList
Mountain Breeze Wind, LLC | GO, GOP | NA | NCR12046 | US | Item | Lists/EntityList
Utah Red Hills Renewable Park, LLC | GO | NA | NCR12050 | US | Item | Lists/EntityList
RE Mustang Two LLC | GO | NA | NCR12063 | US | Item | Lists/EntityList
Griffith Energy | GO, GOP | NA | NCR12070 | US | Item | Lists/EntityList
Maverick Solar, LLC | GO, GOP | NA | NCR12079 | US | Item | Lists/EntityList
Maverick Solar 4, LLC | GO, GOP | NA | NCR12080 | US | Item | Lists/EntityList
Desert Harvest, LLC | GO, GOP | NA | NCR12081 | US | Item | Lists/EntityList
ACT Power Services, LLC | GOP | NA | NCR12082 | US | Item | Lists/EntityList
Desert Harvest II, LLC | GO, GOP | NA | NCR12085 | US | Item | Lists/EntityList
Cove Mountain 2, LLC | GO | NA | NCR12089 | US | Item | Lists/EntityList
Cove Mountain 1, LLC | GO | NA | NCR12090 | US | Item | Lists/EntityList
NovaSource Power Services | GOP | NA | NCR12096 | US | Item | Lists/EntityList
AES ES Alamitos, LLC | GO, GOP | NA | NCR12104 | US | Item | Lists/EntityList
Wind Wall 1 LLC | GO, GOP | NA | NCR12116 | US | Item | Lists/EntityList
Milford Solar I | GO | NA | NCR12117 | US | Item | Lists/EntityList
Battle Mountain SP, LLC | GO, GOP | NA | NCR12118 | US | Item | Lists/EntityList
Pioneer Solar (CO), LLC | GO | NA | NCR12119 | US | Item | Lists/EntityList
Rancho Seco Solar II, LLC | GO | NA | NCR12120 | US | Item | Lists/EntityList
Copper Mountain Solar 5, LLC | GO, GOP | NA | NCR12121 | US | Item | Lists/EntityList
Little Bear Solar 1, LLC | GO | longroadenergy | NCR12124 | US | Item | Lists/EntityList
Little Bear Solar 3, LLC | GO | NA | NCR12125 | US | Item | Lists/EntityList
Hunter Solar LLC | GO | NA | NCR12126 | US | Item | Lists/EntityList
Harry Allen Solar Energy, LLC | GO | NA | NCR12127 | US | Item | Lists/EntityList
Invenergy Services-Dry Lake | GOP | NA | NCR12128 | US | Item | Lists/EntityList
Terra-Gen Operating Company LLC | GO, GOP | NA | NCR12142 | US | Item | Lists/EntityList
Diablo Energy Storage, LLC | GO, GOP | revrenewables | NCR12151 | US | Item | Lists/EntityList
NAES Corporation - Aquamarine | GO, GOP | NA | NCR12159 | US | Item | Lists/EntityList
Origis Services, LLC | GOP | NA | NCR12161 | US | Item | Lists/EntityList
Sun Streams 2 | GO | NA | NCR12164 | US | Item | Lists/EntityList
Sigurd Solar LLC | GO | NA | NCR12173 | US | Item | Lists/EntityList
HDSI, LLC | GO | NA | NCR12187 | US | Item | Lists/EntityList
Maverick Solar 6, LLC | GO, GOP | NA | NCR12198 | US | Item | Lists/EntityList
Maverick Solar 7, LLC | GO, GOP | NA | NCR12199 | US | Item | Lists/EntityList
SE Athos II, LLC | GO | NA | NCR12200 | US | Item | Lists/EntityList
Bighorn Solar 1, LLC | GO | NA | NCR12215 | US | Item | Lists/EntityList
Townsite Solar, LLC | GO | NA | NCR12222 | US | Item | Lists/EntityList
Canadian Solar O&M (U.S.) LLC | GOP | NA | NCR12223 | US | Item | Lists/EntityList
RE Slate 1, LLC | GO | NA | NCR12224 | US | Item | Lists/EntityList
Spring Canyon Energy II LLC | GO, GOP | NA | NCR12252 | US | Item | Lists/EntityList
Spring Canyon Energy III LLC | GO, GOP | NA | NCR12253 | US | Item | Lists/EntityList
Graphite Solar I, LLC | GO | NA | NCR12254 | US | Item | Lists/EntityList
LeConte Energy Storage, LLC | GO, GOP | NA | NCR12265 | US | Item | Lists/EntityList
SE Athos I, LLC | GO | NA | NCR12267 | US | Item | Lists/EntityList
Panorama Wind, LLC | GO, GOP | NA | NCR12268 | US | Item | Lists/EntityList
Drew Solar LLC | GO | NA | NCR12293 | US | Item | Lists/EntityList
Jackpot Solar Project, LLC | GO | NA | NCR12318 | US | Item | Lists/EntityList
Sun Mountain Solar 1, LLC | GO | NA | NCR12319 | US | Item | Lists/EntityList
MTSun Solar LLC | GO | NA | NCR12320 | US | Item | Lists/EntityList
Sonoran West Solar Holdings, LLC | GO | NA | NCR12324 | US | Item | Lists/EntityList
Arrow Canyon Solar, LLC | GO, GOP | NA | NCR12334 | US | Item | Lists/EntityList
Rabbitbrush Solar, LLC | GO, GOP | NA | NCR12335 | US | Item | Lists/EntityList
Lockhart Solar PV, LLC (Lockhart I) | GO | NA | NCR12346 | US | Item | Lists/EntityList
Lockhart Solar PV II, LLC (Lockhart II) | GO | NA | NCR12347 | US | Item | Lists/EntityList
Gaskell West | GO | NA | NCR12348 | US | Item | Lists/EntityList
325MK 8me LLC | GO | NA | NCR12349 | US | Item | Lists/EntityList
Sagebrush ESS, LLC | GO | NA | NCR12350 | US | Item | Lists/EntityList
WGP Redwood Holdings, LLC | GO, GOP | NA | NCR12353 | US | Item | Lists/EntityList
Onward Energy ROC LLC | GOP | NA | NCR12355 | US | Item | Lists/EntityList
North Valley Geothermal | GO, GOP | NA | NCR12368 | US | Item | Lists/EntityList
Apex Solar LLC | GO | NA | NCR12369 | US | Item | Lists/EntityList
Fall River Solar, LLC | GO | NA | NCR12370 | US | Item | Lists/EntityList
Warren Substation | TO | NA | NCR12372 | US | Item | Lists/EntityList
Arroyo Energy Storage LLC | GO | NA | NCR12373 | US | Item | Lists/EntityList
Appaloosa Solar I, LLC | GO | NA | NCR12424 | US | Item | Lists/EntityList
Strauss Wind, LLC | GO, GOP | NA | NCR12425 | US | Item | Lists/EntityList
Eleven-Mile Solar Center, LLC | GO | NA | NCR12452 | US | Item | Lists/EntityList
IP Oberon, LLC | GO | NA | NCR12453 | US | Item | Lists/EntityList
NAES Corporation - Chestnut | GO, GOP | NA | NCR12459 | US | Item | Lists/EntityList
NAES Corporation - Solar Blue | GO, GOP | NA | NCR12460 | US | Item | Lists/EntityList
Sun Streams PVS, LLC | GO | NA | NCR12463 | US | Item | Lists/EntityList
Blythe Mesa Solar II, LLC | GO | NA | NCR12466 | US | Item | Lists/EntityList
Invenergy Services-Rancho Seco II | GOP | NA | NCR12468 | US | Item | Lists/EntityList
Lighthouse Renewables, Corp. | GO | NA | NCR12470 | US | Item | Lists/EntityList
Escalante Solar, LLC | GO | NA | NCR12471 | US | Item | Lists/EntityList
Superstition Energy Storage, LLC | GO | NA | NCR12475 | US | Item | Lists/EntityList
BigBeau Solar, LLC | GO, GOP | NA | NCR12477 | US | Item | Lists/EntityList
Rocket Solar, LLC | GO | NA | NCR12479 | US | Item | Lists/EntityList
Solar Partners XI, LLC | GO | NA | NCR12480 | US | Item | Lists/EntityList
RWE Clean Energy, LLC | GO, GOP | NA | NCR12482 | US | Item | Lists/EntityList
Jicarilla Apache Nation Power Authority | TO, TP | NA | NCR12486 | US | Item | Lists/EntityList
Tumbleweed Energy Storage, LLC | GO, GOP | NA | NCR12488 | US | Item | Lists/EntityList
Condor Energy Storage, LLC | GO | NA | NCR12498 | US | Item | Lists/EntityList
RNWBL, LLC | GOP | NA | NCR12501 | US | Item | Lists/EntityList
QE Solar, LLC | GOP | NA | NCR12507 | US | Item | Lists/EntityList
Steel Solar, LLC | GO | NA | NCR12508 | US | Item | Lists/EntityList
Vikings Energy Farm LLC | GO | NA | NCR12512 | US | Item | Lists/EntityList
Sierra Estrella Energy Storage, LLC | GO | NA | NCR12519 | US | Item | Lists/EntityList
Beaumont ESS, LLC | GO | NA | NCR12521 | US | Item | Lists/EntityList
SJS 1 Storage, LLC | GO | NA | NCR12522 | US | Item | Lists/EntityList
68SF 8me, LLC | GO | NA | NCR12523 | US | Item | Lists/EntityList
White Wing Ranch North, LLC | GO, GOP | NA | NCR12540 | US | Item | Lists/EntityList
Boswell Wind, LLC | GO, GOP | NA | NCR12544 | US | Item | Lists/EntityList
Desert Quartzite, LLC | GO | NA | NCR12557 | US | Item | Lists/EntityList
Encino Solar | GO, GOP | NA | NCR12558 | US | Item | Lists/EntityList
Hunter Solar, LLC (Hunter Colorado) | GO | NA | NCR12563 | US | Item | Lists/EntityList
Elektron Solar, LLC | GO | NA | NCR12567 | US | Item | Lists/EntityList
Horseshoe Solar, LLC | GO | NA | NCR12568 | US | Item | Lists/EntityList
Pleasant Valley Solar, LLC | GO | NA | NCR12571 | US | Item | Lists/EntityList
DCR Transmission, L.L.C. | TO, TP | NA | NCR13009 | US | Item | Lists/EntityList
LS Power Grid California | TO, TOP, TP | NA | NCR13015 | US | Item | Lists/EntityList

## Tab 1a - Aggregate Load (WECC)
OFF-NOMINAL FREQUENCY SYSTEM PROTECTION AND RESTORATION PLAN
Compliance with the WECC
Coordinated Plan (Plan 1a)
Company Name: _____________________________________________
| Location of Load: |  | Northern Island |  |  | Southern Island |  |  | Both
What is the amount of load that your company trips to comply with the WECC Coordinated Plan (1a)?
| During Winter Peak: |  |  | (MW) |  |  | During Summer Peak: |  |  | (MW)
Does your company change the load armed to be tripped seasonally?
|  |  |  | ___ Yes |  | ___ No
If yes, provide a set of data for all seasons that have different loads armed to be tripped.
Are there any other exceptions to the WECC plan (1a)? Yes ___ No ___
If yes, please explain:
| Is the peak during the winter or summer? |  |  |  | Winter: |  | Summer:
| Company Peak Load that participates in the WECC Coordinated Plan (1a): | [7 empty] | (MW)
How much load will your company trip at each of the following frequency points to comply with the
WECC Coordinated Plan (1a)(no intentional tripping time delay):
| Block | Frequency |  | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
| 1 | 59.1 | [5 empty] | no more than 14 cycles
| 2 | 58.9 | [5 empty] | no more than 14 cycles
| 3 | 58.7 | [5 empty] | no more than 14 cycles
| 4 | 58.5 | [5 empty] | no more than 14 cycles
| 5 | 58.3 | [5 empty] | no more than 14 cycles
|  | TOTAL |  | 0 |  | 0
Does your company trip additional load at frequencies lower than the minimum standard of 58.3 Hz?
Yes ___ No ___
If so, please fill in the following table completely.
|  | Frequency |  | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
58.1
57.9
57.7
57.5
|  | TOTAL |  | 0 |  | 0
Comments:
(Page 1 of 2)
How much load will your company trip at each of the following frequency points to comply with the
WECC Coordinated Plan (1a)(load shedding to correct for underfrequency stalling):
| Block | Frequency |  | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
| 6 | 59.3 | [5 empty] | 15 sec
| 7 | 59.5 | [5 empty] | 30 sec
| 8 | 59.5 | [5 empty] | 1 min
|  | TOTAL |  | 0 |  | 0
Comments:
How much load will your company restore at each of the following frequency points to comply with the
WECC Coordinated Plan (1a)(automatic load restoration to correct for frequency overshoot):
| Block | Frequency |  | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
| 9 | 60.5 | [5 empty] | 30 sec
| 10 | 60.7 | [5 empty] | 5 sec
| 11 | 60.9 | [5 empty] | 0.25 sec
|  | TOTAL |  | 0 |  | 0
Comments:
Does your company have additional automatic load restoration at frequencies not listed in the table
above? Yes ___ No ___
If so, please fill out the following table completely and add comments to demonstrate your compliance.
|  | Frequency |  | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
|  | TOTAL |  | 0 |  | 0
Comments:
(Page 2 of 2)
Northern Island
Southern Island

## Tab 1b - Aggregate Load (WPP)
OFF-NOMINAL FREQUENCY SYSTEM PROTECTION AND RESTORATION PLAN
Compliance with the Western Power Pool (WPP) sub-area
Coordinated Plan (Plan 1b)
Company Name: _____________________________________________
What is the amount of load that your company trips to comply with the Northwest Power Pool sub-area
plan?
| During Winter Peak: |  | (MW) |  | During Summer Peak: |  |  | (MW)
Does your company change the load armed to be tripped seasonally?
|  |  | ___ Yes | ___ No
If yes, provide a set of data for all seasons that have different loads armed to be tripped.
Are there any other exceptions to the Northwest Power Pool sub-area plan (1b)? Yes ___ No ___
If yes, please explain:
Is the peak during the winter or summer? Winter ___ Summer ___
| Company Peak Load that participates in the NWPP sub-area Plan (1b): | [5 empty] | (MW)
How much load will your company trip at each of the following frequency points to comply with the
NWPP sub-area Plan (1b)(no intentional tripping time delay):
| Block | Frequency | % of Load at Peak | MW at Peak |  | Total Tripping (relay + breaker) Time
| 1 | 59.3 |  |  |  | no more than 14 cycles
| 2 | 59.2 |  |  |  | no more than 14 cycles
| 3 | 59 |  |  |  | no more than 14 cycles
| 4 | 58.8 |  |  |  | no more than 14 cycles
| 5 | 58.6 |  |  |  | no more than 14 cycles
|  | TOTAL | 0 | 0
Does your company trip additional load at frequencies lower than the minimum standard of 58.3 Hz?
Yes ___ No ___
If so, please fill in the following table completely.
|  | Frequency | % of Load at Peak | MW at Peak |  | Total Tripping (relay + breaker) Time
58.1
57.9
57.7
57.5
|  | TOTAL | 0 | 0
Comments:
(Page 1 of 2)
How much load will your company trip at each of the following frequency points to comply with the
NWPP sub-area Plan (1b)(load shedding to correct for underfrequency stalling):
| Block | Frequency | % of Load at Peak | MW at Peak |  | Total Tripping (relay + breaker) Time
| 6 | 59.3 |  |  |  | 15 sec
| 7 | 59.5 |  |  |  | 30 sec
| 8 | 59.5 |  |  |  | 1 min
|  | TOTAL | 0 | 0
Comments:
How much load will your company restore at each of the following frequency points to comply with the
NWPP sub-area Plan (1b)(automatic load restoration to correct for frequency overshoot):
| Block | Frequency | % of Load at Peak | MW at Peak |  | Total Tripping (relay + breaker) Time
| 9 | 60.5 |  |  |  | 30 sec
| 10 | 60.7 |  |  |  | 5 sec
| 11 | 60.9 |  |  |  | 0.25 sec
|  | TOTAL | 0 | 0
Comments:
Does your company have additional automatic load restoration at frequencies not listed in the table
above? Yes ___ No ___
If so, please fill out the following table completely and add comments to demonstrate your compliance.
|  | Frequency | % of Load at Peak | MW at Peak |  | Total Tripping (relay + breaker) Time
|  | TOTAL | 0 | 0
Comments:
(Page 2 of 2)
Northern Island
Southern Island

## Tab 1c - Aggregate Load (SILTP)
OFF-NOMINAL FREQUENCY SYSTEM PROTECTION AND RESTORATION PLAN
Compliance with the
Southern Island Load Tripping Plan (SILTP) (Plan 1c)
Company Name: _____________________________________________
How is your company complying with the Southern Island Load Tripping Plan?
| ___ Direct Load Tripping |  |  | ___ 59.6 Hz Tripping |  |  |  | __ 59.5 Hz Tripping
Based on the response above, what is the amount of load that your company trips to comply with the
SILTP (1c)?
| During Winter Peak: |  | (MW) |  |  | During Summer Peak: |  |  | (MW)
Does your company change the load armed to be tripped seasonally?
|  |  | ___ Yes |  | __ No
If yes, provide a set of data for all seasons that have different loads armed to be tripped.
Are there any other exceptions to the SILTP? ___ Yes __ No
If yes, please explain:
| Company Peak Load that participates in the SILTP (1c): | [5 empty] | (MW)
Did you move load from 59.1 Hz to 59.5/59.6 Hz? ___ Yes __ No
How much load will your company trip at each of the following frequency points to comply with the
SILTP (1c) (no intentional tripping time delay):
| Block | Frequency | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
|  | DLT (SILTP) |  |  |  |  | no more than 14 cycles
|  | 59.6 (SILTP) |  |  |  |  | no more than 14 cycles
|  | 59.5 (SILTP) |  |  |  |  | no more than 14 cycles
| 1 | 59.1 |  |  |  |  | no more than 14 cycles
| 2 | 58.9 |  |  |  |  | no more than 14 cycles
| 3 | 58.7 |  |  |  |  | no more than 14 cycles
| 4 | 58.5 |  |  |  |  | no more than 14 cycles
| 5 | 58.3 |  |  |  |  | no more than 14 cycles
|  | TOTAL | 0% |  | 0
Does your company trip additional load at frequencies lower than the minimum standard of 58.3 Hz?
Yes ___ No ___
If so, please fill in the following table completely.
|  | Frequency | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
58.1
57.9
57.7
57.5
|  | TOTAL | 0% |  | 0
Comments:
(Page 1 of 2)
How much load will your company trip at each of the following frequency points to comply with the
SILTP (1c) (load shedding to correct for underfrequency stalling):
| Block | Frequency | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
| 6 | 59.3 |  |  |  |  | 15 sec
| 7 | 59.5 |  |  |  |  | 30 sec
| 8 | 59.5 |  |  |  |  | 1 min
|  | TOTAL | 0% |  | 0
Comments:
How much load will your company restore at each of the following frequency points to comply with the
SILTP (1c) (automatic load restoration to correct for frequency overshoot):
| Block | Frequency | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
| 9 | 60.5 |  |  |  |  | 30 sec
| 10 | 60.7 |  |  |  |  | 5 sec
| 11 | 60.9 |  |  |  |  | 0.25 sec
|  | TOTAL | 0% |  | 0
Comments:
Does your company have additional automatic load restoration at frequencies not listed in the table
above? Yes ___ No ___
If so, please fill out the following table completely and add comments to demonstrate your compliance.
|  | Frequency | % of Load at Peak |  | MW at Peak |  | Total Tripping (relay + breaker) Time
|  | TOTAL | 0% |  | 0
Comments:
(Page 2 of 2)
Northern Island
Southern Island

## Tab 2 - Detail Load
UNDER FREQUENCY LOAD SHED
UFLS SCHEDULE (YEAR) _________
| Total System Peak in (Year): |  |  | (MW)
| UF Block (SILTP) | Element Tripped (Line, Substation, Transformer, Feeder) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Reset Freq. (Hz) | Trip Time Delay (sec) | Breaker Time (cycles) | Total Tripping Time | Manual Restore Delay Time (Min) | Load Shed MW
|  |  |  | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
DLT
DLT
DLT
DLT
DLT
DLT
|  |  |  | Req. MW Load Shed for Block #1 | [7 empty] | Block #1 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #1 | [7 empty] | Block #1 % Load Shed
Note:
| UF Block (SILTP) | Element Tripped (Line, Substation, Transformer, Feeder) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Reset Freq. (Hz) | Trip Time Delay (sec) | Breaker Time (cycles) | Total Tripping Time | Manual Restore Delay Time (Min) | Load Shed MW
|  |  |  | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
59.6
59.6
59.6
59.6
59.6
59.6
|  |  |  | Req. MW Load Shed for Block #1 | [7 empty] | Block #1 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #1 | [7 empty] | Block #1 % Load Shed
Note:
| UF Block (SILTP) | Element Tripped (Line, Substation, Transformer, Feeder) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Reset Freq. (Hz) | Trip Time Delay (sec) | Breaker Time (cycles) | Total Tripping Time | Manual Restore Delay Time (Min) | Load Shed MW
|  |  |  | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
59.5
59.5
59.5
59.5
59.5
59.5
|  |  |  | Req. MW Load Shed for Block #1 | [7 empty] | Block #1 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #1 | [7 empty] | Block #1 % Load Shed
Note:
| UF Block # | Element Tripped (Line, Substation, Transformer, Feeder) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Reset Freq. (Hz) | Trip Time Delay (sec) | Breaker Time (cycles) | Total Tripping Time | Manual Restore Delay Time (Min) | Load Shed MW
|  |  |  | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
1
1
1
1
1
1
|  |  |  | Req. MW Load Shed for Block #1 | [7 empty] | Block #1 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #1 | [7 empty] | Block #1 % Load Shed
Note:
2
2
2
2
2
2
|  |  |  | Req. MW Load Shed for Block #2 | [7 empty] | Block #2 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #2 | [7 empty] | Block #2 % Load Shed
Note:
3
3
3
3
3
|  |  |  | Req. MW Load Shed for Block #3 | [7 empty] | Block #3 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #3 | [7 empty] | Block #3 % Load Shed
Note:
4
4
4
4
4
|  |  |  | Req. MW Load Shed for Block #4 | [7 empty] | Block #4 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #4 | [7 empty] | Block #4 % Load Shed
Note:
5
5
5
5
5
|  |  |  | Req. MW Load Shed for Block #5 | [7 empty] | Block #5 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #5 | [7 empty] | Block #5 % Load Shed
Note:
(Page 1 of 3)
UNDER FREQUENCY LOAD SHED
UFLS SCHEDULE (YEAR) _________
Automatic load shedding to correct for under frequency stalling.
| UF Block # | Element Tripped (Line, Substation, Transformer, Feeder) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Reset Freq. (Hz) | Trip Time Delay (sec) | Breaker Time (cycles) | Total Tripping Time | Manual Restore Delay Time (Min) | Load Shed MW
|  |  |  | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
6
6
6
6
6
|  |  |  | Req. MW Load Shed for Block #6 | [7 empty] | Block #6 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #6 | [7 empty] | Block #6 % Load Shed
Note:
7
7
7
7
7
7
|  |  |  | Req. MW Load Shed for Block #7 | [7 empty] | Block #7 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #7 | [7 empty] | Block #7 % Load Shed
Note:
8
8
8
8
8
8
|  |  |  | Req. MW Load Shed for Block #8 | [7 empty] | Block #8 Total MW Load Shed
|  |  |  | Req. % Load Shed for Block #8 | [7 empty] | Block #8 % Load Shed
Note:
(Page 2 of 3)
UNDER FREQUENCY LOAD SHED
UFLS SCHEDULE (YEAR) _________
Load automatically restored to correct for frequency overshoot.
| Auto Reset Block # | Element Tripped (Line, Substation, Transformer, Feeder) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Over Freq. (Hz) | Reset Freq. (Hz) | Automatic Restoration Time Delay (sec) |  |  |  | Load Restore MW
|  |  |  | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
9
9
|  |  |  | Req. MW Load Restore for Block #9 | [7 empty] | Total MW Load Restore
|  |  |  | Req. % Load Restore for Block #9 | [7 empty] | % Load Restore for this Block
Note:
10
10
10
|  |  |  | Req. MW Load Restore for Block #10 | [7 empty] | Total MW Load Restore
|  |  |  | Req. % Load Restore for Block #10 | [7 empty] | % Load Restore for this Block
Note:
11
11
11
|  |  |  | Req. MW Load Restore for Block #11 | [7 empty] | Total MW Load Restore
|  |  |  | Req. % Load Restore for Block #11 | [7 empty] | % Load Restore for this Block
Note:
Does your company use only solid state and/or microprocessor underfrequency relays to comply with the WECC Coordinated Plan? ____ Yes ____ No
If No, please explain here:
Will your company's frequency relays use define time characteristics and operate within any voltage above 80% of nominal? ____ Yes ____ No
If No, please explain here:
Are there any other exceptions to the WECC Coordinated Plan? ____ Yes ____ No
If Yes, please explain here:
(Page 3 of 3)

## Tab 3a – Load PSLF (lsdt9)
[9 empty] | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
NEW | Dynamic Model in PSLF format - Line and Load Protection Models | [7 empty] | 16: Legend
UPDATE | Notes: PASTE AS VALUES ONLY OR BREAKS FORMATTING | [7 empty] | 17: If a cell is highlighted orange, it indicates we can't find that model in our database and is either a new model or the ID is different (verify the device exists in the basecase with the same ID)
DELETE | Models should also be reflected in the WECC Master Dynamics File by submitting the DYD data to the applicable Transmission Planner or directly to WECC (email: basecase@wecc.org)
NO CHANGES REQUIRED | [8 empty] | 17: If a cell is highlighted red, it indicates the data you provided is different from our database. Verify the data you are providing is the most up to date so we can keep our database accurate
Models should be based on system configurations in current Operating Base Cases.
**PLEASE ENTER NAME AND ID AS IT IS IN THE WECC BASE CASE
Dynamic Model for Substations
| Model Status | Model | Bus Number | Name | Voltage (kV) | ID | PSLF Syntax | Output Channel Level | 15: Transducer Time Constant (sec); 16: Reset Time (sec); 17: First stage; 21: Second stage (if applicable); 25: Third stage (if applicable); 29: Fourth stage (if applicable); 33: Fifth stage (if applicable); 37: Sixth stage (if applicable); 41: Seventh stage (if applicable); 45: Eight stage (if applicable); 49: Ninth stage (if applicable)
[11 empty] | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu) | Pick up (Hz) | Time Delay (sec) | Breaker delay (sec) | Shedding Fraction (pu)
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9
lsdt9

## Tab 3b – Load PSLF (tlin1)
| Dynamic Model in PSLF format - Line and Load Protection Models | [8 empty] | Legend
NEW | Notes: PASTE AS VALUES ONLY OR BREAKS FORMATTING | [9 empty] | If a cell is highlighted orange, it indicates we can't find that model in our database and is either a new model or the ID is different (verify the device exists in the basecase with the same ID)
UPDATE | Models should also be reflected in the WECC Master Dynamics File by submitting the DYD data to the applicable Transmission Planner or directly to WECC (email: basecase@wecc.org)
DELETE | [10 empty] | If a cell is highlighted red, it indicates the data you provided is different from our database. Verify the data you are providing is the most up to date so we can keep our database accurate
NO CHANGES REQUIRED | Models should be based on system configurations in current Operating Base Cases.
[13 empty] | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
**PLEASE ENTER NAME AND ID AS IT IS IN THE WECC BASE CASE
Dynamic Model for Lines
| Model Status | Model | From Bus Number | Name | Voltage (kV) | ID | To Bus Number | Name | Voltage | ID | PSLF Syntax | Output Channel Level | Input Signal (0=f, 1=v) | Transducer or Filter Time Constant (sec) | Mode Flag | Far End Bus Number | Relay pickup setting | Relay Time Setting | Circuit Breaker Operating Time (sec) | External Monitored Bus Number | Output Signal
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1
tlin1

## Tab 4a - Generator
PRC-006 curves
| OFF-NOMINAL FREQUENCY SYSTEM PROTECTION AND RESTORATION PLAN | [9 empty] | time | Over frequency | Under frequency
| Compliance with the WECC | [9 empty] | 0.1 | 62.2 | 57.8
| Coordinated Plan, Western Power Pool (WPP) sub-area Coordinated Plan, & | [9 empty] | 0.2 | 62.2 | 57.8
| Southern Island Load Tripping Plan (SILTP) | [9 empty] | 0.3 | 62.2 | 57.8
[11 empty] | 0.4 | 62.2 | 57.8
[11 empty] | 0.5 | 62.2 | 57.8
| Company Name: | [9 empty] | 0.6 | 62.2 | 57.8
[11 empty] | 0.7 | 62.2 | 57.8
| Location of Generation: ____ Northern Island _____ Southern Island | [9 empty] | 0.8 | 62.2 | 57.8
[11 empty] | 0.9 | 62.2 | 57.8
GENERATOR FREQUENCY TRIPPING SCHEDULE | [10 empty] | 1 | 62.2 | 57.8
TO COMPLY WITH THE WECC COORDINATED PLAN | [10 empty] | 2 | 62.2 | 57.8
[11 empty] | 3 | 62.0827 | 57.9043
| Please provide a frequency-tripping schedule that you use for your generators to comply with the WECC | [9 empty] | 4 | 61.997 | 57.9762
| Coordinated Plan (fill out a line for each step). If you use different tripping plans for different generators, | [9 empty] | 5 | 61.9305 | 58.0319
| please fill in the Generator/Generator Group column. If your tripping plan differs from the WECC Plan, | [9 empty] | 6 | 61.8762 | 58.0774
| please explain in the comments section. COLUMN D VALUES SHOULD BE IN SECONDS. ONLY INCLUDE THE VALUE, PLEASE DON'T TYPE (s, sec, seconds) AFTER THE VALUE. COLUMN C SHOULD BE IN HERTZ, DON'T TYPE Hz | [9 empty] | 7 | 61.8303 | 58.1159
[11 empty] | 8 | 61.7905 | 58.1493
| Frequency (Hz) | Tripping Time Delay IN SECONDS | WECC Bus # | WECC Unit # | Generator/Generator Group* | Physical Location |  |  |  |  | 9 | 61.7554 | 58.1787
[11 empty] | 10 | 61.724 | 58.205
[11 empty] | 20 | 61.5175 | 58.3781
[11 empty] | 30 | 61.3967 | 58.4793
[11 empty] | 40 | 61.311 | 58.5512
[11 empty] | 50 | 61.2445 | 58.6069
[11 empty] | 60 | 61.1902 | 58.6524
[11 empty] | 70 | 61.1443 | 58.6909
[11 empty] | 80 | 61.1045 | 58.7243
[11 empty] | 90 | 61.0694 | 58.7537
[11 empty] | 100 | 61.038 | 58.78
[11 empty] | 200 | 60.8315 | 58.9531
[11 empty] | 300 | 60.7107 | 59.0543
[11 empty] | 400 | 60.625 | 59.1262
[11 empty] | 500 | 60.5585 | 59.1819
[11 empty] | 600 | 60.5042 | 59.2274
[11 empty] | 700 | 60.4583 | 59.2659
[11 empty] | 800 | 60.4185 | 59.2993
[11 empty] | 900 | 60.3834 | 59.3287
[11 empty] | 1000 | 60.352 | 59.355
GENERATOR FREQUENCY TRIPPING SCHEDULE
TO COMPLY WITH THE WECC COORDINATED PLAN
Does your company use only solid state and/or microprocessor underfrequency relays to comply with the
[8 empty] | WECC Coordinated Plan? |  | _______ Yes ______ No
If No, please explain here:
Will your company's frequency relays use define time characteristics and operate within any voltage
[8 empty] | above 80% of nominal? |  | ______ Yes ______ No
If No, please explain here:
Are there any other exceptions to the WECC Off-Nominal Frequency Load Shedding and Restoration Plan?
______ Yes _____ No
Please explain here:
(Page 2 of 2)
* Includes Generator, Generator/Pump, and Pump
Comments:

## Tab 4b - Gen PSLF dyd data
Dynamic Model in PSLF format - Line and Load Protection Models | [9 empty] | Legend
Notes: PASTE AS VALUES ONLY OR BREAKS FORMATTING | [10 empty] | If a cell is highlighted orange, it indicates we can't find that model in our database and is either a new model or the ID is different (verify the device exists in the basecase with the same ID)
Models should also be reflected in the WECC Master Dynamics File by submitting the DYD data to the applicable Transmission Planner or directly to WECC (email: basecase@wecc.org)
If a cell is highlighted red, it indicates the data you provided is different from our database. Verify the data you are providing is the most up to date so we can keep our database accurate
Models should be based on system configurations in current Operating Base Cases.
**PLEASE ENTER NAME AND ID AS IT IS IN THE WECC BASE CASE
Dynamic Model for Generators
Model Status | Model | From Bus Number | Name | Voltage (kV) | ID | To Bus Number (if applicable) | Name (if applicable) | Voltage (if applicable) | PSLF Syntax | Output Channel Level | Frequency Reference (default = 60 Hz) | Delta freq trip level 1, Hz | Delta freq trip level 2, Hz | Delta freq trip level 3, Hz | Delta freq trip level 4, Hz | Delta freq trip level 5, Hz | Delta freq trip level 6, Hz | Delta freq trip level 7, Hz | Delta freq trip level 8, Hz | Delta freq trip level 9, Hz | Delta freq trip level 10, Hz | Delta freq trip time 1, sec | Delta freq trip time 2, sec | Delta freq trip time 3, sec | Delta freq trip time 4, sec | Delta freq trip time 5, sec | Delta freq trip time 6, sec | Delta freq trip time 7, sec | Delta freq trip time 8, sec | Delta freq trip time 9, sec | Delta freq trip time 10, sec | Alarm (default = 0)
| lhfrt | [31 empty] | PRC-006-5, Requirement D.B.4:
| lhfrt | [31 empty] | D.B.4.1 | Underfrequency trip settings of individual generating units greater
| lhfrt | [32 empty] | than 20 MVA (gross nameplate rating) directly connected to the BES
| lhfrt | [32 empty] | that trip above the Generator Underfrequency Trip Modeling curve
| lhfrt | [32 empty] | in PRC-006-5 - Attachment 1.
lhfrt
| lhfrt | [31 empty] | D.B.4.2 | Underfrequency trip settings of generating plants/facilities greater
| lhfrt | [32 empty] | than 75 MVA (gross aggregate nameplate rating) directly connected
| lhfrt | [32 empty] | to the BES that trip above the Generator Underfrequency Trip
| lhfrt | [32 empty] | Modeling curve in PRC-006-5 - Attachment 1.
lhfrt
| lhfrt | [31 empty] | D.B.4.3 | Underfrequency trip settings of any facility consisting of one or more
| lhfrt | [32 empty] | units connected to the BES at a common bus with total generation
| lhfrt | [32 empty] | above 75 MVA (gross nameplate rating) that trip above the
| lhfrt | [32 empty] | Generator Underfrequency Trip Modeling curve in PRC-006-5 -
| lhfrt | [32 empty] | Attachment 1.
lhfrt
| lhfrt | [31 empty] | D.B.4.4 | Overfrequency trip settings of individual generating units greater
| lhfrt | [32 empty] | than 20 MVA (gross nameplate rating) directly connected to the BES
| lhfrt | [32 empty] | that trip below the Generator Overfrequency Trip Modeling curve in
| lhfrt | [32 empty] | PRC-006-5 — Attachment 1.
lhfrt
| lhfrt | [31 empty] | D.B.4.5 | Overfrequency trip settings of generating plants/facilities greater
| lhfrt | [32 empty] | than 75 MVA (gross aggregate nameplate rating) directly connected
| lhfrt | [32 empty] | to the BES that trip below the Generator Overfrequency Trip
| lhfrt | [32 empty] | Modeling curve in PRC-006-5 — Attachment 1.
lhfrt
| lhfrt | [31 empty] | D.B.4.6 | Overfrequency trip settings of any facility consisting of one or more
| lhfrt | [32 empty] | units connected to the BES at a common bus with total generation
| lhfrt | [32 empty] | above 75 MVA (gross nameplate rating) that trip below the
| lhfrt | [32 empty] | Generator Overfrequency Trip Modeling curve in PRC-006-5 —
| lhfrt | [32 empty] | Attachment 1.
lhfrt
| lhfrt | [31 empty] | D.B.4.7 | Any automatic Load restoration that impacts frequency stabilization
| lhfrt | [32 empty] | and operates within the duration of the simulations run for the
| lhfrt | [32 empty] | assessment
lhfrt
lhfrt
lhfrt
lhfrt
Add additional rows as necessary

## Tab 5 - Tie Line
WECC Coordinated Plan
Compliance with the WECC
Coordinated Plan, Western Power Pool (WPP) sub-area Coordinated Plan, &
Southern Island Load Tripping Plan (SILTP)
Company Name: ____________________________________________________
Location of Generation: ____ Northern Island _____ Southern Island
TIE-LINE UNDER-FREQUENCY TRIPPING
TO COMPLY WITH THE WECC COORDINATED PLAN
Please provide tie-line under-frequency tripping that your company use to comply with the WECC
Coordinated Plan. If you use different tripping plans for different tie-line, please fill in
the table below. If your tripping plan differs from the WECC Plan, please
explain in the comments section.
| Frequency (Hz) | Tripping Time Delay | Transmission Line Name | Voltage (kV) | Metering End | Name of Utility Company Transmission Line Ties to
Comments:
(Page 1 of 2)
TIE-LINE UNDER-FREQUENCY TRIPPING
TO COMPLY WITH THE WECC COORDINATED PLAN
Does your company use only solid state and/or microprocessor underfrequency relays to comply with the
WECC Coordinated Plan?
If No, please explain here:
Will your company's frequency relays use define time characteristics and operate within any voltage
above 80% of nominal?
If No, please explain here:
Are there any other exceptions to the WECC Off-Nominal Frequency Load Shedding and Restoration Plan?
______ Yes _____ No
Please explain here:
(Page 2 of 2)

## Tab 6 - Shunts
Tab 6 - SHUNT WITH Frequency Trips
Substation | Breaker Number(s) | Substation Name or Line From |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Cap Group | Section | Feeder KV | MVAR to Trip
|  | WECC Bus Name | WECC Bus #

## Contents and Applicability
Attachment A
PRC-006-WECC-CRT-3.1
Underfrequency Load Shedding Criterion
UFLS Entity Data Submittals Requirements
Compliance with the WECC Coordinated Plan,
Western Power Pool (WPP) Sub-area Coordinated Plan, &
Southern Island Load Tripping Plan (SILTP)
Tab Name | Applicability | Due Date
Entity Contact Tab | All UFLS Entities | July 1 annually
Tab 1a - Aggregate Load (WECC) | UFLS Entities that adopted the WECC plan (not SILTP or NWPP sub-area plans) | July 1 annually
Tab 1b - Aggregate Load (NWPP) | UFLS Entities that adopted the WPP sub-area plan | July 1 annually
Tab 1c - Aggregate Load (SILTP) | UFLS Entities that adopted the SILTP sub-area plan | July 1 annually
Tab 2 - Detail Load | All UFLS Entities that adopted a load tripping plan | July 1 annually
Tab 3a - Load PSLF (lsdt9) | All UFLS Entities that adopted a load tripping plan | July 1 annually
Tab 3b - Load PLSF (tlin1) | All UFLS Entities that adopted a load tripping plan | July 1 annually
Tab 4a - Generator | All GOs that have generators that must be explicitly modeled pursuant to WECC data reporting requirements | June 1 annually
Tab 4b - Generator PSLF dyd data | All GOs that: 1) have generators that must be explicitly modeled pursuant to WECC data reporting requirements; and 2) have frequency tripping within the Underfrequency Trip Modeling curves for generators in PRC-006 - Attachment 1 | June 1 annually
Tab 5 - Tie Line | All UFLS Entities that have Tie-Lines | July 1 annually
Tab 6 - Shunts | All UFLS Entities that have Shunts | July 1 annually

## Track History of Changes
# | Tasks/Actions | Date | By | Comments
1 | Draft data submittals request form for WECC-0065 Under-frequency Load Shedding Criterion | 2010-02-09 | Chue Thor - SMUD | These data submittal request forms were draft based 'Off-Frequency System Protection and Restoration Committee' form and internal discussions.
2 | Revised to align with updated Criterion from December 2010 Drafting Team Meeting | 2010-12-17 | Mark Willis - SMUD
3 | Added Tab 4b, revised "Tab 4" to "Tab 4a", updated Contents and Applicability tab to reflect changes | 2014-04-09 | UFLSRG | PSLF model lhfrt was added to the WECC Approved Dynamics Model List in August 2013.
4 | Clarified Tabs 1a, 1b, and 1c. Corrected "Delta freq trip time" units on Tab 4b | 2015-04-08 | UFLSRG
5 | Included WECC Island Location Map - NE/SE separation scheme cut-plane and Frequency Ride Through (lhfrt) Description on the Reference Documentation Tab | 2015-05-01 | Kent Bolton - WECC | Added reference information to address frequently asked questions
6 | Cell C3 updated to reflect most recent SAR | 2016-03-09 | W. Shannon Black - WECC
7 | Revised for clarity | 2016-04-25 | UFLSRG
8 | Added information on WECC islands, clarified requirements for generator dyd models, and clarified scope of load dyd models | 2017-04-07 | UFLSRG
9 | Locked sheets and some columns so they could not be deleted | 2018-04-30 | Tyson Niemann-WECC | Locked cells for consistency purposes
10 | Added "Model Status" column on Tab 3 & Tab 4b | 2019-12-30 | Tyson Niemann-WECC
11 | Added additional entity submittal box on Entity Contact Tab, separated Tab 3 into two sheets (Tab 3a and Tab 3b), added conditional formating to Tabs 3a, 3b, 4a, and 4b. Added PRC-006 curve to Tab 4b | 2021-04-29 | WECC | Updated with data checking and automation
12 | Updated Entity Contact page, added individual cells for MW in Tab 1 and 2 | 2022-01-31 | WECC | Updated with data checking and automation
13 | Updated Entity Contact page, changed wording from NWPP to WPP, updated PRC standard references | 2023-05-01 | WECC | Updated with data checking and automation
14 | Added manual entry option on Entity Contact Tab | 2024-04-09 | WECC
Notes.
1. This tab was created to track the progress of drafting the 'Data Submittals Request Form'.

## mdf_lsdt9 (hidden)
unique_ID | no. | Bus | Name | kv | ID | st | area | zone | Mbase | MbaseR | MODEL_LID | : | #9 | tfilter | treset | fp1 | Tp1 | Tcb1 | sf1 | fp2 | Tp2 | Tcb2 | sf2 | fp3 | Tp3 | Tcb3 | sf3 | fp4 | Tp4 | Tcb4 | sf4 | fp5 | Tp5 | Tcb5 | sf5 | fp6 | Tp6 | Tcb6 | sf6 | fp7 | Tp7 | Tcb7 | sf7 | fp8 | Tp8 | Tcb8 | sf8 | fp9 | Tp9 | Tcb9 | sf9
100051 | lsdt9 | 10005 | ALCAZAR | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100171 | lsdt9 | 10017 | ARRIBA | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100201 | lsdt9 | 10020 | ASPEN | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100341 | lsdt9 | 10034 | BEL_AIR | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100401 | lsdt9 | 10040 | BEV_WOOD | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100431 | lsdt9 | 10043 | BLCKRA | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100611 | lsdt9 | 10061 | CENTRALP | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.13333 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100671 | lsdt9 | 10067 | CLAREMNT | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100701 | lsdt9 | 10070 | COAL | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100761 | lsdt9 | 10076 | COLINAS | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100811 | lsdt9 | 10081 | CORNELL | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100931 | lsdt9 | 10093 | EASTRDGE | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100971 | lsdt9 | 10097 | EL_CERRO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101041 | lsdt9 | 10104 | EMBUDO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101081 | lsdt9 | 10108 | FT_MARCY | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.083333 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101151 | lsdt9 | 10115 | GIRARD | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101191 | lsdt9 | 10119 | HAMLTN_1 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101201 | lsdt9 | 10120 | HAMLTN_2 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101221 | lsdt9 | 10122 | HAWKINS | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101381 | lsdt9 | 10138 | IND_HOSP | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.13333 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101401 | lsdt9 | 10140 | INEZ | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101451 | lsdt9 | 10145 | ISLETAPAL | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101471 | lsdt9 | 10147 | JARALES | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101541 | lsdt9 | 10154 | KAFB | 115 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.083 | 0.01 | 58.9 | 0 | 0.083 | 0.06 | 58.5 | 0 | 0.083 | 0.04 | 58.3 | 0 | 0.083 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101681 | lsdt9 | 10168 | LAWRENCE | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101711 | lsdt9 | 10171 | LENKURT | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101731 | lsdt9 | 10173 | LEYENDKR | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101811 | lsdt9 | 10181 | S.ANTON2 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101881 | lsdt9 | 10188 | M_PLAZA | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101931 | lsdt9 | 10193 | MANZANO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 60 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101951 | lsdt9 | 10195 | MARIPOSA | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102031 | lsdt9 | 10203 | MENAUL | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102081 | lsdt9 | 10208 | MONTANO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102111 | lsdt9 | 10211 | MORRIS | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102221 | lsdt9 | 10222 | NO_BERN | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102341 | lsdt9 | 10234 | ORTIZ | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102351 | lsdt9 | 10235 | PALM | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102561 | lsdt9 | 10256 | PRAGER | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102581 | lsdt9 | 10258 | PRINCESS | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102691 | lsdt9 | 10269 | RIOHONDO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 60 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102711 | lsdt9 | 10271 | VERANDA | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.083333 | 0.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102731 | lsdt9 | 10273 | RITA | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 60 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102741 | lsdt9 | 10274 | RODEO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102771 | lsdt9 | 10277 | STUDIO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102831 | lsdt9 | 10283 | S._COORS | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103001 | lsdt9 | 10300 | SANPEDRO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 0.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103171 | lsdt9 | 10317 | SIGNETIC | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103251 | lsdt9 | 10325 | SPACHCO2 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103441 | lsdt9 | 10344 | TOME | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103461 | lsdt9 | 10346 | TRAMWAY | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.13333 | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103481 | lsdt9 | 10348 | TRUMAN | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103601 | lsdt9 | 10360 | VOLCANO1 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103641 | lsdt9 | 10364 | WAYNE 1 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103661 | lsdt9 | 10366 | WESMECO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103731 | lsdt9 | 10373 | WAYNE 2 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103811 | lsdt9 | 10381 | WYOMING | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103911 | lsdt9 | 10391 | SANDIAK5 | 115 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.083 | 0.04 | 59.5 | 30 | 0.083 | 0.02 | 59.5 | 60 | 0.083 | 0.03 | 59.3 | 15 | 0.083 | 0.05 | 58.7 | 0 | 0.083 | 0.16 | 58.5 | 0 | 0.083 | 0.03 | 58.3 | 0 | 0.083 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104171 | lsdt9 | 10417 | LOS_MOR1 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104411 | lsdt9 | 10441 | ENCHANTED | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104461 | lsdt9 | 10446 | LOSTHRZN | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104621 | lsdt9 | 10462 | RANDOLPH | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.083333 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104711 | lsdt9 | 10471 | PRGRSS | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104801 | lsdt9 | 10480 | IRIS | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104891 | lsdt9 | 10489 | ZAFARANO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104931 | lsdt9 | 10493 | LOS_MOR2 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104951 | lsdt9 | 10495 | DEM_GOLD | 13.8 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105021 | lsdt9 | 10502 | CDELRIO | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105221 | lsdt9 | 10522 | SNOW_VISTA | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105461 | lsdt9 | 10546 | INNOVTION | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108001 | lsdt9 | 10800 | VOLCANO2 | 12.5 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110121 | lsdt9 | 11012 | ANTHONY1 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.1 | 0.77774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110131 | lsdt9 | 11013 | ANTHONY2 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.1 | 0.60589 | 58.5 | 0.1 | 0.1 | 0.39411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110161 | lsdt9 | 11016 | ARROYO1 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110211 | lsdt9 | 11021 | ASCARATE_T1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.62921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110241 | lsdt9 | 11024 | AUSTIN | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110261 | lsdt9 | 11026 | AUSTIN_1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110271 | lsdt9 | 11027 | AUSTIN_2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 0.24265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110401 | lsdt9 | 11040 | CHAPARAL1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.1 | 0.63059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110551 | lsdt9 | 11055 | CROMO1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 0.20402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110641 | lsdt9 | 11064 | DYER_1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 0.47539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110671 | lsdt9 | 11067 | SPARKS1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.64204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110681 | lsdt9 | 11068 | CALIENTE | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.1 | 0.6369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110721 | lsdt9 | 11072 | FARAH | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.40835 | 58.9 | 0.1 | 0.1 | 0.22268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110891 | lsdt9 | 11089 | LASCRUC1 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 0.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110901 | lsdt9 | 11090 | LASCRUC2 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.36099 | 58.5 | 0.1 | 0.1 | 0.21798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110921 | lsdt9 | 11092 | LEA_T2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.1 | 0.3847 | 58.5 | 0.1 | 0.1 | 0.13304 | 58.3 | 0.1 | 0.1 | 0.48226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110961 | lsdt9 | 11096 | MANN_2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.1 | 0.46399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111071 | lsdt9 | 11107 | MONTOYA2 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.1 | 0.18361 | 58.5 | 0.1 | 0.1 | 0.44362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111091 | lsdt9 | 11109 | MONTOYA3 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111191 | lsdt9 | 11119 | MONTWOOD1 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.1 | 0.54444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111251 | lsdt9 | 11125 | PICACHO | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.33049 | 58.3 | 0.1 | 0.1 | 0.66951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111371 | lsdt9 | 11137 | SALOPEK1 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.1 | 0.2196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111441 | lsdt9 | 11144 | SCOTSDALE1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.1 | 0.1982 | 58.3 | 0.1 | 0.1 | 0.45334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111521 | lsdt9 | 11152 | SOL_1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.41827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111621 | lsdt9 | 11162 | THORN_2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.77617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111661 | lsdt9 | 11166 | VISCOUNT_T1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111681 | lsdt9 | 11168 | VISTA_1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.50905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111691 | lsdt9 | 11169 | VISTA_2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111731 | lsdt9 | 11173 | WRANGLR1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.24516 | 58.9 | 0.1 | 0.1 | 0.20213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111751 | lsdt9 | 11175 | DURAZNO1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111761 | lsdt9 | 11176 | MILAGRO2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.1 | 0.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111791 | lsdt9 | 11179 | BUTERFL2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.75972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111821 | lsdt9 | 11182 | MILAGRO3 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.39596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111841 | lsdt9 | 11184 | SPARKS2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.1 | 0.46667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111851 | lsdt9 | 11185 | RIO_BOS1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.26384 | 58.3 | 0.1 | 0.1 | 0.59901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112001 | lsdt9 | 11200 | NUWAY_2 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.1 | 0.54499 | 58.3 | 0.1 | 0.1 | 0.45501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112051 | lsdt9 | 11205 | CHAPARAL2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 0.63152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112111 | lsdt9 | 11211 | SALOPEK2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.1 | 0.50025 | 58.3 | 0.1 | 0.1 | 0.49975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112211 | lsdt9 | 11221 | PENDALE1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 0.71443 | 58.5 | 0.1 | 0.1 | 0.28557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112221 | lsdt9 | 11222 | PENDALE2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.1 | 0.54204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112251 | lsdt9 | 11225 | DIA_HD1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.37197 | 58.9 | 0.1 | 0.1 | 0.36985 | 58.7 | 0.1 | 0.1 | 0.25817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112401 | lsdt9 | 11240 | PELICANO2 | 23.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.1 | 0.27863 | 58.3 | 0.1 | 0.1 | 0.72137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112411 | lsdt9 | 11241 | SCOTSDALE2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.23358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112521 | lsdt9 | 11252 | SANTA_T2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.63076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112541 | lsdt9 | 11254 | GR_A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.85126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112551 | lsdt9 | 11255 | GR_B | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.1 | 0.46318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112941 | lsdt9 | 11294 | EXECUTIVE | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112951 | lsdt9 | 11295 | EXECUTIVE_2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.1 | 0.1 | 0.1 | 0.48938 | 58.5 | 0.1 | 0.1 | 0.51062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115011 | lsdt9 | 11501 | SUNSET_T2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.1 | 0.44163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12001TS | lsdt9 | 12001 | ALAMOGPG | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12006TS | lsdt9 | 12006 | AMISTAD | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12009TS | lsdt9 | 12009 | BERNARDO | 24.9 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.083 | 0.76 | 59.3 | 15 | 0.083 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12013TS | lsdt9 | 12013 | BLUEWATR | 24.9 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12024TS | lsdt9 | 12024 | CHUCILLO | 24.9 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12025TS | lsdt9 | 12025 | DEMINGTS | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12034TS | lsdt9 | 12034 | GRANTS | 24.9 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12037TS | lsdt9 | 12037 | HERNANDZ | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 0.1 | 0.083 | 0.54 | 58.7 | 0.1 | 0.083 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12046TS | lsdt9 | 12046 | MORIARTY | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 0.1 | 0.083 | 0.44 | 58.7 | 0.1 | 0.083 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12064TS | lsdt9 | 12064 | ROWE | 24.9 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12074TS | lsdt9 | 12074 | SOCORROP | 24.9 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12076TS | lsdt9 | 12076 | SPRINGER | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.167 | 0.083 | 0.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12090TS | lsdt9 | 12090 | YORKCANY | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12091TS | lsdt9 | 12091 | YORKCANY | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12132TS | lsdt9 | 12132 | C_CANYON | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 0.083 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12139TS | lsdt9 | 12139 | C_CANYON | 24.9 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12213TS | lsdt9 | 12213 | TORREON | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130091 | lsdt9 | 13009 | LORDSBRG | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.1 | 0.13333 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130401 | lsdt9 | 13040 | MD3 | 23 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.1 | 0.083333 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133051 | lsdt9 | 13305 | ETA-A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.07 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133111 | lsdt9 | 13311 | TA-3-BL | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.07 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133231 | lsdt9 | 13323 | ETA-B | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.07 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15104SR | lsdt9 | 15104 | CARLOTA | 115 | SR | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15108SR | lsdt9 | 15108 | HAYDENAZ | 115 | SR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15114SR | lsdt9 | 15114 | MIAMI | 115 | SR | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15119SR | lsdt9 | 15119 | PINAL | 115 | SR | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151272 | lsdt9 | 15127 | SPURLOCK | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151273 | lsdt9 | 15127 | SPURLOCK | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151291 | lsdt9 | 15129 | SUPERIOR | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151302 | lsdt9 | 15130 | CARREL | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15131SR | lsdt9 | 15131 | TRASK | 115 | SR | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153072 | lsdt9 | 15307 | ANDERSON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153073 | lsdt9 | 15307 | ANDERSON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153092 | lsdt9 | 15309 | BROADWA2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153114 | lsdt9 | 15311 | BROADWA4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153121 | lsdt9 | 15312 | FOOTHILL_S | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153122 | lsdt9 | 15312 | FOOTHILL_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153131 | lsdt9 | 15313 | HEARD 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153174 | lsdt9 | 15317 | HURLEY 4_S | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153184 | lsdt9 | 15318 | JEPSEN | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153214 | lsdt9 | 15321 | RIVERSI4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15322I | lsdt9 | 15322 | MICCHIP | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153234 | lsdt9 | 15323 | WEILER | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153241 | lsdt9 | 15324 | WILKINS1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153252 | lsdt9 | 15325 | WILKINS2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153253 | lsdt9 | 15325 | WILKINS2 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153282 | lsdt9 | 15328 | SINNOTT | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153292 | lsdt9 | 15329 | IRVIN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153293 | lsdt9 | 15329 | IRVIN | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153302 | lsdt9 | 15330 | DORMAN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153341 | lsdt9 | 15334 | HURLEY 1_S | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153364 | lsdt9 | 15336 | PARKER_S | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153372 | lsdt9 | 15337 | BARTLETT | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153383 | lsdt9 | 15338 | MARCOS 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153392 | lsdt9 | 15339 | MARCOS 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153403 | lsdt9 | 15340 | SAYLOR 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153421 | lsdt9 | 15342 | BIGSPINN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153442 | lsdt9 | 15344 | CLEMANS2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153453 | lsdt9 | 15345 | CLEMANS3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15347I | lsdt9 | 15347 | DISPLAY | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153493 | lsdt9 | 15349 | HIGHLINE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153533 | lsdt9 | 15353 | LASSEN 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153544 | lsdt9 | 15354 | MARCOS 4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15355I | lsdt9 | 15355 | OMEGA | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153562 | lsdt9 | 15356 | SAYLOR 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153613 | lsdt9 | 15361 | OWENS 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153622 | lsdt9 | 15362 | LASSEN 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153631 | lsdt9 | 15363 | LASSEN 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153654 | lsdt9 | 15365 | OWENS 4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153672 | lsdt9 | 15367 | GILA 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153683 | lsdt9 | 15368 | GILA 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153694 | lsdt9 | 15369 | GILA 4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153701 | lsdt9 | 15370 | ROE 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153712 | lsdt9 | 15371 | ROE 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153723 | lsdt9 | 15372 | ROE 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153743 | lsdt9 | 15374 | RUPPERS | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153744 | lsdt9 | 15374 | RUPPERS | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15375I | lsdt9 | 15375 | STELLAR | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153761 | lsdt9 | 15376 | WINSOR | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153762 | lsdt9 | 15376 | WINSOR | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153771 | lsdt9 | 15377 | SAYLOR 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153782 | lsdt9 | 15378 | HEARD 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153793 | lsdt9 | 15379 | HEARD 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153812 | lsdt9 | 15381 | MARLEY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15383I | lsdt9 | 15383 | AMPLIFY | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153882 | lsdt9 | 15388 | BARCELON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153883 | lsdt9 | 15388 | BARCELON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153902 | lsdt9 | 15390 | COOK 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153933 | lsdt9 | 15393 | GLENN | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153934 | lsdt9 | 15393 | GLENN | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153942 | lsdt9 | 15394 | HARMON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153943 | lsdt9 | 15394 | HARMON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153983 | lsdt9 | 15398 | MARYVALE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153984 | lsdt9 | 15398 | MARYVALE | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153992 | lsdt9 | 15399 | MOORE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153993 | lsdt9 | 15399 | MOORE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154001 | lsdt9 | 15400 | NORTHER1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154023 | lsdt9 | 15402 | NORTHER3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154034 | lsdt9 | 15403 | NORTHER4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154044 | lsdt9 | 15404 | SANDERSO | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154053 | lsdt9 | 15405 | WASSER | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154054 | lsdt9 | 15405 | WASSER | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154092 | lsdt9 | 15409 | OLIVE_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154093 | lsdt9 | 15409 | OLIVE_S | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154102 | lsdt9 | 15410 | AHWA 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154141 | lsdt9 | 15414 | FOWLER_S | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154161 | lsdt9 | 15416 | ALHAMBR1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154172 | lsdt9 | 15417 | ALHAMBR2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154183 | lsdt9 | 15418 | ALHAMBR3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154212 | lsdt9 | 15421 | ALTAVIS2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154223 | lsdt9 | 15422 | ALTAVIS3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15424I | lsdt9 | 15424 | CORTEZ 2 | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154272 | lsdt9 | 15427 | MARLETT2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154283 | lsdt9 | 15428 | MARLETT3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154300 | lsdt9 | 15430 | VALENCI2 | 69 | 0 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154302 | lsdt9 | 15430 | VALENCI2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154313 | lsdt9 | 15431 | VALENCI3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154324 | lsdt9 | 15432 | VALENCI4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154331 | lsdt9 | 15433 | WESTWOO1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154353 | lsdt9 | 15435 | WESTWOO3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154364 | lsdt9 | 15436 | WESTWOO4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154372 | lsdt9 | 15437 | PRINGLE_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154373 | lsdt9 | 15437 | PRINGLE_S | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154374 | lsdt9 | 15437 | PRINGLE_S | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154412 | lsdt9 | 15441 | CHAPARRA | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154413 | lsdt9 | 15441 | CHAPARRA | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154461 | lsdt9 | 15446 | BEELINE1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154472 | lsdt9 | 15447 | BEELINE2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154483 | lsdt9 | 15448 | BEELINE3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154531 | lsdt9 | 15453 | INDIANB1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154542 | lsdt9 | 15454 | INDIANB2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154553 | lsdt9 | 15455 | INDIANB3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15457I | lsdt9 | 15457 | PICO | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154582 | lsdt9 | 15458 | PIMASRP2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154593 | lsdt9 | 15459 | PIMASRP3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154612 | lsdt9 | 15461 | STADIUM | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154613 | lsdt9 | 15461 | STADIUM | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154624 | lsdt9 | 15462 | TOVREA | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154702 | lsdt9 | 15470 | ARCADIA2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154713 | lsdt9 | 15471 | ARCADIA3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154722 | lsdt9 | 15472 | ARIZONA2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154733 | lsdt9 | 15473 | ARIZONA3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154741 | lsdt9 | 15474 | CEDRSTR1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154772 | lsdt9 | 15477 | FALLS | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154773 | lsdt9 | 15477 | FALLS | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154774 | lsdt9 | 15477 | FALLS | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154792 | lsdt9 | 15479 | INGLESI2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154803 | lsdt9 | 15480 | INGLESI3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154811 | lsdt9 | 15481 | MADISON | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154813 | lsdt9 | 15481 | MADISON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154832 | lsdt9 | 15483 | OSBORN 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154843 | lsdt9 | 15484 | OSBORN 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154862 | lsdt9 | 15486 | PERA | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154872 | lsdt9 | 15487 | SCOTTSDA | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154873 | lsdt9 | 15487 | SCOTTSDA | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154881 | lsdt9 | 15488 | SPARTAN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154882 | lsdt9 | 15488 | SPARTAN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154883 | lsdt9 | 15488 | SPARTAN | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154892 | lsdt9 | 15489 | YAZZIE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154893 | lsdt9 | 15489 | YAZZIE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154902 | lsdt9 | 15490 | TAVAN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154903 | lsdt9 | 15490 | TAVAN | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154961 | lsdt9 | 15496 | ALAMEDA1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154972 | lsdt9 | 15497 | ALAMEDA2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154983 | lsdt9 | 15498 | ALAMEDA3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154994 | lsdt9 | 15499 | ALAMEDA4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155011 | lsdt9 | 15501 | DOBSON 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155022 | lsdt9 | 15502 | DOBSON 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155033 | lsdt9 | 15503 | DOBSON 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155052 | lsdt9 | 15505 | HOKAM | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155053 | lsdt9 | 15505 | HOKAM | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155054 | lsdt9 | 15505 | HOKAM | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155055 | lsdt9 | 15505 | HOKAM | 69 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155061 | lsdt9 | 15506 | MICRO 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155092 | lsdt9 | 15509 | PICKREL2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155102 | lsdt9 | 15510 | TEMPESRP | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155103 | lsdt9 | 15510 | TEMPESRP | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155111 | lsdt9 | 15511 | UNIVERSI | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155112 | lsdt9 | 15511 | UNIVERSI | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155151 | lsdt9 | 15515 | PENDERGS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155152 | lsdt9 | 15515 | PENDERGS | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155211 | lsdt9 | 15521 | BROOKS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155212 | lsdt9 | 15521 | BROOKS | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155222 | lsdt9 | 15522 | CARTWRI2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155233 | lsdt9 | 15523 | CARTWRI3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155244 | lsdt9 | 15524 | CARTWRI4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155252 | lsdt9 | 15525 | CHRISTY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155253 | lsdt9 | 15525 | CHRISTY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155261 | lsdt9 | 15526 | EVANS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155262 | lsdt9 | 15526 | EVANS | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155272 | lsdt9 | 15527 | ISAAC | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155273 | lsdt9 | 15527 | ISAAC | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155274 | lsdt9 | 15527 | ISAAC | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155282 | lsdt9 | 15528 | KAY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155283 | lsdt9 | 15528 | KAY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155291 | lsdt9 | 15529 | SHAW | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155292 | lsdt9 | 15529 | SHAW | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155311 | lsdt9 | 15531 | SHEELY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155312 | lsdt9 | 15531 | SHEELY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155313 | lsdt9 | 15531 | SHEELY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155323 | lsdt9 | 15532 | SOUTHRN4 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155324 | lsdt9 | 15532 | SOUTHRN4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15534I | lsdt9 | 15534 | TRESRIOS | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155362 | lsdt9 | 15536 | CHEATHAM | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155372 | lsdt9 | 15537 | COWDEN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155383 | lsdt9 | 15538 | BURTON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155392 | lsdt9 | 15539 | HANSON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155424 | lsdt9 | 15542 | CASHION4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155435 | lsdt9 | 15543 | CASHION5 | 69 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155442 | lsdt9 | 15544 | COLLIER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155443 | lsdt9 | 15544 | COLLIER | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155451 | lsdt9 | 15545 | CONOVALO | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155452 | lsdt9 | 15545 | CONOVALO | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155472 | lsdt9 | 15547 | GRASMOE2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155483 | lsdt9 | 15548 | GRASMOE3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155491 | lsdt9 | 15549 | STOKER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155492 | lsdt9 | 15549 | STOKER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155502 | lsdt9 | 15550 | SUNSET 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155513 | lsdt9 | 15551 | SUNSET 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155531 | lsdt9 | 15553 | TOLBY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155532 | lsdt9 | 15553 | TOLBY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155543 | lsdt9 | 15554 | WELBORN3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155552 | lsdt9 | 15555 | WELBORN2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155601 | lsdt9 | 15560 | ROVEY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155602 | lsdt9 | 15560 | ROVEY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155643 | lsdt9 | 15564 | BASELIN3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155654 | lsdt9 | 15565 | BASELIN4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155660 | lsdt9 | 15566 | CITRUS 0 | 69 | 0 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155672 | lsdt9 | 15567 | CITRUS 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155701 | lsdt9 | 15570 | COOPER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155702 | lsdt9 | 15570 | COOPER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155712 | lsdt9 | 15571 | GERMANN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15571I | lsdt9 | 15571 | GERMANN | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155721 | lsdt9 | 15572 | MOODY 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155732 | lsdt9 | 15573 | MOODY 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155762 | lsdt9 | 15576 | HUNT | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155763 | lsdt9 | 15576 | HUNT | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155771 | lsdt9 | 15577 | KEMPTON1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155782 | lsdt9 | 15578 | KEMPTON2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155793 | lsdt9 | 15579 | KEMPTON3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155811 | lsdt9 | 15581 | LACY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155812 | lsdt9 | 15581 | LACY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155822 | lsdt9 | 15582 | NEELY_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155823 | lsdt9 | 15582 | NEELY_S | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155831 | lsdt9 | 15583 | QUAIL 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155842 | lsdt9 | 15584 | QUAIL 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155873 | lsdt9 | 15587 | QUEENCRE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155874 | lsdt9 | 15587 | QUEENCRE | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155893 | lsdt9 | 15589 | RITTENHO | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155894 | lsdt9 | 15589 | RITTENHO | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155903 | lsdt9 | 15590 | WORTMAN | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155911 | lsdt9 | 15591 | SHULTZ 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155922 | lsdt9 | 15592 | SHULTZ 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155952 | lsdt9 | 15595 | TENNEY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155953 | lsdt9 | 15595 | TENNEY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155961 | lsdt9 | 15596 | WILLIAMS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155962 | lsdt9 | 15596 | WILLIAMS | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156151 | lsdt9 | 15615 | WARD | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156152 | lsdt9 | 15615 | WARD | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156192 | lsdt9 | 15619 | OWENS 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156201 | lsdt9 | 15620 | CASEY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156202 | lsdt9 | 15620 | CASEY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156212 | lsdt9 | 15621 | FREESTON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156213 | lsdt9 | 15621 | FREESTON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156232 | lsdt9 | 15623 | ZIMMERMN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156272 | lsdt9 | 15627 | AMOS | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156283 | lsdt9 | 15628 | MCPHERSO | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156302 | lsdt9 | 15630 | WATKINS | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156331 | lsdt9 | 15633 | GREER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156332 | lsdt9 | 15633 | GREER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156341 | lsdt9 | 15634 | POTTER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156342 | lsdt9 | 15634 | POTTER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156352 | lsdt9 | 15635 | COOLEY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156353 | lsdt9 | 15635 | COOLEY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156361 | lsdt9 | 15636 | BOGLE | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156362 | lsdt9 | 15636 | BOGLE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156372 | lsdt9 | 15637 | WALKER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156382 | lsdt9 | 15638 | MORCOM | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156383 | lsdt9 | 15638 | MORCOM | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156392 | lsdt9 | 15639 | HUMPHREY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156393 | lsdt9 | 15639 | HUMPHREY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156402 | lsdt9 | 15640 | PERALES | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156423 | lsdt9 | 15642 | TWEEDY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15644I | lsdt9 | 15644 | DELTA 3 | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15646I | lsdt9 | 15646 | DELTA 5 | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156471 | lsdt9 | 15647 | JONES | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156472 | lsdt9 | 15647 | JONES | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156473 | lsdt9 | 15647 | JONES | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156481 | lsdt9 | 15648 | ROTH | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156482 | lsdt9 | 15648 | ROTH | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156483 | lsdt9 | 15648 | ROTH | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156502 | lsdt9 | 15650 | SANCARL2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156513 | lsdt9 | 15651 | SANCARL3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15653I | lsdt9 | 15653 | LUNA | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156542 | lsdt9 | 15654 | SUNLAKES | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156543 | lsdt9 | 15654 | SUNLAKES | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15655I | lsdt9 | 15655 | SYNERGY | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156563 | lsdt9 | 15656 | WILLIS | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15657I | lsdt9 | 15657 | HOOPES | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156582 | lsdt9 | 15658 | PACE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156583 | lsdt9 | 15658 | PACE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15660I | lsdt9 | 15660 | CENTENNI | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15661I | lsdt9 | 15661 | AMERICA | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156651 | lsdt9 | 15665 | AIRPARK | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156662 | lsdt9 | 15666 | CORBELL | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156663 | lsdt9 | 15666 | CORBELL | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156664 | lsdt9 | 15666 | CORBELL | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156691 | lsdt9 | 15669 | GRISWOLD | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156692 | lsdt9 | 15669 | GRISWOLD | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156693 | lsdt9 | 15669 | GRISWOLD | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156701 | lsdt9 | 15670 | HANGER 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156712 | lsdt9 | 15671 | HANGER 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156723 | lsdt9 | 15672 | HANGER 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156741 | lsdt9 | 15674 | HOUSTON | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156742 | lsdt9 | 15674 | HOUSTON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15675I | lsdt9 | 15675 | LINOX | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156762 | lsdt9 | 15676 | MANOR | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156763 | lsdt9 | 15676 | MANOR | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156771 | lsdt9 | 15677 | MEMORY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156781 | lsdt9 | 15678 | MILLER 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156792 | lsdt9 | 15679 | MILLER 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15682I | lsdt9 | 15682 | WAFER | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156842 | lsdt9 | 15684 | AUSTIN_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156843 | lsdt9 | 15684 | AUSTIN_S | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156862 | lsdt9 | 15686 | CEDRSTR2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156872 | lsdt9 | 15687 | GAUCHO 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156883 | lsdt9 | 15688 | GAUCHO 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156892 | lsdt9 | 15689 | EVERGRE2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156923 | lsdt9 | 15692 | EVERGRE3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156932 | lsdt9 | 15693 | FOUNTAIN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156943 | lsdt9 | 15694 | GLENBROO | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156962 | lsdt9 | 15696 | VERDESRP | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156971 | lsdt9 | 15697 | WHEELER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156972 | lsdt9 | 15697 | WHEELER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157004 | lsdt9 | 15700 | GAUCHO 4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157061 | lsdt9 | 15706 | BASSHAM | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157062 | lsdt9 | 15706 | BASSHAM | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157071 | lsdt9 | 15707 | BUCKHORN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157072 | lsdt9 | 15707 | BUCKHORN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157123 | lsdt9 | 15712 | FALCON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15712I | lsdt9 | 15712 | FALCON | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157131 | lsdt9 | 15713 | LEISURE1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157142 | lsdt9 | 15714 | LEISURE2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157172 | lsdt9 | 15717 | TRYON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157173 | lsdt9 | 15717 | TRYON | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157192 | lsdt9 | 15719 | VENTURE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157193 | lsdt9 | 15719 | VENTURE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157201 | lsdt9 | 15720 | APACHE | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157202 | lsdt9 | 15720 | APACHE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157211 | lsdt9 | 15721 | BOONE_S | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157212 | lsdt9 | 15721 | BOONE_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157243 | lsdt9 | 15724 | PICKREL3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157244 | lsdt9 | 15724 | PICKREL3 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157271 | lsdt9 | 15727 | CULBERTS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157281 | lsdt9 | 15728 | FAIRWAY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157282 | lsdt9 | 15728 | FAIRWAY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157283 | lsdt9 | 15728 | FAIRWAY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157292 | lsdt9 | 15729 | LEHI 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157303 | lsdt9 | 15730 | LEHI 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157332 | lsdt9 | 15733 | REED 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157343 | lsdt9 | 15734 | REED 3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157351 | lsdt9 | 15735 | RICE | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157352 | lsdt9 | 15735 | RICE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157353 | lsdt9 | 15735 | RICE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157381 | lsdt9 | 15738 | STAPLEY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157382 | lsdt9 | 15738 | STAPLEY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157383 | lsdt9 | 15738 | STAPLEY | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15740I | lsdt9 | 15740 | VALVIST2 | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157422 | lsdt9 | 15742 | HUGHES_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157441 | lsdt9 | 15744 | WOOD 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157452 | lsdt9 | 15745 | WOOD 2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157482 | lsdt9 | 15748 | KIRK_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157491 | lsdt9 | 15749 | CLUFF | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157502 | lsdt9 | 15750 | EALY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157504 | lsdt9 | 15750 | EALY | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157512 | lsdt9 | 15751 | NOACK | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157531 | lsdt9 | 15753 | SEATON | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157532 | lsdt9 | 15753 | SEATON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157542 | lsdt9 | 15754 | SHANNON | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157572 | lsdt9 | 15757 | SUPERST2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157583 | lsdt9 | 15758 | SUPERST3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157602 | lsdt9 | 15760 | CAMERON_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157612 | lsdt9 | 15761 | MCCOY | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157622 | lsdt9 | 15762 | GLENBRO2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157673 | lsdt9 | 15767 | SGNLBUT3 | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157684 | lsdt9 | 15768 | SGNLBUT4 | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157702 | lsdt9 | 15770 | SAGE_S | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157703 | lsdt9 | 15770 | SAGE_S | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157704 | lsdt9 | 15770 | SAGE_S | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157821 | lsdt9 | 15782 | FINLEY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158462 | lsdt9 | 15846 | EGAN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158463 | lsdt9 | 15846 | EGAN | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158682 | lsdt9 | 15868 | RIOVERDE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158692 | lsdt9 | 15869 | PINKERTO | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15871I | lsdt9 | 15871 | TRIGAS | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158722 | lsdt9 | 15872 | WEBBER | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158723 | lsdt9 | 15872 | WEBBER | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158752 | lsdt9 | 15875 | ROHRIG | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158762 | lsdt9 | 15876 | CLARK | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158763 | lsdt9 | 15876 | CLARK | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158772 | lsdt9 | 15877 | SEARGANT | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158773 | lsdt9 | 15877 | SEARGANT | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158782 | lsdt9 | 15878 | MCREYNO2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15893I | lsdt9 | 15893 | HOWARD | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15976I | lsdt9 | 15976 | MCGINNIS | 69 | I | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17000AE | lsdt9 | 17000 | APACHE-AE | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.2 | 0.083 | 0.108 | 58.7 | 0.2 | 0.083 | 0.116 | 58.5 | 0.2 | 0.083 | 0.198 | 58.3 | 0.2 | 0.083 | 0.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17009AE | lsdt9 | 17009 | GREEN-AE | 230 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17019AE | lsdt9 | 17019 | RIVIERA | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.2 | 0.083 | 0.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17038AE | lsdt9 | 17038 | KARTCHNR | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.115 | 59.5 | 30 | 0.083 | 0.062 | 58.9 | 0.2 | 0.083 | 0.067 | 58.7 | 0.2 | 0.083 | 0.057 | 58.3 | 0.2 | 0.083 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17045AE | lsdt9 | 17045 | HACKBERY | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.2 | 0.083 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17049AE | lsdt9 | 17049 | REDTAIL | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.081 | 59.3 | 15 | 0.083 | 0.221 | 58.5 | 0.2 | 0.083 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17052AE | lsdt9 | 17052 | SAN_RAF | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.019 | 59.5 | 60 | 0.083 | 0.093 | 58.7 | 0.2 | 0.083 | 0.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17103AE | lsdt9 | 17103 | TOPOCK | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17104AE | lsdt9 | 17104 | THRNYDLE | 47.2 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.2 | 0.083 | 0.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17300AE | lsdt9 | 17300 | LONGTIN | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.22 | 58.7 | 0.2 | 0.083 | 0.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17430AE | lsdt9 | 17430 | DAVIS-AE | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17541AE | lsdt9 | 17541 | SCHIEFFELIN | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.109 | 58.9 | 0.2 | 0.083 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17600AE | lsdt9 | 17600 | AVRA | 24.9 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.083 | 0.098 | 58.7 | 0.2 | 0.083 | 0.233 | 58.3 | 0.2 | 0.083 | 0.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17601AE | lsdt9 | 17601 | GREENVLY | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.137 | 59.3 | 15 | 0.083 | 0.082 | 58.7 | 0.2 | 0.083 | 0.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17602AE | lsdt9 | 17602 | MARANA | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.2 | 0.083 | 0.336 | 58.3 | 0.2 | 0.083 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17604AE | lsdt9 | 17604 | THREEPNT | 24.9 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.26 | 58.5 | 0.2 | 0.083 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17605AE | lsdt9 | 17605 | VALEN-AE | 24.9 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.128 | 59.5 | 60 | 0.083 | 0.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17607AE | lsdt9 | 17607 | SAHUARIT | 24.9 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.221 | 58.9 | 0.2 | 0.083 | 0.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17610AE | lsdt9 | 17610 | S.BRKRCH | 24.9 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.083 | 0.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17611AE | lsdt9 | 17611 | BICKNELL | 24.9 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.083 | 0.288 | 58.3 | 0.2 | 0.083 | 0.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17620AE | lsdt9 | 17620 | ORACLE-AE | 115 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.2 | 0.083 | 0.245 | 58.3 | 0.2 | 0.083 | 0.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180271 | lsdt9 | 18027 | TORTISE | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181011 | lsdt9 | 18101 | REGENA | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181861 | lsdt9 | 18186 | NLV | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181863 | lsdt9 | 18186 | NLV | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181864 | lsdt9 | 18186 | NLV | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183871 | lsdt9 | 18387 | PECOS7 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183921 | lsdt9 | 18392 | SPARTA3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186271 | lsdt9 | 18627 | SPEEDWY1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19044WA | lsdt9 | 19044 | COOLIDGE | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19048WA | lsdt9 | 19048 | EMPIRE | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19050WA | lsdt9 | 19050 | GILA | 161 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19051WA | lsdt9 | 19051 | KNOB | 161 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19057WA | lsdt9 | 19057 | ORACLE | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19063WA | lsdt9 | 19063 | WLTMOHK | 161 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.066666 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19065WA | lsdt9 | 19065 | ED-2 | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19067WA | lsdt9 | 19067 | ED-5 | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19071WA | lsdt9 | 19071 | ED-4 | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19102WA | lsdt9 | 19102 | KOFA | 69 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19109WA | lsdt9 | 19109 | Davis | 69 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19222WA | lsdt9 | 19222 | CASAGRND | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19226WA | lsdt9 | 19226 | LONE BUT | 69 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19231WA | lsdt9 | 19231 | WF_EQLD1 | 34.5 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19233WA | lsdt9 | 19233 | WF_EQLD2 | 34.5 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19304WA | lsdt9 | 19304 | HEADGATE | 69 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19607WA | lsdt9 | 19607 | MARICOPA | 69 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.2 | 0.083 | 0.059 | 58.7 | 0.2 | 0.083 | 0.26 | 58.5 | 0.2 | 0.083 | 0.024 | 58.3 | 0.2 | 0.083 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19608WA | lsdt9 | 19608 | SANTARED3 | 69 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.11 | 58.9 | 0.2 | 0.083 | 0.063 | 58.5 | 0.2 | 0.083 | 0.098 | 58.3 | 0.2 | 0.083 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19782WA | lsdt9 | 19782 | GLENCANY | 230 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.066666 | 0.47 | 58.9 | 0.1 | 0.066666 | 0.18 | 58.5 | 0.1 | 0.06666 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19784WA | lsdt9 | 19784 | KAYENTA | 230 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19787WA | lsdt9 | 19787 | LNGHOUSE | 230 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200161 | lsdt9 | 20016 | RIN-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200162 | lsdt9 | 20016 | RIN-161 | 161 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200241 | lsdt9 | 20024 | CNA-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.2 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200242 | lsdt9 | 20024 | CNA-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.2 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200261 | lsdt9 | 20026 | GER-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200262 | lsdt9 | 20026 | GER-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200281 | lsdt9 | 20028 | MXC-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200282 | lsdt9 | 20028 | MXC-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200291 | lsdt9 | 20029 | RII-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.08333 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200301 | lsdt9 | 20030 | UND-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.2 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200302 | lsdt9 | 20030 | UND-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200311 | lsdt9 | 20031 | HMO-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.08333 | 0.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200312 | lsdt9 | 20031 | HMO-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.08333 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200321 | lsdt9 | 20032 | INA-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200351 | lsdt9 | 20035 | LGO-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200362 | lsdt9 | 20036 | LMS-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.08333 | 0.2171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200391 | lsdt9 | 20039 | MEP-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200392 | lsdt9 | 20039 | MEP-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200411 | lsdt9 | 20041 | TEE-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200421 | lsdt9 | 20042 | DRA-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200442 | lsdt9 | 20044 | FTA-69 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.2 | 0.1 | 0.08333 | 0.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200621 | lsdt9 | 20062 | TCU-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.08333 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20069IN | lsdt9 | 20069 | CEC-115 | 115 | IN | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.03333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200701 | lsdt9 | 20070 | GLL-115 | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.08333 | 0.2539 | 58.5 | 0.1 | 0.08333 | 0.7461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200702 | lsdt9 | 20070 | GLL-115 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.03333 | 0.08333 | 0.37 | 58.5 | 0.1 | 0.08333 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200711 | lsdt9 | 20071 | EDA-115 | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.08333 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200712 | lsdt9 | 20071 | EDA-115 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.08333 | 0.199 | 58.5 | 0.1 | 0.08333 | 0.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20101IN | lsdt9 | 20101 | RUM-69 | 69 | IN | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201131 | lsdt9 | 20113 | OZA-230 | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 15 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201132 | lsdt9 | 20113 | OZA-230 | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 15 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20114IN | lsdt9 | 20114 | CSC-230 | 230 | IN | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.03333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201161 | lsdt9 | 20116 | CTY-230 | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201162 | lsdt9 | 20116 | CTY-230 | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20136FX | lsdt9 | 20136 | CPU-161 | 161 | FX | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201471 | lsdt9 | 20147 | CTY-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.08333 | 0.08333 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201481 | lsdt9 | 20148 | NZI-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201482 | lsdt9 | 20148 | NZI-161 | 161 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201501 | lsdt9 | 20150 | CRO-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.2 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201521 | lsdt9 | 20152 | MOE-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.08333 | 0.08333 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201531 | lsdt9 | 20153 | GOR-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.08333 | 0.08333 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201541 | lsdt9 | 20154 | SIS-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.08333 | 0.08333 | 0.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201581 | lsdt9 | 20158 | MXI-345 | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.08333 | 0.08333 | 0.7844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201791 | lsdt9 | 20179 | RZC-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201792 | lsdt9 | 20179 | RZC-161 | 161 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.08333 | 0.08333 | 0.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201801 | lsdt9 | 20180 | HGO-161 | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.03333 | 0.08333 | 0.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201802 | lsdt9 | 20180 | HGO-161 | 161 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.03333 | 0.08333 | 0.8616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202201 | lsdt9 | 20220 | PAF-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.1 | 0.08333 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202211 | lsdt9 | 20221 | SIO-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202241 | lsdt9 | 20224 | FCO-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.1 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202261 | lsdt9 | 20226 | XCO-230 | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202262 | lsdt9 | 20226 | XCO-230 | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202411 | lsdt9 | 20241 | PNM-115 | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 0.1 | 0.08333 | 0.9068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203911 | lsdt9 | 20391 | CHQ-230 | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.2 | 0.08333 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203912 | lsdt9 | 20391 | CHQ-230 | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0 | 0.08333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20512IN | lsdt9 | 20512 | MOE-34.5 | 34.5 | IN | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.08333 | 0.1875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212811 | lsdt9 | 21281 | AVE58 | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.067 | 0.43 | 58.7 | 0.1 | 0.067 | 0.15 | 58.5 | 0.1 | 0.067 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212851 | lsdt9 | 21285 | JEFFERSON | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.24 | 58.5 | 0.1 | 0.067 | 0.06 | 58.3 | 0.1 | 0.067 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212861 | lsdt9 | 21286 | LAQUINTA | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.13 | 58.7 | 0.1 | 0.067 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212891 | lsdt9 | 21289 | N.VIEW | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.067 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212911 | lsdt9 | 21291 | AVE48 | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.067 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212921 | lsdt9 | 21292 | NRTH_LQUINTA | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213021 | lsdt9 | 21302 | CARREON | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 0.07 | 58.9 | 0.1 | 0.067 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213091 | lsdt9 | 21309 | AVE42 | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.39 | 58.9 | 0.1 | 0.067 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213101 | lsdt9 | 21310 | FRANWAY | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213121 | lsdt9 | 21312 | COACHELLASW | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213161 | lsdt9 | 21316 | SHIELDS | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.13 | 58.9 | 0.1 | 0.067 | 0.14 | 58.7 | 0.1 | 0.067 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213241 | lsdt9 | 21324 | USGYPS | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.067 | 0.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213301 | lsdt9 | 21330 | EDOM | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.13 | 58.7 | 0.1 | 0.067 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213361 | lsdt9 | 21336 | MALL | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.11 | 58.9 | 0.1 | 0.067 | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213371 | lsdt9 | 21337 | TERMINAL | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 0.25 | 58.7 | 0.1 | 0.067 | 0.08 | 58.3 | 0.1 | 0.067 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213391 | lsdt9 | 21339 | EUCLID | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.13 | 58.5 | 0.1 | 0.067 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213431 | lsdt9 | 21343 | HEBER | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.067 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213451 | lsdt9 | 21345 | HOLTVILLE | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213481 | lsdt9 | 21348 | CLARK | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.067 | 0.24 | 58.5 | 0.1 | 0.067 | 0.39 | 58.3 | 0.1 | 0.067 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213491 | lsdt9 | 21349 | NEW_JACKSON | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 0.05 | 58.9 | 0.1 | 0.067 | 0.24 | 58.5 | 0.1 | 0.067 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213541 | lsdt9 | 21354 | MARSHALL | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.06 | 58.7 | 0.1 | 0.067 | 0.17 | 58.3 | 0.1 | 0.067 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213551 | lsdt9 | 21355 | NEW_MECCA | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.02 | 58.7 | 0.1 | 0.067 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213571 | lsdt9 | 21357 | MONROE | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.19 | 58.5 | 0.1 | 0.067 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213581 | lsdt9 | 21358 | AVE52 | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213601 | lsdt9 | 21360 | BRAVO92 | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.067 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213661 | lsdt9 | 21366 | PERRY | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.09 | 58.5 | 0.1 | 0.067 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213891 | lsdt9 | 21389 | VANBUREN | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.067 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213971 | lsdt9 | 21397 | CLX92 | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.067 | 0.11 | 58.7 | 0.1 | 0.067 | 0.24 | 58.3 | 0.1 | 0.067 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214061 | lsdt9 | 21406 | SHAHILLS | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.3 | 58.3 | 0.1 | 0.067 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216971 | lsdt9 | 21697 | CALIPAT | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.067 | 0.1 | 58.3 | 0.1 | 0.067 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217401 | lsdt9 | 21740 | PARKVIEW | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.067 | 0.08 | 58.5 | 0.1 | 0.067 | 0.11 | 58.3 | 0.1 | 0.067 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219411 | lsdt9 | 21941 | PANNO | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.067 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219471 | lsdt9 | 21947 | ATEN | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.067 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219481 | lsdt9 | 21948 | PRUETT | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219501 | lsdt9 | 21950 | NEW_IMPERIAL | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.067 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219751 | lsdt9 | 21975 | DAHLIA | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 0.24 | 58.5 | 0.1 | 0.067 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219761 | lsdt9 | 21976 | CENTRAL | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.067 | 0.19 | 58.7 | 0.1 | 0.067 | 0.09 | 58.5 | 0.1 | 0.067 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219781 | lsdt9 | 21978 | BEEFPLANT | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219801 | lsdt9 | 21980 | BRAW92 | 92 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 0.09 | 58.3 | 0.1 | 0.067 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2200810 | lsdt9 | 22008 | ASH | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2204810 | lsdt9 | 22048 | BATIQTOS | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2205610 | lsdt9 | 22056 | BERNARDO | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2210810 | lsdt9 | 22108 | CANNON | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2212410 | lsdt9 | 22124 | CHCARITA | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2213210 | lsdt9 | 22132 | CHOLLAS | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2213610 | lsdt9 | 22136 | CLAIRMNT | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2215210 | lsdt9 | 22152 | CREELMAN | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2221610 | lsdt9 | 22216 | ELLIOTT | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2225210 | lsdt9 | 22252 | ENCNITAS | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2227210 | lsdt9 | 22272 | ESCO | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2227610 | lsdt9 | 22276 | F | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2228810 | lsdt9 | 22288 | FELICITA | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2230010 | lsdt9 | 22300 | FRIARS | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2231610 | lsdt9 | 22316 | GENESEE | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2233610 | lsdt9 | 22336 | GRANITE | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2236410 | lsdt9 | 22364 | JAMACHA | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2237210 | lsdt9 | 22372 | KEARNY | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2239610 | lsdt9 | 22396 | LAGNA NL | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2243210 | lsdt9 | 22432 | MARGARTA | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2244010 | lsdt9 | 22440 | MELROSE | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2244410 | lsdt9 | 22444 | MESA RIM | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2244810 | lsdt9 | 22448 | MESAHGTS | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2251210 | lsdt9 | 22512 | MONSRATE | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2253210 | lsdt9 | 22532 | MURRAY | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2258110 | lsdt9 | 22581 | NORTHCTY | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2259210 | lsdt9 | 22592 | OLD TOWN | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2262010 | lsdt9 | 22620 | PACFCBCH | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2263210 | lsdt9 | 22632 | PALOMAR | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2263610 | lsdt9 | 22636 | PARADISE | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2265610 | lsdt9 | 22656 | PICO | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2266410 | lsdt9 | 22664 | POMERADO | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2267210 | lsdt9 | 22672 | PRCTRVLY | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2267610 | lsdt9 | 22676 | R.CARMEL | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2269610 | lsdt9 | 22696 | ROSE CYN | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2269810 | lsdt9 | 22698 | SALT CREEK | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2270410 | lsdt9 | 22704 | SAMPSON | 12.5 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2270810 | lsdt9 | 22708 | SANLUSRY | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2272010 | lsdt9 | 22720 | SANMATEO | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2272410 | lsdt9 | 22724 | SANMRCOS | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2273410 | lsdt9 | 22734 | SANTEE | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2274010 | lsdt9 | 22740 | SANYSDRO | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2276010 | lsdt9 | 22760 | SHADOWR | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2279610 | lsdt9 | 22796 | SPRNGVLY | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2282010 | lsdt9 | 22820 | SWEETWTR | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2285210 | lsdt9 | 22852 | TELECYN | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2285610 | lsdt9 | 22856 | TOREYPNS | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2286010 | lsdt9 | 22860 | TRABUCO | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2286510 | lsdt9 | 22865 | GRNT HLL | 138 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2286810 | lsdt9 | 22868 | URBAN | 69 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240241 | lsdt9 | 24024 | CHINO | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.492 | 57.7 | 0.1 | 0.1 | 0.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240281 | lsdt9 | 24028 | DELAMO | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.617 | 57.9 | 0.1 | 0.1 | 0.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240571 | lsdt9 | 24057 | GOLETA | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240751 | lsdt9 | 24075 | LAGUBELL | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 0.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240831 | lsdt9 | 24083 | LITEHIPE | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240981 | lsdt9 | 24098 | MOORPARK | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.394 | 57.7 | 0.1 | 0.1 | 0.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241111 | lsdt9 | 24111 | PADUA | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241331 | lsdt9 | 24133 | SANTIAGO | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241351 | lsdt9 | 24135 | SAUGUS | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241571 | lsdt9 | 24157 | WALNUT | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241601 | lsdt9 | 24160 | VALLEYSC | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241971 | lsdt9 | 24197 | ELLIS | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241991 | lsdt9 | 24199 | CHEVMAIN | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242011 | lsdt9 | 24201 | BARRE | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 0.329 | 57.9 | 0.1 | 0.1 | 0.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242031 | lsdt9 | 24203 | CENTER | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.289 | 57.9 | 0.1 | 0.1 | 0.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242061 | lsdt9 | 24206 | GOULD | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242071 | lsdt9 | 24207 | JOHANNA | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242081 | lsdt9 | 24208 | LCIENEGA | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242091 | lsdt9 | 24209 | MESA CAL | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242101 | lsdt9 | 24210 | MIRALOMW | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242111 | lsdt9 | 24211 | OLINDA | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242121 | lsdt9 | 24212 | RECTOR | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242131 | lsdt9 | 24213 | RIOHONDO | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242141 | lsdt9 | 24214 | SANBRDNO | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242161 | lsdt9 | 24216 | VILLA PK | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242291 | lsdt9 | 24229 | VALLEY-S | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244021 | lsdt9 | 24402 | ANTELOPE | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247221 | lsdt9 | 24722 | CONTROL | 55 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 55 | 0.2 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247861 | lsdt9 | 24786 | CSA DIAB | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.2 | 0.1 | 0.766 | 57 | 0.2 | 0.1 | 0.095 | 55 | 0.2 | 0.1 | 0.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248051 | lsdt9 | 24805 | DEVERS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248071 | lsdt9 | 24807 | MIRAGE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249021 | lsdt9 | 24902 | VSTA | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252021 | lsdt9 | 25202 | LWIS ANM | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.083 | 0.058 | 58.9 | 0.1 | 0.083 | 0.067 | 58.7 | 0.1 | 0.083 | 0.072 | 58.5 | 0.1 | 0.083 | 0.073 | 58.3 | 0.1 | 0.083 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256671 | lsdt9 | 25667 | EL CASCO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256821 | lsdt9 | 25682 | EDWARDS 33 | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256841 | lsdt9 | 25684 | INYOKERN 33 | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256891 | lsdt9 | 25689 | SOUTHBAS 33 | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26501B | lsdt9 | 26501 | STJ B F | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 57.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26503D | lsdt9 | 26503 | STJ D F | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26505B | lsdt9 | 26505 | CEN B F | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26506C | lsdt9 | 26506 | CEN C F | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26507D | lsdt9 | 26507 | CEN D F | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26514C | lsdt9 | 26514 | WIL C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 57.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26518A | lsdt9 | 26518 | FAR A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26519B | lsdt9 | 26519 | FAR C M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26520C | lsdt9 | 26520 | FAR C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26521D | lsdt9 | 26521 | FAR D M | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26528A | lsdt9 | 26528 | TOL A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26530C | lsdt9 | 26530 | TOL C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26531D | lsdt9 | 26531 | TOL D M | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26534A | lsdt9 | 26534 | VEL A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26535B | lsdt9 | 26535 | VEL B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26536C | lsdt9 | 26536 | VEL C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26541B | lsdt9 | 26541 | ATW B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26542C | lsdt9 | 26542 | ATW C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26543D | lsdt9 | 26543 | ATW D M | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26547A | lsdt9 | 26547 | NR A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26548B | lsdt9 | 26548 | NR B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26549C | lsdt9 | 26549 | NR C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26550D | lsdt9 | 26550 | NR D M | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26551A | lsdt9 | 26551 | OLY A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26552B | lsdt9 | 26552 | OLY B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26553C | lsdt9 | 26553 | OLY C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26554D | lsdt9 | 26554 | OLY D M | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26557B | lsdt9 | 26557 | VAL B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26561C | lsdt9 | 26561 | AIR C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 57.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26562A | lsdt9 | 26562 | MKT A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 57.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26563B | lsdt9 | 26563 | MKT B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 57.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26564C | lsdt9 | 26564 | MKT C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 57.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26565D | lsdt9 | 26565 | MKT D M | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 57.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26566A | lsdt9 | 26566 | HAR A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 57.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26567B | lsdt9 | 26567 | HAR B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 57.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26568C | lsdt9 | 26568 | HAR A M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 57.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26569A | lsdt9 | 26569 | VN A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26570B | lsdt9 | 26570 | VN B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26571C | lsdt9 | 26571 | VN C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26572A | lsdt9 | 26572 | CAN A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26573B | lsdt9 | 26573 | CAN B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26574C | lsdt9 | 26574 | CAN C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26575A | lsdt9 | 26575 | TAR A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26576B | lsdt9 | 26576 | TAR B M | 34.5 | B | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26577C | lsdt9 | 26577 | TAR C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26578A | lsdt9 | 26578 | RIN A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26580C | lsdt9 | 26580 | RIN C M | 34.5 | C | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26581A | lsdt9 | 26581 | HAL A M | 34.5 | A | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26586D | lsdt9 | 26586 | VN D M | 34.5 | D | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272401 | lsdt9 | 27240 | Winona | 35.26 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.1 | 0.08 | 0.094294 | 58.9 | 0.1 | 0.08 | 0.1814 | 58.7 | 0.1 | 0.08 | 0 | 58.5 | 0.1 | 0.08 | 0.34234 | 58.3 | 0.1 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272411 | lsdt9 | 27241 | Golden State | 70.9 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.1 | 0.08 | 0 | 58.9 | 0.1 | 0.08 | 0 | 58.7 | 0.1 | 0.08 | 0 | 58.5 | 0.1 | 0.08 | 0 | 58.3 | 0.1 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272431 | lsdt9 | 27243 | Clybourn | 35.39 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.1 | 0.08 | 0 | 58.9 | 0.1 | 0.08 | 0 | 58.7 | 0.1 | 0.08 | 0.095471 | 58.5 | 0.1 | 0.08 | 0.22491 | 58.3 | 0.1 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272431 | lsdt9 | 27243 | Victory | 35.39 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.1 | 0.08 | 0 | 58.9 | 0.1 | 0.08 | 0.084441 | 58.7 | 0.1 | 0.08 | 0.21841 | 58.5 | 0.1 | 0.08 | 0.069903 | 58.3 | 0.1 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272631 | lsdt9 | 27263 | Burbank | 12.71 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.1 | 0.08 | 0 | 58.9 | 0.1 | 0.08 | 0 | 58.7 | 0.1 | 0.08 | 0 | 58.5 | 0.1 | 0.08 | 0 | 58.3 | 0.1 | 0.08 | 0.48343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273221 | lsdt9 | 27322 | Glorietta | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.4 | 29.85 | 0.08 | 0.028 | 59.3 | 14.85 | 0.08 | 0.027 | 59.1 | 0.15 | 0.08 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273261 | lsdt9 | 27326 | Columbus | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.08 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273301 | lsdt9 | 27330 | Tropico | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 59.85 | 0.08 | 0.012 | 59.1 | 0.15 | 0.08 | 0.016935 | 58.7 | 0.15 | 0.08 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273321 | lsdt9 | 27332 | Montrose | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.15 | 0.08 | 0.017 | 58.5 | 0.15 | 0.08 | 0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301111 | lsdt9 | 30111 | LOGAN CR | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.34 | 58.3 | 0.1 | 0.1 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304305 | lsdt9 | 30430 | FULTON | 230 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304671 | lsdt9 | 30467 | PARKWAY | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3052310 | lsdt9 | 30523 | CC SUB | 230 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305239 | lsdt9 | 30523 | CC SUB | 230 | 9 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305371 | lsdt9 | 30537 | NDUBLIN | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.45 | 58.9 | 0.1 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305451 | lsdt9 | 30545 | ROSSMOOR | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305452 | lsdt9 | 30545 | ROSSMOOR | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.29 | 58.3 | 0.1 | 0.1 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305541 | lsdt9 | 30554 | CASTROVL | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305542 | lsdt9 | 30554 | CASTROVL | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305553 | lsdt9 | 30555 | SANRAMON | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305554 | lsdt9 | 30555 | SANRAMON | 230 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.27 | 58.5 | 0.1 | 0.1 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305555 | lsdt9 | 30555 | SANRAMON | 230 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305556 | lsdt9 | 30555 | SANRAMON | 230 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305612 | lsdt9 | 30561 | TASSAJAR | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305651 | lsdt9 | 30565 | BRENTWOD | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305652 | lsdt9 | 30565 | BRENTWOD | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305653 | lsdt9 | 30565 | BRENTWOD | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305851 | lsdt9 | 30585 | LS PSTAS | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305852 | lsdt9 | 30585 | LS PSTAS | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306222 | lsdt9 | 30622 | EIGHT MI | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.48 | 58.9 | 0.1 | 0.1 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306223 | lsdt9 | 30622 | EIGHT MI | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306851 | lsdt9 | 30685 | EMBRCDRD | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.47 | 58.3 | 0.1 | 0.1 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306852 | lsdt9 | 30685 | EMBRCDRD | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307201 | lsdt9 | 30720 | SARATOGA | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307202 | lsdt9 | 30720 | SARATOGA | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307203 | lsdt9 | 30720 | SARATOGA | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307301 | lsdt9 | 30730 | HICKS | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307302 | lsdt9 | 30730 | HICKS | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307303 | lsdt9 | 30730 | HICKS | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307903 | lsdt9 | 30790 | PANOCHE | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307952 | lsdt9 | 30795 | STOREY 2 | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308251 | lsdt9 | 30825 | MCMULLN1 | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308411 | lsdt9 | 30841 | FIGRDN 1 | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.5 | 58.7 | 0.1 | 0.1 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308462 | lsdt9 | 30846 | FIGRDN 2 | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.43 | 58.7 | 0.1 | 0.1 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308463 | lsdt9 | 30846 | FIGRDN 2 | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308501 | lsdt9 | 30850 | ASHLAN | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308502 | lsdt9 | 30850 | ASHLAN | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308503 | lsdt9 | 30850 | ASHLAN | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309053 | lsdt9 | 30905 | TEMPLETN | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.46 | 58.7 | 0.1 | 0.1 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309304 | lsdt9 | 30930 | MESA PGE | 230 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309406 | lsdt9 | 30940 | STOCKDALED | 230 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309423 | lsdt9 | 30942 | STOCKDALEF | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309501 | lsdt9 | 30950 | BAKERSFIELDD | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309512 | lsdt9 | 30951 | BAKERSFIELDE | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309523 | lsdt9 | 30952 | BAKERSFIELDF | 230 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310501 | lsdt9 | 31050 | ORICK | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310581 | lsdt9 | 31058 | JANS CRK | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310582 | lsdt9 | 31058 | JANS CRK | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310621 | lsdt9 | 31062 | BLUE LKE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310961 | lsdt9 | 31096 | WILLWCRK | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.51 | 58.3 | 0.1 | 0.1 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311022 | lsdt9 | 31102 | NEWBURG | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311121 | lsdt9 | 31112 | FRUITLND | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312041 | lsdt9 | 31204 | UKIAH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.25 | 58.3 | 0.1 | 0.1 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312042 | lsdt9 | 31204 | UKIAH | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312081 | lsdt9 | 31208 | CLOVRDLE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.55 | 58.7 | 0.1 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312221 | lsdt9 | 31222 | REDBUD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312223 | lsdt9 | 31222 | REDBUD | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312381 | lsdt9 | 31238 | MONROE1 | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312392 | lsdt9 | 31239 | MONROE2 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312401 | lsdt9 | 31240 | SNTA RSA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312402 | lsdt9 | 31240 | SNTA RSA | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312403 | lsdt9 | 31240 | SNTA RSA | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312581 | lsdt9 | 31258 | SONOMA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312582 | lsdt9 | 31258 | SONOMA | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313061 | lsdt9 | 31306 | WILLITS | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313091 | lsdt9 | 31309 | FT_BRGD1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313112 | lsdt9 | 31311 | FT_BRGD2 | 12.47 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313341 | lsdt9 | 31334 | CLER LKE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313361 | lsdt9 | 31336 | HPLND JT | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313462 | lsdt9 | 31346 | GUALALA | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313682 | lsdt9 | 31368 | GYSRVLLE | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314541 | lsdt9 | 31454 | PANRAMA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314671 | lsdt9 | 31467 | JESSUP | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314802 | lsdt9 | 31480 | WYANDTTE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314961 | lsdt9 | 31496 | NORD 1 | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314962 | lsdt9 | 31496 | NORD 1 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314981 | lsdt9 | 31498 | SYCAMORE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314982 | lsdt9 | 31498 | SYCAMORE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314983 | lsdt9 | 31498 | SYCAMORE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315021 | lsdt9 | 31502 | CHICO B | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315022 | lsdt9 | 31502 | CHICO B | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315142 | lsdt9 | 31514 | PARADSE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315501 | lsdt9 | 31550 | MC ARTHR | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315741 | lsdt9 | 31574 | ANDERSON | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.32 | 58.3 | 0.1 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315922 | lsdt9 | 31592 | DESCHUTS | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316082 | lsdt9 | 31608 | RED BLFF | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316101 | lsdt9 | 31610 | TYLER | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31611PK | lsdt9 | 31611 | RBPPJCT | 60 | PK | [6 empty] | : | #9 | 0.05 | 0.05 | 59.6 | 0.33 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316262 | lsdt9 | 31626 | CORNING | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316402 | lsdt9 | 31640 | TRES VIS | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316841 | lsdt9 | 31684 | EST QNCY | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317102 | lsdt9 | 31710 | CHICO A | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317161 | lsdt9 | 31716 | ESQUON | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317241 | lsdt9 | 31724 | ORLAND B | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.45 | 58.7 | 0.1 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317381 | lsdt9 | 31738 | ANITA | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319701 | lsdt9 | 31970 | WOODLD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319702 | lsdt9 | 31970 | WOODLD | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319861 | lsdt9 | 31986 | W.SCRMNO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319862 | lsdt9 | 31986 | W.SCRMNO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319863 | lsdt9 | 31986 | W.SCRMNO | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319882 | lsdt9 | 31988 | DEEPWATR | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319901 | lsdt9 | 31990 | DAVIS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319902 | lsdt9 | 31990 | DAVIS | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319903 | lsdt9 | 31990 | DAVIS | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320501 | lsdt9 | 32050 | RICE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320502 | lsdt9 | 32050 | RICE | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320701 | lsdt9 | 32070 | CLSA JCT | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321001 | lsdt9 | 32100 | DIXONPGE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321002 | lsdt9 | 32100 | DIXONPGE | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.5 | 58.5 | 0.1 | 0.1 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322001 | lsdt9 | 32200 | PEASE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322003 | lsdt9 | 32200 | PEASE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322042 | lsdt9 | 32204 | OLIVHRST | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322061 | lsdt9 | 32206 | BOGUE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322062 | lsdt9 | 32206 | BOGUE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322262 | lsdt9 | 32226 | BRUNSWCK | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322271 | lsdt9 | 32227 | BRNSWALT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322301 | lsdt9 | 32230 | HORSESHE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322302 | lsdt9 | 32230 | HORSESHE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322481 | lsdt9 | 32248 | ROCKLIN | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322482 | lsdt9 | 32248 | ROCKLIN | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322702 | lsdt9 | 32270 | PENRYN | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.68 | 58.7 | 0.1 | 0.1 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322723 | lsdt9 | 32272 | DEL MAR | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.48 | 58.9 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323341 | lsdt9 | 32334 | LIVE OAK | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.61 | 58.9 | 0.1 | 0.1 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323342 | lsdt9 | 32334 | LIVE OAK | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325122 | lsdt9 | 32512 | WISE | 12.47 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325501 | lsdt9 | 32550 | SILVERDO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325502 | lsdt9 | 32550 | SILVERDO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325641 | lsdt9 | 32564 | PUEBLO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.29 | 58.9 | 0.1 | 0.1 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325642 | lsdt9 | 32564 | PUEBLO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325682 | lsdt9 | 32568 | IGNACIO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.33 | 59.3 | 15 | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325685 | lsdt9 | 32568 | IGNACIO | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326542 | lsdt9 | 32654 | TULUCAY | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326561 | lsdt9 | 32656 | NAPA | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326562 | lsdt9 | 32656 | NAPA | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326711 | lsdt9 | 32671 | BOLINAS | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326821 | lsdt9 | 32682 | ALTO | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.25 | 58.9 | 0.1 | 0.1 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326823 | lsdt9 | 32682 | ALTO | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.24 | 58.9 | 0.1 | 0.1 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326882 | lsdt9 | 32688 | SAUSALTO | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327682 | lsdt9 | 32768 | RICHMOND | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.62 | 58.7 | 0.1 | 0.1 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327683 | lsdt9 | 32768 | RICHMOND | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327826 | lsdt9 | 32782 | STATIN D | 115 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327902 | lsdt9 | 32790 | STATIN X | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327904 | lsdt9 | 32790 | STATIN X | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327905 | lsdt9 | 32790 | STATIN X | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327921 | lsdt9 | 32792 | STATIN J | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327922 | lsdt9 | 32792 | STATIN J | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327925 | lsdt9 | 32792 | STATIN J | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327931 | lsdt9 | 32793 | SCHNITZ | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.6 | 0.33 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3290810 | lsdt9 | 32908 | OAK C12 | 12 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329082 | lsdt9 | 32908 | OAK C12 | 12 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.23 | 58.7 | 0.1 | 0.1 | 0.06 | 58.3 | 0.1 | 0.1 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329083 | lsdt9 | 32908 | OAK C12 | 12 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329571 | lsdt9 | 32957 | PRAXAIR | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.6 | 0.33 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329905 | lsdt9 | 32990 | MARTNZ D | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330004 | lsdt9 | 33000 | CC SUB | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330205 | lsdt9 | 33020 | MORAGA.C | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331031 | lsdt9 | 33103 | TASSAJARA_D1 | 21.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332031 | lsdt9 | 33203 | MISSON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332032 | lsdt9 | 33203 | MISSON | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.23 | 58.5 | 0.1 | 0.1 | 0.39 | 58.3 | 0.1 | 0.1 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332051 | lsdt9 | 33205 | HNTRS PT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332056 | lsdt9 | 33205 | HNTRS PT | 115 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332081 | lsdt9 | 33208 | MARTIN C | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332082 | lsdt9 | 33208 | MARTIN C | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332089 | lsdt9 | 33208 | MARTIN C | 115 | 9 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332181 | lsdt9 | 33218 | LARKIN 1 | 12 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332191 | lsdt9 | 33219 | LARKIN 2 | 12 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.3 | 58.3 | 0.1 | 0.1 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333031 | lsdt9 | 33303 | EST GRND | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333034 | lsdt9 | 33303 | EST GRND | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333035 | lsdt9 | 33303 | EST GRND | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333036 | lsdt9 | 33303 | EST GRND | 115 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333073 | lsdt9 | 33307 | MILLBRAE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333074 | lsdt9 | 33307 | MILLBRAE | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333109 | lsdt9 | 33310 | SANMATEO | 115 | 9 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333121 | lsdt9 | 33312 | BELMONT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333122 | lsdt9 | 33312 | BELMONT | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333123 | lsdt9 | 33312 | BELMONT | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333133 | lsdt9 | 33313 | BAIR | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333501 | lsdt9 | 33350 | SNTH LNE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333502 | lsdt9 | 33350 | SNTH LNE | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333531 | lsdt9 | 33353 | MILLBRAE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333574 | lsdt9 | 33357 | SAN MATO | 60 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333663 | lsdt9 | 33366 | HLF MNBY | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333701 | lsdt9 | 33370 | REDWOOD | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333704 | lsdt9 | 33370 | REDWOOD | 60 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333705 | lsdt9 | 33370 | REDWOOD | 60 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333721 | lsdt9 | 33372 | BLLE HVN | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333722 | lsdt9 | 33372 | BLLE HVN | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333723 | lsdt9 | 33372 | BLLE HVN | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333724 | lsdt9 | 33372 | BLLE HVN | 60 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333813 | lsdt9 | 33381 | GLENWOOD | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333871 | lsdt9 | 33387 | WOODSIDE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333872 | lsdt9 | 33387 | WOODSIDE | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335062 | lsdt9 | 33506 | STANISLS | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335101 | lsdt9 | 33510 | AVENA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335145 | lsdt9 | 33514 | MANTECA | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335146 | lsdt9 | 33514 | MANTECA | 115 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335147 | lsdt9 | 33514 | MANTECA | 115 | 7 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335181 | lsdt9 | 33518 | VIERRA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.72 | 58.7 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335291 | lsdt9 | 33529 | LAMMERS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.33 | 58.7 | 0.1 | 0.1 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335292 | lsdt9 | 33529 | LAMMERS | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.28 | 58.5 | 0.1 | 0.1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335481 | lsdt9 | 33548 | TRACY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335482 | lsdt9 | 33548 | TRACY | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335483 | lsdt9 | 33548 | TRACY | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335484 | lsdt9 | 33548 | TRACY | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335533 | lsdt9 | 33553 | STKTON B | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335554 | lsdt9 | 33555 | STKTON A | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335555 | lsdt9 | 33555 | STKTON A | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.31 | 58.5 | 0.1 | 0.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335644 | lsdt9 | 33564 | LOCKFORD | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336043 | lsdt9 | 33604 | WESTPOINTPH | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336082 | lsdt9 | 33608 | PNE GRVE | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336181 | lsdt9 | 33618 | OLETA | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336182 | lsdt9 | 33618 | OLETA | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336221 | lsdt9 | 33622 | CLAY | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336241 | lsdt9 | 33624 | INE PRSN | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336421 | lsdt9 | 33642 | LINDEN | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336504 | lsdt9 | 33650 | WEBER D | 60 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336623 | lsdt9 | 33662 | WEBER E | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336682 | lsdt9 | 33668 | WATERLOO | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336821 | lsdt9 | 33682 | SUMIDEN | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.6 | 0.33 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336901 | lsdt9 | 33690 | ROGH-RDY | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337183 | lsdt9 | 33718 | METTLER | 60 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337282 | lsdt9 | 33728 | LODI | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337781 | lsdt9 | 33778 | MDL_RIVR | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339441 | lsdt9 | 33944 | RVRBANK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339442 | lsdt9 | 33944 | RVRBANK | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339522 | lsdt9 | 33952 | VALLY HM | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341001 | lsdt9 | 34100 | CHWCHLLA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341002 | lsdt9 | 34100 | CHWCHLLA | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.6 | 58.3 | 0.1 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341041 | lsdt9 | 34104 | ATWATER | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341042 | lsdt9 | 34104 | ATWATER | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341161 | lsdt9 | 34116 | LE GRAND | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341301 | lsdt9 | 34130 | LIVNGSTN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341381 | lsdt9 | 34138 | EL CAPTN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341382 | lsdt9 | 34138 | EL CAPTN | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341383 | lsdt9 | 34138 | EL CAPTN | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341681 | lsdt9 | 34168 | EL NIDO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341682 | lsdt9 | 34168 | EL NIDO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342102 | lsdt9 | 34210 | SNTA NLA | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342111 | lsdt9 | 34211 | BULLD 21 | 21.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.31 | 58.3 | 0.1 | 0.1 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342132 | lsdt9 | 34213 | BULLD 12 | 12.47 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342133 | lsdt9 | 34213 | BULLD 12 | 12.47 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342157 | lsdt9 | 34215 | MIDWY D7 | 12.47 | 7 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342215 | lsdt9 | 34221 | MCCALL 5 | 12.47 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342481 | lsdt9 | 34248 | INDN FLT | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342622 | lsdt9 | 34262 | CASSIDY | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343491 | lsdt9 | 34349 | CANTUA_DIST1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343552 | lsdt9 | 34355 | AIRWAYS2 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.31 | 59.1 | 0.1 | 0.1 | 0.2 | 58.9 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343611 | lsdt9 | 34361 | AIRWAYS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.25 | 58.7 | 0.1 | 0.1 | 0.23 | 58.5 | 0.1 | 0.1 | 0.31 | 58.3 | 0.1 | 0.1 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343642 | lsdt9 | 34364 | CLOVIS-2 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343661 | lsdt9 | 34366 | SANGER | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.08 | 58.3 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343721 | lsdt9 | 34372 | MALAGA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343722 | lsdt9 | 34372 | MALAGA | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.44 | 59.5 | 30 | 0.1 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343723 | lsdt9 | 34372 | MALAGA | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343803 | lsdt9 | 34380 | REEDLEY | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343822 | lsdt9 | 34382 | WAHTOKE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343823 | lsdt9 | 34382 | WAHTOKE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343881 | lsdt9 | 34388 | RAINBW | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344022 | lsdt9 | 34402 | CAL AVE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344041 | lsdt9 | 34404 | WST FRSO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344042 | lsdt9 | 34404 | WST FRSO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344081 | lsdt9 | 34408 | BARTON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344083 | lsdt9 | 34408 | BARTON | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344102 | lsdt9 | 34410 | MANCHSTR | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344141 | lsdt9 | 34414 | WOODWARD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344142 | lsdt9 | 34414 | WOODWARD | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344143 | lsdt9 | 34414 | WOODWARD | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.26 | 58.3 | 0.1 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344181 | lsdt9 | 34418 | KINGSBURGD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.24 | 58.9 | 0.1 | 0.1 | 0.26 | 58.7 | 0.1 | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344183 | lsdt9 | 34418 | KINGSBURGD | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344261 | lsdt9 | 34426 | ALPAUGH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344581 | lsdt9 | 34458 | HARDWICK | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344661 | lsdt9 | 34466 | BIOLA | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344781 | lsdt9 | 34478 | TVY VLLY | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344803 | lsdt9 | 34480 | KEARNEY | 70 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344841 | lsdt9 | 34484 | KERMAN1 | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.46 | 58.7 | 0.1 | 0.1 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344862 | lsdt9 | 34486 | KERMAN2 | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344921 | lsdt9 | 34492 | REEDLEY | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344931 | lsdt9 | 34493 | AUBERRY | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344932 | lsdt9 | 34493 | AUBERRY | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345001 | lsdt9 | 34500 | DINUBA | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345002 | lsdt9 | 34500 | DINUBA | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.46 | 58.9 | 0.1 | 0.1 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345081 | lsdt9 | 34508 | CAMDEN | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345121 | lsdt9 | 34512 | CARUTHRS | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345122 | lsdt9 | 34512 | CARUTHRS | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345181 | lsdt9 | 34518 | LEMOORE | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.49 | 58.3 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345361 | lsdt9 | 34536 | ANGIOLA | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345405 | lsdt9 | 34540 | HENRIETTAD | 70 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345421 | lsdt9 | 34542 | JCBSCRNR | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345422 | lsdt9 | 34542 | JCBSCRNR | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345441 | lsdt9 | 34544 | TLRE LKE | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345481 | lsdt9 | 34548 | KETTLEMN | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345601 | lsdt9 | 34560 | CALFLAX | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.25 | 58.7 | 0.1 | 0.1 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345631 | lsdt9 | 34563 | STROUD_DIST1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346134 | lsdt9 | 34613 | GATES_DIST4 | 12.47 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.22 | 58.3 | 0.1 | 0.1 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346413 | lsdt9 | 34641 | GATES_DIST3 | 12.47 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346681 | lsdt9 | 34668 | KEARNEY_D1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346903 | lsdt9 | 34690 | CORCORAN_D3 | 12.47 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346911 | lsdt9 | 34691 | AVENAL_D1 | 21 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346924 | lsdt9 | 34692 | CORCORAN_D4 | 12.47 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347001 | lsdt9 | 34700 | SMYRNA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347002 | lsdt9 | 34700 | SMYRNA | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347022 | lsdt9 | 34702 | GOSE LKE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347101 | lsdt9 | 34710 | CHARKA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347121 | lsdt9 | 34712 | FAMOSO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347141 | lsdt9 | 34714 | LERDO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347142 | lsdt9 | 34714 | LERDO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347181 | lsdt9 | 34718 | KERN OIL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347182 | lsdt9 | 34718 | KERN OIL | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347183 | lsdt9 | 34718 | KERN OIL | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.34 | 58.9 | 0.1 | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347361 | lsdt9 | 34736 | MAGUNDEN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.12 | 58.5 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347404 | lsdt9 | 34740 | STOCKDLE | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347433 | lsdt9 | 34743 | SEMITROPIC_E | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.36 | 58.5 | 0.1 | 0.1 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347501 | lsdt9 | 34750 | TUPMAN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347526 | lsdt9 | 34752 | KERN PWR | 115 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347572 | lsdt9 | 34757 | TEVIS2 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347583 | lsdt9 | 34758 | LAMONT | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347602 | lsdt9 | 34760 | RIO BRVO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347603 | lsdt9 | 34760 | RIO BRVO | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347621 | lsdt9 | 34762 | RENFRO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347661 | lsdt9 | 34766 | SHAFTER | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.86 | 58.3 | 0.1 | 0.1 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347663 | lsdt9 | 34766 | SHAFTER | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347672 | lsdt9 | 34767 | RENFRO2 | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347748 | lsdt9 | 34774 | MIDWAY | 115 | 8 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347763 | lsdt9 | 34776 | TAFT | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347764 | lsdt9 | 34776 | TAFT | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.67 | 58.7 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347781 | lsdt9 | 34778 | FELLOWS | 21 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347782 | lsdt9 | 34778 | FELLOWS | 21 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347881 | lsdt9 | 34788 | NORCO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348101 | lsdt9 | 34810 | POSO MT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348721 | lsdt9 | 34872 | LAKEVIEW | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348741 | lsdt9 | 34874 | WHEELER | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.8 | 58.7 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348761 | lsdt9 | 34876 | TEJON | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348801 | lsdt9 | 34880 | SN BRNRD | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348881 | lsdt9 | 34888 | ARVIN | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348901 | lsdt9 | 34890 | WEEDPTCH | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349041 | lsdt9 | 34904 | OLD RIVR | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.21 | 58.3 | 0.1 | 0.1 | 0.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349042 | lsdt9 | 34904 | OLD RIVR | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349111 | lsdt9 | 34911 | FRUITVLE | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.78 | 58.9 | 0.1 | 0.1 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349112 | lsdt9 | 34911 | FRUITVLE | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.49 | 58.9 | 0.1 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349201 | lsdt9 | 34920 | ELK HLLS | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349352 | lsdt9 | 34935 | CUYAMA2 | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349361 | lsdt9 | 34936 | CUYAMA | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349661 | lsdt9 | 34966 | ANTELOPE | 70 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349671 | lsdt9 | 34967 | TWISSLEMN_D1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349692 | lsdt9 | 34969 | TWISSLEMN_D2 | 12.47 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350841 | lsdt9 | 35084 | GOOSELAKE_D1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351011 | lsdt9 | 35101 | SN LNDRO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351012 | lsdt9 | 35101 | SN LNDRO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351013 | lsdt9 | 35101 | SN LNDRO | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.31 | 58.7 | 0.1 | 0.1 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351041 | lsdt9 | 35104 | GRANT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351042 | lsdt9 | 35104 | GRANT | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351061 | lsdt9 | 35106 | MT EDEN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.23 | 58.7 | 0.1 | 0.1 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351062 | lsdt9 | 35106 | MT EDEN | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351063 | lsdt9 | 35106 | MT EDEN | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.32 | 58.7 | 0.1 | 0.1 | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351071 | lsdt9 | 35107 | DUMBARTN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351072 | lsdt9 | 35107 | DUMBARTN | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351073 | lsdt9 | 35107 | DUMBARTN | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352031 | lsdt9 | 35203 | LIVERMRE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352191 | lsdt9 | 35219 | VINEYARD | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352192 | lsdt9 | 35219 | VINEYARD | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352252 | lsdt9 | 35225 | LIVRMR_2 | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354501 | lsdt9 | 35450 | LOS ALTS | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356101 | lsdt9 | 35610 | MONTAGUE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356121 | lsdt9 | 35612 | TRIMBLE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356122 | lsdt9 | 35612 | TRIMBLE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356123 | lsdt9 | 35612 | TRIMBLE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356125 | lsdt9 | 35612 | TRIMBLE | 115 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356161 | lsdt9 | 35616 | SJB DG | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356164 | lsdt9 | 35616 | SJB DG | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356192 | lsdt9 | 35619 | SJB EF | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356193 | lsdt9 | 35619 | SJB EF | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356201 | lsdt9 | 35620 | EL PATIO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356202 | lsdt9 | 35620 | EL PATIO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356203 | lsdt9 | 35620 | EL PATIO | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356204 | lsdt9 | 35620 | EL PATIO | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356221 | lsdt9 | 35622 | SWIFT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.48 | 58.3 | 0.1 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356222 | lsdt9 | 35622 | SWIFT | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356223 | lsdt9 | 35622 | SWIFT | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356241 | lsdt9 | 35624 | MILPITAS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356243 | lsdt9 | 35624 | MILPITAS | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.4 | 58.5 | 0.1 | 0.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356246 | lsdt9 | 35624 | MILPITAS | 115 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356261 | lsdt9 | 35626 | MCKEE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356262 | lsdt9 | 35626 | MCKEE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356263 | lsdt9 | 35626 | MCKEE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356302 | lsdt9 | 35630 | MABURY | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356381 | lsdt9 | 35638 | EDENVALE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356382 | lsdt9 | 35638 | EDENVALE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356383 | lsdt9 | 35638 | EDENVALE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356384 | lsdt9 | 35638 | EDENVALE | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356463 | lsdt9 | 35646 | MRGN HIL | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.29 | 58.5 | 0.1 | 0.1 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356483 | lsdt9 | 35648 | LLAGAS | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.31 | 58.7 | 0.1 | 0.1 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356563 | lsdt9 | 35656 | PIERCY | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.73 | 58.5 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356593 | lsdt9 | 35659 | NORTECH | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357571 | lsdt9 | 35757 | ALMADEN | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359012 | lsdt9 | 35901 | GREENVALLEY | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359163 | lsdt9 | 35916 | PRUNEDLE | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359193 | lsdt9 | 35919 | SOLEDAD | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359403 | lsdt9 | 35940 | HOLST D | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360201 | lsdt9 | 36020 | LGNTS J1 | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.6 | 0.33 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360491 | lsdt9 | 36049 | BNA VSTA | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360531 | lsdt9 | 36053 | SPENCE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360532 | lsdt9 | 36053 | SPENCE | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360604 | lsdt9 | 36060 | GONZALES | 60 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360642 | lsdt9 | 36064 | SOLEDAD | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360692 | lsdt9 | 36069 | LOS OSTS | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.37 | 58.7 | 0.1 | 0.1 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360821 | lsdt9 | 36082 | SAN ARDO | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360841 | lsdt9 | 36084 | OILFLDS | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360842 | lsdt9 | 36084 | OILFLDS | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362546 | lsdt9 | 36254 | SN LS OB | 115 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362662 | lsdt9 | 36266 | SNTA MRA | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362663 | lsdt9 | 36266 | SNTA MRA | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.28 | 58.5 | 0.1 | 0.1 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363562 | lsdt9 | 36356 | PSA RBLS | 70 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363563 | lsdt9 | 36356 | PSA RBLS | 70 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368571 | lsdt9 | 36857 | Mission | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0 | 0.083 | 0.157 | 59.5 | 30 | 0.083 | 0.348 | 59.3 | 15 | 0.083 | 0.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368572 | lsdt9 | 36857 | Mission | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 30 | 0.083 | 0.198 | 59.5 | 60 | 0.083 | 0.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368573 | lsdt9 | 36857 | Mission | 60 | 3 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.3 | 0 | 0.083 | 0.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368601 | lsdt9 | 36860 | Palm | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0 | 0.083 | 0.32 | 58.5 | 0 | 0.083 | 0.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368601 | lsdt9 | 36860 | Laf T3 | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.9 | 0.0667 | 0.0667 | 0.26405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368602 | lsdt9 | 36860 | Palm | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0 | 0.083 | 0.424 | 59.5 | 30 | 0.083 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368701 | lsdt9 | 36870 | Agnew | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.5 | 0.0667 | 0.0667 | 0.17469 | 58.3 | 0.0667 | 0.0667 | 0.53752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368702 | lsdt9 | 36870 | Agnew | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.5 | 0.0667 | 0.0667 | 0.21194 | 58.3 | 0.0667 | 0.0667 | 0.39738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368711 | lsdt9 | 36871 | Brokaw | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.9 | 0.0667 | 0.0667 | 0.16054 | 58.7 | 0.0667 | 0.0667 | 0.31072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368712 | lsdt9 | 36871 | Brokaw | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.9 | 0.0667 | 0.0667 | 0.47276 | 58.7 | 0.0667 | 0.0667 | 0.43494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368731 | lsdt9 | 36873 | Central | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.5 | 0.0667 | 0.0667 | 0.66178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368732 | lsdt9 | 36873 | Central | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.7 | 0.0667 | 0.0667 | 0.34535 | 58.5 | 0.0667 | 0.0667 | 0.64466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368791 | lsdt9 | 36879 | Laf T1 | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.9 | 0.0667 | 0.0667 | 0.67328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368801 | lsdt9 | 36880 | Laf T2 | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.9 | 0.0667 | 0.0667 | 0.48724 | 58.7 | 0.0667 | 0.0667 | 0.3171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368871 | lsdt9 | 36887 | Serra | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.1 | 0 | 0.083 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368892 | lsdt9 | 36889 | Uranium | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.9 | 0 | 0.083 | 0.289 | 58.3 | 0 | 0.083 | 0.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368893 | lsdt9 | 36889 | Uranium | 60 | 3 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.7 | 0 | 0.083 | 0.552 | 58.3 | 0 | 0.083 | 0.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368901 | lsdt9 | 36890 | Walsh | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0 | 0.083 | 0.04 | 58.7 | 0 | 0.083 | 0.208 | 58.3 | 0 | 0.083 | 0.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368911 | lsdt9 | 36891 | Zeno | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.7 | 0 | 0.083 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368912 | lsdt9 | 36891 | Walsh | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0 | 0.083 | 0.258 | 58.9 | 15 | 0.083 | 0.17 | 58.7 | 0 | 0.083 | 0.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368961 | lsdt9 | 36896 | Fairview | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0.0667 | 0.0667 | 0.1439 | 58.9 | 0.0667 | 0.0667 | 0.23874 | 58.5 | 0.0667 | 0.0667 | 0.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368961 | lsdt9 | 36896 | Fairview | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.9 | 0 | 0.083 | 0.198 | 58.7 | 0 | 0.083 | 0.222 | 58.5 | 0 | 0.083 | 0.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368962 | lsdt9 | 36896 | Fairview | 60 | 2 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0.0667 | 0.0667 | 0.15136 | 59.1 | 0.0667 | 0.0667 | 0.15136 | 58.7 | 0.0667 | 0.0667 | 0.22046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368963 | lsdt9 | 36896 | Fairview | 60 | 3 | [6 empty] | : | #9 | 0.067 | 0.067 | 58.3 | 0.0667 | 0.0667 | 0.12396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369001 | lsdt9 | 36900 | RICHMOND | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.5 | 58.7 | 0.1 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371011 | lsdt9 | 37101 | CARMICAL | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.12 | 59.3 | 15 | 0.1 | 0.09 | 58.5 | 0.1 | 0.1 | 0.36 | 58.3 | 0.1 | 0.1 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371021 | lsdt9 | 37102 | ELKGROV1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371031 | lsdt9 | 37103 | ELVERTA1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.35 | 58.9 | 0.1 | 0.1 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371051 | lsdt9 | 37105 | FOOTHIL1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.37 | 58.5 | 0.1 | 0.1 | 0.34 | 58.3 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371061 | lsdt9 | 37106 | HEDGE 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.2 | 59.5 | 60 | 0.1 | 0.34 | 59.3 | 15 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371071 | lsdt9 | 37107 | HEDGE 3 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.29 | 58.5 | 0.1 | 0.1 | 0.09 | 58.3 | 0.1 | 0.1 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371081 | lsdt9 | 37108 | HURLEY 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.24 | 59.5 | 60 | 0.1 | 0.22 | 58.9 | 0.1 | 0.1 | 0.26 | 58.5 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371091 | lsdt9 | 37109 | HURLEY 2 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371111 | lsdt9 | 37111 | LAKE 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.34 | 59.5 | 30 | 0.1 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371141 | lsdt9 | 37114 | ORANGVL1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371151 | lsdt9 | 37115 | ORANGVL2 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.18 | 58.7 | 0.1 | 0.1 | 0.47 | 58.5 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371161 | lsdt9 | 37116 | POCKET 1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.26 | 58.7 | 0.1 | 0.1 | 0.33 | 58.3 | 0.1 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371171 | lsdt9 | 37117 | POCKET 2 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371211 | lsdt9 | 37121 | ELKGROV2 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.46 | 58.7 | 0.1 | 0.1 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371221 | lsdt9 | 37122 | LAKE 2 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.37 | 58.5 | 30 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371231 | lsdt9 | 37123 | NATOMAS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.17 | 58.5 | 0.1 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371241 | lsdt9 | 37124 | CORDOVA | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371251 | lsdt9 | 37125 | NATOMAS2 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.65 | 59.5 | 60 | 0.1 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371261 | lsdt9 | 37126 | FRANKLN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379051 | lsdt9 | 37905 | AIRPORT1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.05 | 0.385 | 59.3 | 15 | 0.05 | 0.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379061 | lsdt9 | 37906 | AIRPORT2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.05 | 0.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379081 | lsdt9 | 37908 | BELT1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.05 | 0.226 | 58.5 | 0.1 | 0.05 | 0.233 | 58.3 | 0.1 | 0.05 | 0.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379121 | lsdt9 | 37912 | CANBY2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.05 | 0.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379131 | lsdt9 | 37913 | CANBY3 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.05 | 0.167 | 58.5 | 0.1 | 0.05 | 0.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379171 | lsdt9 | 37917 | COLLEGE1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.05 | 0.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379201 | lsdt9 | 37920 | EASTRDG1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.05 | 0.215 | 58.3 | 0.1 | 0.05 | 0.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379291 | lsdt9 | 37929 | MOORE1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.05 | 0.408 | 58.7 | 0.1 | 0.05 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379301 | lsdt9 | 37930 | MOORE2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.05 | 0.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379491 | lsdt9 | 37949 | SULP1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.05 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379501 | lsdt9 | 37950 | SULP2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.05 | 0.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379521 | lsdt9 | 37952 | TEXASSP1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.05 | 0.401 | 58.3 | 0.1 | 0.05 | 0.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379591 | lsdt9 | 37959 | CANBY4 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.05 | 0.297 | 58.5 | 0.1 | 0.05 | 0.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380201 | lsdt9 | 38020 | CITY UKH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.083 | 0.15 | 0.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380221 | lsdt9 | 38022 | CARTWRT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380222 | lsdt9 | 38022 | CARTWRT | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.18 | 0.05 | 0.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380241 | lsdt9 | 38024 | JENNY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.15 | 0.083 | 0.207 | 58.3 | 0.15 | 0.083 | 0.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380281 | lsdt9 | 38028 | PLO ALTO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.043 | 59.1 | 0.1 | 0.1 | 0.013 | 58.9 | 0.1 | 0.1 | 0.168 | 58.5 | 0.1 | 0.1 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380282 | lsdt9 | 38028 | PLO ALTO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.084 | 59.1 | 0.1 | 0.1 | 0.212 | 58.5 | 0.1 | 0.1 | 0.055 | 58.3 | 0.1 | 0.1 | 0.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380283 | lsdt9 | 38028 | PLO ALTO | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.057 | 58.7 | 0.1 | 0.1 | 0.163 | 58.3 | 0.1 | 0.1 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380671 | lsdt9 | 38067 | FIDDYMENT | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.2632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380701 | lsdt9 | 38070 | PARKEAST | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.429 | 58.5 | 0.1 | 0.1 | 0.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380702 | lsdt9 | 38070 | PARKEAST | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.3625 | 58.3 | 0.1 | 0.1 | 0.3506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380721 | lsdt9 | 38072 | FTHILL | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380732 | lsdt9 | 38073 | RSCIND | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.25 | 58.5 | 0.1 | 0.1 | 0.31618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380761 | lsdt9 | 38076 | CIRBY | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.34783 | 59.5 | 60 | 0.1 | 0.59006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380781 | lsdt9 | 38078 | BASLN | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380821 | lsdt9 | 38082 | WEST RSC | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1 | 0.84407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380831 | lsdt9 | 38083 | BAKKIE | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.20996 | 59.5 | 30 | 0.1 | 0.24555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380861 | lsdt9 | 38086 | HARDROCK | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1 | 0.098712 | 59.3 | 15 | 0.1 | 0.51931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380871 | lsdt9 | 38087 | SO_EAST | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.76126 | 58.5 | 0.1 | 0.1 | 0.13514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380872 | lsdt9 | 38087 | SO_EAST | 60 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.30178 | 58.5 | 0.1 | 0.1 | 0.14793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380891 | lsdt9 | 38089 | SVISTA | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381421 | lsdt9 | 38142 | Pattton 2 | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0 | 0.18 | 0.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381461 | lsdt9 | 38146 | Leavitt 1 F2 | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0 | 0.12 | 0.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381471 | lsdt9 | 38147 | Leavitt 2 F4 | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0 | 0.12 | 0.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382051 | lsdt9 | 38205 | Parker_2 | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.15 | 0.083 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382521 | lsdt9 | 38252 | Standfrd | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382541 | lsdt9 | 38254 | Finney | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.15 | 0.083 | 0.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382561 | lsdt9 | 38256 | Rosemore | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382601 | lsdt9 | 38260 | Prescott | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382621 | lsdt9 | 38262 | Brggsmre | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.15 | 0.083 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382641 | lsdt9 | 38264 | Enslen | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.15 | 0.083 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382661 | lsdt9 | 38266 | Woodrow | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382721 | lsdt9 | 38272 | Lapham | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.083 | 0.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382741 | lsdt9 | 38274 | MARIPOS1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382781 | lsdt9 | 38278 | Oakdale | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 60 | 0.083 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382801 | lsdt9 | 38280 | Sylvan | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.15 | 0.083 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382821 | lsdt9 | 38282 | Reinway | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 0.15 | 0.083 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382841 | lsdt9 | 38284 | Lincoln | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382901 | lsdt9 | 38290 | Paradse | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0.15 | 0.083 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382921 | lsdt9 | 38292 | Sisk | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.15 | 0.083 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383021 | lsdt9 | 38302 | Roselle | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.083 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383071 | lsdt9 | 38307 | Kiernan | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0.15 | 0.083 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383081 | lsdt9 | 38308 | Stock Av | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0.233 | 0.05 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383131 | lsdt9 | 38313 | Claribel | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0.15 | 0.083 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383141 | lsdt9 | 38314 | Stoddard | 69 | 1 | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0.15 | 0.083 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384111 | lsdt9 | 38411 | WASHINGTON | 115 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 59.5 | 0.1 | 0.05 | 0.62 | 58.5 | 0.1 | 0.05 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384121 | lsdt9 | 38412 | ROGERS | 115 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 59.5 | 0.1 | 0.05 | 0.04 | 59.5 | 30 | 0.05 | 0.31 | 58.3 | 0.1 | 0.05 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384211 | lsdt9 | 38421 | CASTLEME | 115 | 1 | [6 empty] | : | #9 | 0.02 | 0.05 | 59.5 | 60 | 0.08333 | 0.09135 | 59.3 | 15 | 0.083333 | 0.36217 | 59.1 | 0.1 | 0.083333 | 0.45964 | 58.9 | 0.1 | 0.083333 | 0.098207 | 58.7 | 0.1 | 0.083333 | 0.082809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384221 | lsdt9 | 38422 | COOPER | 115 | 1 | [6 empty] | : | #9 | 0.02 | 0.05 | 58.7 | 0.1 | 0.08333 | 0.10092 | 58.5 | 0.1 | 0.083333 | 0.20842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384261 | lsdt9 | 38426 | PINEER | 115 | 1 | [6 empty] | : | #9 | 0.02 | 0.05 | 58.9 | 0.1 | 0.08333 | 0.1939 | 58.3 | 0.1 | 0.083333 | 0.3697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384301 | lsdt9 | 38430 | HILMAR | 115 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 59.5 | 0.1 | 0.05 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384341 | lsdt9 | 38434 | MARSHALL | 115 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 59.5 | 0.1 | 0.05 | 0.22 | 58.9 | 0.1 | 0.05 | 0.18 | 58.7 | 0.1 | 0.05 | 0.21 | 58.5 | 0.1 | 0.05 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384381 | lsdt9 | 38438 | TAYLR | 115 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 59.5 | 0.1 | 0.05 | 0.23 | 59.3 | 0.1 | 15 | 0.24 | 58.7 | 0.1 | 0.05 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384421 | lsdt9 | 38442 | AUGUST | 115 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 59.5 | 0.1 | 0.05 | 0.44 | 58.7 | 0.1 | 0.05 | 0.38 | 58.3 | 0.1 | 0.05 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384521 | lsdt9 | 38452 | ROEDING | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.9 | 0.1 | 0.05 | 0.22 | 58.3 | 0.1 | 0.05 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384541 | lsdt9 | 38454 | INDUTRIL | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.9 | 0.1 | 0.05 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384601 | lsdt9 | 38460 | CERES | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.7 | 0.1 | 0.05 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384681 | lsdt9 | 38468 | GILSTRAP | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.3 | 0.1 | 0.05 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384701 | lsdt9 | 38470 | HUGHSON | 115 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 59.5 | 0.1 | 0.05 | 0.04 | 59.3 | 15 | 0.05 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384721 | lsdt9 | 38472 | GEER | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.5 | 0.1 | 0.05 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384781 | lsdt9 | 38478 | WESTPORT | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.9 | 0.1 | 0.05 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384941 | lsdt9 | 38494 | CROWSLND | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.5 | 0.1 | 0.05 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385011 | lsdt9 | 38501 | COMMONS | 69 | 1 | [6 empty] | : | #9 | 0 | 0.1 | 58.5 | 0.1 | 0.05 | 0.61 | 58.3 | 0.1 | 0.05 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
389051 | lsdt9 | 38905 | Kenneth | 60 | 1 | [6 empty] | : | #9 | 0.067 | 0.067 | 59.5 | 0.0667 | 0.0667 | 0.58443 | 59.3 | 15 | 0.0667 | 0.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40007N1 | lsdt9 | 40007 | ABERDEEN | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40007N1 | lsdt9 | 40007 | ABERDEEN | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40007N2 | lsdt9 | 40007 | ABERDEEN | 115 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40039N1 | lsdt9 | 40039 | ALFALFA+ | 230 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40039N1 | lsdt9 | 40039 | ALFALFA+ | 230 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40047N | lsdt9 | 40047 | ALVEY_N | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.177 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40047N | lsdt9 | 40047 | ALVEY_N | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.177 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40115N | lsdt9 | 40115 | BINGEN | 69 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40127N1 | lsdt9 | 40127 | BOARDMAN | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40127N1 | lsdt9 | 40127 | BOARDMAN | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40127N2 | lsdt9 | 40127 | BOARDMAN | 115 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40127N2 | lsdt9 | 40127 | BOARDMAN | 115 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40247N | lsdt9 | 40247 | COLMBIA_FALS | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40247N | lsdt9 | 40247 | COLUMBIA_F | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40277N1 | lsdt9 | 40277 | COSMOPLS | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40348N | lsdt9 | 40348 | DIXON+ | 230 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 15 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40348N | lsdt9 | 40348 | DIXON+ | 230 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40440N | lsdt9 | 40440 | FRANKLIN_E | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.12 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
404451 | lsdt9 | 40445 | FREEWATER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.116 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40481N | lsdt9 | 40481 | GRANDVIEW | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.072 | 0.083 | 0.5 | 59.2 | 0.105 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40481N | lsdt9 | 40481 | GRANDVEW | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.072 | 0.083 | 0.5 | 59.2 | 0.105 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40509N | lsdt9 | 40509 | HARRISBURG+ | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.133 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
405301 | lsdt9 | 40530 | HENKLE_ST | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
406191 | lsdt9 | 40619 | LA_GRANDE | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
406201 | lsdt9 | 40620 | LA_GRANDE1 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40633N | lsdt9 | 40633 | LAPINE | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40641N | lsdt9 | 40641 | LEBANON | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.95897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40717N | lsdt9 | 40717 | MCNARY_S1 | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
407891 | lsdt9 | 40789 | OKANOGAN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59.3 | 0.1 | 0.05 | 0.589 | 59 | 0.1 | 0.05 | 0.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40789N | lsdt9 | 40789 | OKANOGAN | 115 | N | [6 empty] | : | #9 | 0.05 | 0.1 | 59 | 0.03 | 0.083333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40841N2 | lsdt9 | 40841 | PORT_ANG | 69 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.083 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40841N2 | lsdt9 | 40841 | PORT_ANG | 69 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40841N1 | lsdt9 | 40841 | PORT_ANG | 69 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.167 | 0.05 | 0.50659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40853N1 | lsdt9 | 40853 | POTLATCH+ | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40874N | lsdt9 | 40874 | REDMOND_W | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.083 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40899N | lsdt9 | 40899 | ROSS_W | 230 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
409111 | lsdt9 | 40911 | SACAJAWEA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.12 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40921N | lsdt9 | 40921 | SALEM | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.05 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40969N | lsdt9 | 40969 | SHELTON | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 0.99578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41071N1 | lsdt9 | 41071 | T_DALLE | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.033 | 0.133 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41071N2 | lsdt9 | 41071 | T_DALLE | 115 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.033 | 0.133 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41073N | lsdt9 | 41073 | TILLAMOOK | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41081N1 | lsdt9 | 41081 | TOLEDO | 69 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.083 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41081N2 | lsdt9 | 41081 | TOLEDO | 69 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.083 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
411391 | lsdt9 | 41139 | WENDSON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41159N1 | lsdt9 | 41159 | WINTHROP | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.1 | 58.8 | 0.03 | 0.083333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41163N | lsdt9 | 41163 | WILRDJON | 69 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41207N | lsdt9 | 41207 | GARDINER | 115 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.05 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41214F | lsdt9 | 41214 | INTALCO_1 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41214F | lsdt9 | 41214 | INTALCO_1 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41215F | lsdt9 | 41215 | INTALCO_2 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41216F | lsdt9 | 41216 | INTALCO_3 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41217F | lsdt9 | 41217 | INTALCO_4 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41218F | lsdt9 | 41218 | INTALCO_5 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41219F | lsdt9 | 41219 | INTALCO_6 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41220F | lsdt9 | 41220 | INTALCO_7 | 13.8 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41250N | lsdt9 | 41250 | REDMOND | 69 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.083 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420511 | lsdt9 | 42051 | SEMIAHMO | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59 | 0.1 | 0.1 | 0.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420541 | lsdt9 | 42054 | LAUREL P | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 0.1 | 0.1 | 0.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420701 | lsdt9 | 42070 | LKLOUISE | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420821 | lsdt9 | 42082 | SEHOME | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 30.2333 | 0.1 | 0.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421531 | lsdt9 | 42153 | GAGES | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.2 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421571 | lsdt9 | 42157 | ANACORT | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421651 | lsdt9 | 42165 | BURROWS | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421671 | lsdt9 | 42167 | HICKOX | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421711 | lsdt9 | 42171 | NORLUM | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421741 | lsdt9 | 42174 | PETHCORN | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421841 | lsdt9 | 42184 | SUMMITPK | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 0.1 | 0.1 | 0.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423091 | lsdt9 | 42309 | MOUNT SI | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 30.2333 | 0.1 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423101 | lsdt9 | 42310 | COTAGEBR | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423841 | lsdt9 | 42384 | BRIDLE | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423842 | lsdt9 | 42384 | BRIDLE | 115 | 2 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 0.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423971 | lsdt9 | 42397 | FACTORIA | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
424041 | lsdt9 | 42404 | HOUGHTON | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 15.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
424081 | lsdt9 | 42408 | JUANITAP | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 0.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
424082 | lsdt9 | 42408 | JUANITAP | 115 | 2 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 0.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
424121 | lsdt9 | 42412 | KLAHANIE | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 30.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
424181 | lsdt9 | 42418 | MEDINA | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
425061 | lsdt9 | 42506 | CHRISTOP | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
425301 | lsdt9 | 42530 | STARWOOD | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 15.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
425302 | lsdt9 | 42530 | STARWOOD | 115 | 2 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 15.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
426011 | lsdt9 | 42601 | FREEWAY | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
426091 | lsdt9 | 42609 | LKYOUNGS | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 0.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
426291 | lsdt9 | 42629 | NNORMTAP | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
426391 | lsdt9 | 42639 | PRES PK | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 60.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
426481 | lsdt9 | 42648 | 4CORNERS | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
427631 | lsdt9 | 42763 | KNOBLEP | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
427671 | lsdt9 | 42767 | HOLDEN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.08 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
427811 | lsdt9 | 42781 | SUNRISEP | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428081 | lsdt9 | 42808 | BLUMAER | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428511 | lsdt9 | 42851 | MCAL.SPR | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428641 | lsdt9 | 42864 | CHAMBERP | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428801 | lsdt9 | 42880 | PATTERSN | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428831 | lsdt9 | 42883 | SOUTHWIK | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 58.6 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428921 | lsdt9 | 42892 | RAINR VW | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428941 | lsdt9 | 42894 | FR.GROVE | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.2 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428951 | lsdt9 | 42895 | HAWKS PR | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.5 | 30.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
429481 | lsdt9 | 42948 | KINGSTON | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.2 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
429681 | lsdt9 | 42968 | R.POINT | 115 | 1 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 15.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
429682 | lsdt9 | 42968 | R.POINT | 115 | 2 | [6 empty] | : | #9 | 0 | 0.4 | 59.3 | 15.2333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430071 | lsdt9 | 43007 | ALDERCRT | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.6 | 0.1 | 0.083333 | 0.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430111 | lsdt9 | 43011 | ARLETA | 59.8 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.03 | 0.083333 | 0.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430131 | lsdt9 | 43013 | BANKS | 59.8 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.1 | 0.083333 | 0.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430291 | lsdt9 | 43029 | BEAVERTON | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.1 | 0.083333 | 0.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430331 | lsdt9 | 43033 | BELL | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430431 | lsdt9 | 43043 | BETHELSO | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430611 | lsdt9 | 43061 | BRGHTWD | 59.8 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.1 | 0.083333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430911 | lsdt9 | 43091 | CEDARHIL | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430951 | lsdt9 | 43095 | CLACKMAS | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59 | 0.1 | 0.083333 | 0.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430971 | lsdt9 | 43097 | CLAXTER | 59.8 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430991 | lsdt9 | 43099 | CNTENIAL | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.07 | 0.083333 | 0.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
431371 | lsdt9 | 43137 | DAYTON | 59.8 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
431451 | lsdt9 | 43145 | DENNY | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.08 | 0.083333 | 0.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
431571 | lsdt9 | 43157 | E SUBSTA | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.6 | 0.1 | 0.083333 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
431851 | lsdt9 | 43185 | FAIRVW P | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59 | 0.1 | 0.083333 | 0.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
432071 | lsdt9 | 43207 | GLNDOVER | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
432651 | lsdt9 | 43265 | INDIAN | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
433151 | lsdt9 | 43315 | MERIDIAN | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.6 | 0.1 | 0.083333 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
433231 | lsdt9 | 43323 | MOLALLAN | 59.8 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
433571 | lsdt9 | 43357 | NEWBERG | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59 | 0.1 | 0.083333 | 0.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434211 | lsdt9 | 43421 | PORTSMTH | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434751 | lsdt9 | 43475 | ROCKWD | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.1 | 0.083333 | 0.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
435311 | lsdt9 | 43531 | SIXCRNRS | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
435511 | lsdt9 | 43551 | STMARYES | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.1 | 0.083333 | 0.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
435591 | lsdt9 | 43559 | SULIVAN | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.1 | 0.083333 | 0.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
435871 | lsdt9 | 43587 | TIGARD | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
436501 | lsdt9 | 43650 | WILSNVIL | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
436621 | lsdt9 | 43662 | WSTUNION | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
436911 | lsdt9 | 43691 | CURTISPG | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.8 | 0.1 | 0.083333 | 0.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
436931 | lsdt9 | 43693 | DURHAM | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
437101 | lsdt9 | 43710 | KELLEYPT | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
437131 | lsdt9 | 43713 | MARKET | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
437671 | lsdt9 | 43767 | LIBTY PG | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.3 | 0.1 | 0.083333 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
437951 | lsdt9 | 43795 | OXFRD PG | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.6 | 0.1 | 0.083333 | 0.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
438061 | lsdt9 | 43806 | MURAY LD | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 59.2 | 0.1 | 0.083333 | 0.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
438111 | lsdt9 | 43811 | ORENCOLD | 115 | 1 | [6 empty] | : | #9 | 0.1 | 0.05 | 58.6 | 0.1 | 0.083333 | 0.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445201 | lsdt9 | 44520 | VERNON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445202 | lsdt9 | 44520 | VERNON | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449251 | lsdt9 | 44925 | ROXYANN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449361 | lsdt9 | 44936 | BEALL LN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449591 | lsdt9 | 44959 | SHEVLNPK | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449601 | lsdt9 | 44960 | WEED | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449701 | lsdt9 | 44970 | MTSHASTA | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449702 | lsdt9 | 44970 | MTSHASTA | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450091 | lsdt9 | 45009 | APPLEGAT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450161 | lsdt9 | 45016 | BELKNAP | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450191 | lsdt9 | 45019 | BOWMAN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450241 | lsdt9 | 45024 | BEND PLT | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450271 | lsdt9 | 45027 | BUCKAROO | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450491 | lsdt9 | 45049 | CLINTON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450531 | lsdt9 | 45053 | COLUM PG | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450532 | lsdt9 | 45053 | COLUM PG | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450671 | lsdt9 | 45067 | COQUILLE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450681 | lsdt9 | 45068 | BOND ST | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450701 | lsdt9 | 45070 | BRYANT | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450721 | lsdt9 | 45072 | BUCHANAN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450741 | lsdt9 | 45074 | CAMPBELL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450751 | lsdt9 | 45075 | DALREED | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450752 | lsdt9 | 45075 | DALREED | 230 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450821 | lsdt9 | 45082 | CASCADE | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450822 | lsdt9 | 45082 | CASCADE | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450823 | lsdt9 | 45082 | CASCADE | 69 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450824 | lsdt9 | 45082 | CASCADE | 69 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450825 | lsdt9 | 45082 | CASCADE | 69 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450921 | lsdt9 | 45092 | CHERRYLN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451191 | lsdt9 | 45119 | GRANDVW2 | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451431 | lsdt9 | 45143 | HLLYWOOD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451432 | lsdt9 | 45143 | HLLYWOOD | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451451 | lsdt9 | 45145 | HOOD RVR | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451472 | lsdt9 | 45147 | HOPLAND | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451581 | lsdt9 | 45158 | DODGE BR | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451642 | lsdt9 | 45164 | DUNSMUIR | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451691 | lsdt9 | 45169 | LEBANONP | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451692 | lsdt9 | 45169 | LEBANONP | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451771 | lsdt9 | 45177 | LOCKHRT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451861 | lsdt9 | 45186 | FLDR CRK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452061 | lsdt9 | 45206 | GRANT PP | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452062 | lsdt9 | 45206 | GRANT PP | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452073 | lsdt9 | 45207 | MURDERCK | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452074 | lsdt9 | 45207 | MURDERCK | 115 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452081 | lsdt9 | 45208 | GREEN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452111 | lsdt9 | 45211 | NACHES | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452141 | lsdt9 | 45214 | GRIFFINP | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452171 | lsdt9 | 45217 | NOBHILL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452172 | lsdt9 | 45217 | NOBHILL | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452355 | lsdt9 | 45235 | PENDLTON | 69 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452356 | lsdt9 | 45235 | PENDLTON | 69 | 6 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452411 | lsdt9 | 45241 | POMEROYP | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452441 | lsdt9 | 45244 | INTPAPER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452521 | lsdt9 | 45252 | JACKSNVL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452551 | lsdt9 | 45255 | PRINVILE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452571 | lsdt9 | 45257 | PROSPECW | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452572 | lsdt9 | 45257 | PROSPECW | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452631 | lsdt9 | 45263 | RDMNDPPL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452671 | lsdt9 | 45267 | RIVR RD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452672 | lsdt9 | 45267 | RIVR RD | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452691 | lsdt9 | 45269 | RUSSELLV | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452692 | lsdt9 | 45269 | RUSSELLV | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452711 | lsdt9 | 45271 | SAGEROAD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452712 | lsdt9 | 45271 | SAGEROAD | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452751 | lsdt9 | 45275 | SEASIDE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452771 | lsdt9 | 45277 | SELAH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452772 | lsdt9 | 45277 | SELAH | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452851 | lsdt9 | 45285 | SWEETHOM | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452951 | lsdt9 | 45295 | TOPPENSH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452952 | lsdt9 | 45295 | TOPPENSH | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453231 | lsdt9 | 45323 | WAITBURG | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453431 | lsdt9 | 45343 | WHITECTY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453432 | lsdt9 | 45343 | WHITECTY | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453433 | lsdt9 | 45343 | WHITECTY | 115 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453661 | lsdt9 | 45366 | OAKKNOLL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453811 | lsdt9 | 45381 | CAVE JCT | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453821 | lsdt9 | 45382 | CAVEMAN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453871 | lsdt9 | 45387 | DEVIL LK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453872 | lsdt9 | 45387 | DEVIL LK | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453891 | lsdt9 | 45389 | EASY VLY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453892 | lsdt9 | 45389 | EASY VLY | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453911 | lsdt9 | 45391 | FERN HIL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454111 | lsdt9 | 45411 | PARK ST | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454321 | lsdt9 | 45432 | KLNGSWTH | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454322 | lsdt9 | 45432 | KLNGSWTH | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454332 | lsdt9 | 45433 | ORCHARDW | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454361 | lsdt9 | 45436 | ALDRWOOD | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454611 | lsdt9 | 45461 | QUEEN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454612 | lsdt9 | 45461 | QUEEN | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454691 | lsdt9 | 45469 | ROSEBURG | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454692 | lsdt9 | 45469 | ROSEBURG | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45475N | lsdt9 | 45475 | SANTIAM | 69 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454931 | lsdt9 | 45493 | STAT ST | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454932 | lsdt9 | 45493 | STAT ST | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.0833 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454941 | lsdt9 | 45494 | STAYTON | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454961 | lsdt9 | 45496 | STEVENRD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454981 | lsdt9 | 45498 | SULPHR P | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454991 | lsdt9 | 45499 | SUTHRLIN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455011 | lsdt9 | 45501 | TALENT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455012 | lsdt9 | 45501 | TALENT | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455211 | lsdt9 | 45521 | WARRNTON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455301 | lsdt9 | 45530 | WEYERHSR | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455331 | lsdt9 | 45533 | WINCHSTR | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455381 | lsdt9 | 45538 | YREKA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455401 | lsdt9 | 45540 | YUNGSBAY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455402 | lsdt9 | 45540 | YUNGSBAY | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.0833 | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456031 | lsdt9 | 45603 | BALLINGER | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15.055 | 0.0583 | 0.748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456121 | lsdt9 | 45612 | JENNINGS PK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.132 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456301 | lsdt9 | 45630 | PORTAGE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.147 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456311 | lsdt9 | 45631 | E MARYS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.12 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456491 | lsdt9 | 45649 | FLORAL H | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.068 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456531 | lsdt9 | 45653 | FRONTIER | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.119 | 0.05 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456571 | lsdt9 | 45657 | GIBSON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.085 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456651 | lsdt9 | 45665 | GRANFAL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.128 | 0.0833 | 0.566 | 58.6 | 0.142 | 0.0833 | 0.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456791 | lsdt9 | 45679 | HARBOR P | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.09 | 0.0833 | 0.579 | 59 | 0.13 | 0.0833 | 0.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456831 | lsdt9 | 45683 | HILTON LK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1333 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456931 | lsdt9 | 45693 | KELLOGM | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.118 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456991 | lsdt9 | 45699 | LK GOODWIN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.125 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457111 | lsdt9 | 45711 | MARTHA LK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15.053 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457131 | lsdt9 | 45713 | MEADWD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.09 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457171 | lsdt9 | 45717 | MOUNTLAKE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.119 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457231 | lsdt9 | 45723 | MURPHYS CR | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.115 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457291 | lsdt9 | 45729 | N MARYS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30.056 | 0.0583 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457391 | lsdt9 | 45739 | OLIVIA P | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.084 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45745F | lsdt9 | 45745 | PAINE FIELD | 115 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.12 | 0.0833 | 0.419 | 58.8 | 0.127 | 0.05 | 0.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457511 | lsdt9 | 45751 | PICNIC PT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.128 | 0.0833 | 0.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457531 | lsdt9 | 45753 | PINEHURST | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30.057 | 0.0583 | 0.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457591 | lsdt9 | 45759 | RICHMOND | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60.067 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457851 | lsdt9 | 45785 | STIMSON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15.051 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
458031 | lsdt9 | 45803 | THREE LK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.118 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
458091 | lsdt9 | 45809 | TURNERS CR | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.149 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
458231 | lsdt9 | 45823 | WOODS CK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.12 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
458571 | lsdt9 | 45857 | SILVER LK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60.068 | 0.0833 | 0.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
458611 | lsdt9 | 45861 | WATERFRONT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.118 | 0.05 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
458661 | lsdt9 | 45866 | EAGLE CREEK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.114 | 0.05 | 0.451 | 58.6 | 0.11 | 0.05 | 0.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46143F | lsdt9 | 46143 | SILICON | 230 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.05 | 0.3 | 59.5 | 30 | 0.05 | 0.315 | 59.3 | 15 | 0.05 | 0.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46159F | lsdt9 | 46159 | UPPER C | 230 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 0.1 | 58.8 | 0.133 | 0.05 | 0.425 | 58.6 | 0.133 | 0.05 | 0.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462021 | lsdt9 | 46202 | ADAMS_EWEB | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462031 | lsdt9 | 46203 | BERTLSON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462061 | lsdt9 | 46206 | BETHEL_E | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.033 | 0.083 | 0.80745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462131 | lsdt9 | 46213 | CURRIN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.083 | 0.60241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462141 | lsdt9 | 46214 | COBURG | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.083 | 0.083 | 0.79365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462151 | lsdt9 | 46215 | DANEBO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0 | 0.083 | 0.36866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462152 | lsdt9 | 46215 | DANEBO | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0 | 0.083 | 0.36866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462191 | lsdt9 | 46219 | DILLARD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462192 | lsdt9 | 46219 | DILLARD | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462431 | lsdt9 | 46243 | OAKWAY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.083 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462471 | lsdt9 | 46247 | RIVER_RD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.083 | 0.083 | 0.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462501 | lsdt9 | 46250 | SENECA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0 | 0.083 | 0.79365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462511 | lsdt9 | 46251 | SPRING_CK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.033 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462511 | lsdt9 | 46251 | SPRING C | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.033 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462512 | lsdt9 | 46251 | SPRING_CK | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.033 | 0.083 | 0.8642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462512 | lsdt9 | 46251 | SPRING C | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.033 | 0.083 | 0.8642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462531 | lsdt9 | 46253 | ST_CLARA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.083 | 0.083 | 0.68592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462611 | lsdt9 | 46261 | WESTMORE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0 | 0.083 | 0.82192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462612 | lsdt9 | 46261 | WESTMORE | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0 | 0.083 | 0.82192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462691 | lsdt9 | 46269 | WILLAKENZIE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.083 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462751 | lsdt9 | 46275 | WILLOW_CK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0 | 0.083 | 0.77348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464091 | lsdt9 | 46409 | BROAD ST | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.083 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464111 | lsdt9 | 46411 | CANAL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.083 | 0.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464151 | lsdt9 | 46415 | CRESTON | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464171 | lsdt9 | 46417 | DELRIDGE | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464371 | lsdt9 | 46437 | NORTH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.402 | 59.3 | 15 | 0.05 | 0.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464431 | lsdt9 | 46443 | SHORELIN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.083 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464451 | lsdt9 | 46445 | SOUTH | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.083 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46445F | lsdt9 | 46445 | SOUTH | 230 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464551 | lsdt9 | 46455 | VIEWLAND | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466021 | lsdt9 | 46602 | KNOBLE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466791 | lsdt9 | 46679 | BRDGPRT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466861 | lsdt9 | 46686 | CLEMENT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466931 | lsdt9 | 46693 | CRESENT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466941 | lsdt9 | 46694 | CROFT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467181 | lsdt9 | 46718 | GOVE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467221 | lsdt9 | 46722 | HAWTHORN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467251 | lsdt9 | 46725 | HIGHLDTA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467281 | lsdt9 | 46728 | HYLEBOS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467371 | lsdt9 | 46737 | MOUNTAIN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467581 | lsdt9 | 46758 | OLDTWN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467601 | lsdt9 | 46760 | ORCHRD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467641 | lsdt9 | 46764 | PORTLND | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467861 | lsdt9 | 46786 | WESTGAT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469421 | lsdt9 | 46942 | COLLINS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469471 | lsdt9 | 46947 | ELKPLN-T | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469491 | lsdt9 | 46949 | LACAMS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469661 | lsdt9 | 46966 | HUSON | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469681 | lsdt9 | 46968 | RSVLT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469691 | lsdt9 | 46969 | WAPATOTA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469711 | lsdt9 | 46971 | MCNEIL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469741 | lsdt9 | 46974 | CLOVERPK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.13 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470291 | lsdt9 | 47029 | DOUGLAS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59.2 | 1 | 0.045 | 0.54 | 58.6 | 1 | 0.045 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470361 | lsdt9 | 47036 | DONEEN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59.2 | 0.5 | 0.05 | 0.52 | 58.6 | 0.5 | 0.05 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470371 | lsdt9 | 47037 | EASTMONT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59 | 0.5 | 0.05 | 0.1 | 58.6 | 0.5 | 0.05 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470441 | lsdt9 | 47044 | FSTR CR | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59.3 | 0.5 | 0.045 | 0.03 | 59.2 | 0.5 | 0.045 | 0.14 | 59 | 0.5 | 0.045 | 0.26 | 58.6 | 0.5 | 0.045 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470511 | lsdt9 | 47051 | HANNA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59 | 0.5 | 0.042 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470591 | lsdt9 | 47059 | VEEDOL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59.3 | 0.5 | 0.05 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
471271 | lsdt9 | 47127 | BRAYS LD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 59.2 | 1 | 0.045 | 0.87 | 58.6 | 1 | 0.045 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
471851 | lsdt9 | 47185 | MALOTT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 58.8 | 0.03 | 0.083333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
472171 | lsdt9 | 47217 | S_ELMA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
472511 | lsdt9 | 47251 | TWISP | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.1 | 58.8 | 0.03 | 0.083333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47251N | lsdt9 | 47251 | TWISP | 115 | N | [6 empty] | : | #9 | 0.05 | 0.1 | 58.8 | 0.03 | 0.083333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
473401 | lsdt9 | 47340 | RUBY_ST+ | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.05 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F1 | lsdt9 | 47439 | NORPAC | 230 | F1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 13 | 2 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F1 | lsdt9 | 47439 | NORPAC | 230 | F1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F2 | lsdt9 | 47439 | NORPAC | 230 | F2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 13 | 2 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F2 | lsdt9 | 47439 | NORPAC | 230 | F2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F3 | lsdt9 | 47439 | NORPAC | 230 | F3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 13 | 2 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F3 | lsdt9 | 47439 | NORPAC | 230 | F3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F4 | lsdt9 | 47439 | NORPAC | 230 | F4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 13 | 2 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F4 | lsdt9 | 47439 | NORPAC | 230 | F4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F5 | lsdt9 | 47439 | NORPAC | 230 | F5 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 13 | 2 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F5 | lsdt9 | 47439 | NORPAC | 230 | F5 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F6 | lsdt9 | 47439 | NORPAC | 230 | F6 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 13 | 2 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F6 | lsdt9 | 47439 | NORPAC | 230 | F6 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F7 | lsdt9 | 47439 | NORPAC | 230 | F7 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 13 | 2 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47439F7 | lsdt9 | 47439 | NORPAC | 230 | F7 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480131 | lsdt9 | 48013 | APPLEWAY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 0.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480191 | lsdt9 | 48019 | AVONDALE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480211 | lsdt9 | 48021 | BARKER | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480231 | lsdt9 | 48023 | BEACON N | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480291 | lsdt9 | 48029 | BEACON S | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480691 | lsdt9 | 48069 | CHESTER | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480711 | lsdt9 | 48071 | CHEWELAH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480791 | lsdt9 | 48079 | COLBERT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480811 | lsdt9 | 48081 | COLLWALN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.05 | 0.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480831 | lsdt9 | 48083 | COLV AVA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 0.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480931 | lsdt9 | 48093 | DALTON A | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481171 | lsdt9 | 48117 | EASTFARM | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481271 | lsdt9 | 48127 | FRANCEDR | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481291 | lsdt9 | 48129 | FTWRIGHT | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481371 | lsdt9 | 48137 | GLENROSE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.625 | 59.5 | 60 | 0.05 | 0.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481421 | lsdt9 | 48142 | GREENACRES | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481611 | lsdt9 | 48161 | IDAHO_RD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481641 | lsdt9 | 48164 | INDTRAIL | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481851 | lsdt9 | 48185 | LIBTYLK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 0.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481951 | lsdt9 | 48195 | LOLO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.05 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482191 | lsdt9 | 48219 | LYONSTND | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482221 | lsdt9 | 48222 | MEAD SUB | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482431 | lsdt9 | 48243 | MOSCCITY | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.05 | 0.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482711 | lsdt9 | 48271 | NINTHCNT_N | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482721 | lsdt9 | 48272 | NINTHCNT_S | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482771 | lsdt9 | 48277 | NORTHEAS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 0.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482791 | lsdt9 | 48279 | Northwes | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 0.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482911 | lsdt9 | 48291 | TURNER_WSU | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482931 | lsdt9 | 48293 | ODEN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482981 | lsdt9 | 48298 | OLDTOWN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48298F | lsdt9 | 48298 | OLDTOWN | 115 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482991 | lsdt9 | 48299 | OPPORTUN | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483031 | lsdt9 | 48303 | OROFINO | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48323N1 | lsdt9 | 48323 | PLUMMER | 115 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48323N2 | lsdt9 | 48323 | PLUMMER | 115 | N2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483431 | lsdt9 | 48343 | POUNDLNE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.05 | 0.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483711 | lsdt9 | 48371 | ROSSPARK | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 0.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483761 | lsdt9 | 48376 | SAGLE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483771 | lsdt9 | 48377 | SANDPT A | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483891 | lsdt9 | 48389 | SLEWIST | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483951 | lsdt9 | 48395 | SOUTHEAS | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48405F | lsdt9 | 48405 | SPKINDPK | 115 | F | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.133 | 0.05 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484171 | lsdt9 | 48417 | SAINT MARIES | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.133 | 0.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484211 | lsdt9 | 48421 | SUNSET | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.05 | 0.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484291 | lsdt9 | 48429 | TENTHSTW | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484301 | lsdt9 | 48430 | TERRVIEW | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484311 | lsdt9 | 48431 | THIRHACH | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.125 | 59.3 | 0.133 | 0.05 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484471 | lsdt9 | 48447 | WAIKIKI | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485141 | lsdt9 | 48514 | CRCHFELD | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485601 | lsdt9 | 48560 | POLELINE | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.133 | 0.05 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500711 | lsdt9 | 50071 | ERW 60 | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501281 | lsdt9 | 50128 | CSQ 12A | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.0833 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501291 | lsdt9 | 50129 | NEL 12B | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 0.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501341 | lsdt9 | 50134 | RIM 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501411 | lsdt9 | 50141 | HSP 13T2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.7 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501541 | lsdt9 | 50154 | ANN 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501591 | lsdt9 | 50159 | STV 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501681 | lsdt9 | 50168 | CAM 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.055 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502631 | lsdt9 | 50263 | WHY 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502681 | lsdt9 | 50268 | CHK 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502711 | lsdt9 | 50271 | SRY 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502791 | lsdt9 | 50279 | ARN 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502801 | lsdt9 | 50280 | MLN 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.0833 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502821 | lsdt9 | 50282 | CBN 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502851 | lsdt9 | 50285 | SYH 25C | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 0.25 | 58.5 | 0.0833 | 0.1 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
503741 | lsdt9 | 50374 | BKP 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504021 | lsdt9 | 50402 | TM2 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504041 | lsdt9 | 50404 | HSY 12B | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504051 | lsdt9 | 50405 | ESQ 12B | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504091 | lsdt9 | 50409 | HWD 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504111 | lsdt9 | 50411 | KTG 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504121 | lsdt9 | 50412 | PAL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1333 | 0.63 | 58.4 | 0.0833 | 0.1333 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504131 | lsdt9 | 50413 | NFD 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.8333 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504141 | lsdt9 | 50414 | PUN 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504151 | lsdt9 | 50415 | CBL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1333 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504181 | lsdt9 | 50418 | KGH 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504191 | lsdt9 | 50419 | CMX 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 0.4 | 58.7 | 0.0833 | 0.1333 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504201 | lsdt9 | 50420 | PVL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 0.6 | 58.9 | 0.0833 | 0.0833 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504221 | lsdt9 | 50422 | SNY 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504241 | lsdt9 | 50424 | GOW 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504251 | lsdt9 | 50425 | GTP 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504261 | lsdt9 | 50426 | HSY 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504271 | lsdt9 | 50427 | CLD 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504281 | lsdt9 | 50428 | SOO 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504291 | lsdt9 | 50429 | JOR 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.4 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504341 | lsdt9 | 50434 | LTZ 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1217 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506181 | lsdt9 | 50618 | BVY 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506241 | lsdt9 | 50624 | PBL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506261 | lsdt9 | 50626 | BRN 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506271 | lsdt9 | 50627 | DAW 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506281 | lsdt9 | 50628 | CHF 25T11 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506301 | lsdt9 | 50630 | PLT 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506321 | lsdt9 | 50632 | BAB 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506331 | lsdt9 | 50633 | FSS 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506361 | lsdt9 | 50636 | RBF 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
508141 | lsdt9 | 50814 | EV1 66 | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
508591 | lsdt9 | 50859 | FNE 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509351 | lsdt9 | 50935 | 45863 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 5 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509801 | lsdt9 | 50980 | BCC 13A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.1 | 0.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509851 | lsdt9 | 50985 | BCC 13B | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.1 | 0.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509991 | lsdt9 | 50999 | BCM 66A | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510001 | lsdt9 | 51000 | BCM 66B | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510231 | lsdt9 | 51023 | OYR 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510261 | lsdt9 | 51026 | QLC 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510371 | lsdt9 | 51037 | CRS 13 | 13.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510441 | lsdt9 | 51044 | PRT 12B | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510921 | lsdt9 | 51092 | NKL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
511101 | lsdt9 | 51110 | MHY 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.05 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512021 | lsdt9 | 51202 | PRT 12A | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512091 | lsdt9 | 51209 | MLE 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512361 | lsdt9 | 51236 | CFT 13F | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512391 | lsdt9 | 51239 | PGI 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.05 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512961 | lsdt9 | 51296 | FMC 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
513671 | lsdt9 | 51367 | ATH 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
513701 | lsdt9 | 51370 | MKZ 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
513791 | lsdt9 | 51379 | CPS 12 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.17 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514261 | lsdt9 | 51426 | PVO 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514541 | lsdt9 | 51454 | MKZ 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514841 | lsdt9 | 51484 | KMI 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1583 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514941 | lsdt9 | 51494 | AFP 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514951 | lsdt9 | 51495 | CAM 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
515221 | lsdt9 | 51522 | SCO 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516071 | lsdt9 | 51607 | WEY 13T2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.7 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516091 | lsdt9 | 51609 | CUM 27B2 | 27 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516371 | lsdt9 | 51637 | MLE 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516401 | lsdt9 | 51640 | ICP 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516411 | lsdt9 | 51641 | SLO 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1333 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516431 | lsdt9 | 51643 | SLO 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516961 | lsdt9 | 51696 | MGP 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516971 | lsdt9 | 51697 | NWP 13A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516981 | lsdt9 | 51698 | NWP 13B | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517181 | lsdt9 | 51718 | CFE 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517191 | lsdt9 | 51719 | AWT 12T4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517201 | lsdt9 | 51720 | AWT 12T2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517391 | lsdt9 | 51739 | CBP 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517721 | lsdt9 | 51772 | PGP 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517731 | lsdt9 | 51773 | GBR 4T1 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1333 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517821 | lsdt9 | 51782 | MTP 4T2 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517841 | lsdt9 | 51784 | GBR 4T2 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1333 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
518031 | lsdt9 | 51803 | TII 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
520351 | lsdt9 | 52035 | SUB11 63 | 63 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
520662 | lsdt9 | 52066 | SUB13 13A | 13.8 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
525971 | lsdt9 | 52597 | ROX 63 | 63 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526041 | lsdt9 | 52604 | DGB13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526051 | lsdt9 | 52605 | RUC 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526061 | lsdt9 | 52606 | SEX 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526071 | lsdt9 | 52607 | GLE 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526081 | lsdt9 | 52608 | REC 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526091 | lsdt9 | 52609 | SAU 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526111 | lsdt9 | 52611 | STC 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526131 | lsdt9 | 52613 | HOL 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526141 | lsdt9 | 52614 | OKM 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526231 | lsdt9 | 52623 | PRI 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526241 | lsdt9 | 52624 | KET 25 | 25 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526321 | lsdt9 | 52632 | RGA 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526461 | lsdt9 | 52646 | NKM 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526471 | lsdt9 | 52647 | PIN 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526481 | lsdt9 | 52648 | OSO 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526491 | lsdt9 | 52649 | HUT13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526501 | lsdt9 | 52650 | AWA 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526511 | lsdt9 | 52651 | WES 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526541 | lsdt9 | 52654 | SUM 8 | 8.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526551 | lsdt9 | 52655 | TRC 8 | 8.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526561 | lsdt9 | 52656 | WEB 8 | 8.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526631 | lsdt9 | 52663 | WAT 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526931 | lsdt9 | 52693 | BLK 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526941 | lsdt9 | 52694 | BEV 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
527041 | lsdt9 | 52704 | CHR 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
527081 | lsdt9 | 52708 | CRE 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
527091 | lsdt9 | 52709 | AAL 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
527221 | lsdt9 | 52722 | GLM 13 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.067 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5400299 | lsdt9 | 54002 | MAYERTH | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5400399 | lsdt9 | 54003 | COLINTO7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5400499 | lsdt9 | 54004 | WESTLOC7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5400599 | lsdt9 | 54005 | CLYDE 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5400799 | lsdt9 | 54007 | BOYLE 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5400899 | lsdt9 | 54008 | WHI 3647 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5400999 | lsdt9 | 54009 | WHITECO7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5401599 | lsdt9 | 54015 | MTN COA7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5403599 | lsdt9 | 54035 | LODGEPO7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5404099 | lsdt9 | 54040 | N CALDE7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 0.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5404299 | lsdt9 | 54042 | AMOCO BR | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5404499 | lsdt9 | 54044 | FT ASBN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.3 | 15 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5404499 | lsdt9 | 54044 | FT ASBN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5404799 | lsdt9 | 54047 | SHERWOO7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 0.8795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5404999 | lsdt9 | 54049 | KEYSTON7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5405999 | lsdt9 | 54059 | REDWATE7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5406799 | lsdt9 | 54067 | BRUDERH7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 60 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5406799 | lsdt9 | 54067 | BRUDERH7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5406899 | lsdt9 | 54068 | N HOLDE7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407099 | lsdt9 | 54070 | CAMROSE7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 0.8664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407299 | lsdt9 | 54072 | JARROW 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407399 | lsdt9 | 54073 | HARDIST7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 0.9312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407499 | lsdt9 | 54074 | METIS647 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.3 | 15 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407499 | lsdt9 | 54074 | METIS647 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407599 | lsdt9 | 54075 | HUGHEND7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 60 | 0.08 | 0.6601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407599 | lsdt9 | 54075 | HUGHEND7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.6601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407999 | lsdt9 | 54079 | BUFFALO7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.3 | 15 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5407999 | lsdt9 | 54079 | BUFFALO7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5408999 | lsdt9 | 54089 | E EDMON7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 0.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5409199 | lsdt9 | 54091 | NISKU 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 0.7875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5409399 | lsdt9 | 54093 | WETASKI7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5409499 | lsdt9 | 54094 | ERVICK 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5409599 | lsdt9 | 54095 | PONOKA 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5409699 | lsdt9 | 54096 | DEVON 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5409899 | lsdt9 | 54098 | RIMBEY 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 0.7758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5409999 | lsdt9 | 54099 | BENALTO7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5410099 | lsdt9 | 54100 | ROCKY M7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5410199 | lsdt9 | 54101 | COOKING7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5410799 | lsdt9 | 54107 | SUNDRE 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 0.7681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5411399 | lsdt9 | 54113 | BLACKFA7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.8897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5411599 | lsdt9 | 54115 | S RED DE | 138 | 99 | [6 empty] | : | #9 | 0.101 | 0 | 59.5 | 30 | 0.035 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5411599 | lsdt9 | 54115 | S RED DE | 138 | 99 | [6 empty] | : | #9 | 0.102 | 0 | 59.3 | 15 | 0.083 | 0.016 | 58.7 | 0 | 0.032 | 0.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5411799 | lsdt9 | 54117 | RED DE A | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5411999 | lsdt9 | 54119 | N RED D7 | 138 | 99 | [6 empty] | : | #9 | 0.101 | 0 | 59.5 | 30 | 0.035 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5411999 | lsdt9 | 54119 | N RED D7 | 138 | 99 | [6 empty] | : | #9 | 0.102 | 0 | 59.3 | 15 | 0.083 | 0.04 | 58.7 | 0 | 0.032 | 0.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5412199 | lsdt9 | 54121 | OLDS 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 0.8635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5414499 | lsdt9 | 54144 | ALGAR 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5414499 | lsdt9 | 54144 | ALGAR 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5417099 | lsdt9 | 54170 | COCHRAN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5417999 | lsdt9 | 54179 | MARIANA7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5420999 | lsdt9 | 54209 | BRETONA1 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.3 | 15 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5420999 | lsdt9 | 54209 | BRETONA1 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5422099 | lsdt9 | 54220 | HAYTER 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5423299 | lsdt9 | 54232 | COLEMAN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5423799 | lsdt9 | 54237 | FORT MA7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 0.5726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5423999 | lsdt9 | 54239 | OKOTOKS7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5424299 | lsdt9 | 54242 | HIGH RI7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.3 | 15 | 0.08 | 0.9499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5424299 | lsdt9 | 54242 | HIGH RI7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 0.9499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5425099 | lsdt9 | 54250 | DUCHESS7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5425499 | lsdt9 | 54254 | GLEICHE7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5425999 | lsdt9 | 54259 | STRATHM7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5427299 | lsdt9 | 54272 | TABER 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5427599 | lsdt9 | 54275 | TILLEY 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 30 | 0.08 | 0.4214 | 58 | 0 | 0.08 | 0.4214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5428399 | lsdt9 | 54283 | CANMORE7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5430499 | lsdt9 | 54304 | PLAMOND7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5431299 | lsdt9 | 54312 | E CROSS7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5432399 | lsdt9 | 54323 | CADOMIN8 | 69 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5433199 | lsdt9 | 54331 | VIOL GR7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 0.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5435799 | lsdt9 | 54357 | STALBE7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5436099 | lsdt9 | 54360 | STONY P7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 0.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5436399 | lsdt9 | 54363 | NW CARD7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5436599 | lsdt9 | 54365 | BUFORD 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5438599 | lsdt9 | 54385 | SHELL SC | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5438699 | lsdt9 | 54386 | SHELL EA | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5439799 | lsdt9 | 54397 | PINEDAL7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 60 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5439799 | lsdt9 | 54397 | PINEDAL7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5439999 | lsdt9 | 54399 | BASSAN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 30 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5439999 | lsdt9 | 54399 | BASSAN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5440199 | lsdt9 | 54401 | HAYS 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5441199 | lsdt9 | 54411 | CHEV KG7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 0.659 | 58.3 | 0 | 0.08 | 0.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5441299 | lsdt9 | 54412 | BENBOW 7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5441799 | lsdt9 | 54417 | WAUP1 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5442899 | lsdt9 | 54428 | SG_B1 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5445999 | lsdt9 | 54459 | ROSEVAL1 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5446599 | lsdt9 | 54465 | TL138 | 138 | 99 | [6 empty] | : | #9 | 0.101 | 0 | 59.5 | 30 | 0.035 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5446599 | lsdt9 | 54465 | TL138 | 138 | 99 | [6 empty] | : | #9 | 0.102 | 0 | 59.3 | 15 | 0.083 | 0.079 | 58.7 | 0 | 0.032 | 0.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5448899 | lsdt9 | 54488 | CHERHIL1 | 240 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5450299 | lsdt9 | 54502 | HARDIST8 | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.173 | 0.055 | 59.1 | 0 | 0.173 | 0.085 | 58.7 | 0 | 0.173 | 0.37 | 58.5 | 0 | 0.173 | 0.057 | 58 | 0 | 0.173 | 0.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5450599 | lsdt9 | 54505 | JASPER 4 | 240 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 60 | 0.173 | 0.044 | 58.9 | 0 | 0.173 | 0.115 | 58.5 | 0 | 0.173 | 0.146 | 58.3 | 0 | 0.173 | 0.053 | 58.1 | 0 | 0.173 | 0.167 | 58 | 0 | 0.173 | 0.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5451199 | lsdt9 | 54511 | SUMMERS1 | 240 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 60 | 0.173 | 0.274 | 58.9 | 0 | 0.173 | 0.161 | 58 | 0 | 0.173 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5451399 | lsdt9 | 54513 | LAMBTON4 | 240 | 99 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0 | 0.173 | 0.177 | 58.5 | 0 | 0.173 | 0.256 | 58.3 | 0 | 0.173 | 0.116 | 58.1 | 0 | 0.173 | 0.071 | 58 | 0 | 0.173 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5451999 | lsdt9 | 54519 | CASTLEDN | 240 | 99 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0 | 0.173 | 0.105 | 58.5 | 0 | 0.173 | 0.138 | 58.3 | 0 | 0.173 | 0.152 | 58.1 | 0 | 0.173 | 0.326 | 58 | 0 | 0.173 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5452199 | lsdt9 | 54521 | PETROLIA | 240 | 99 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0 | 0.173 | 0.179 | 58.7 | 0 | 0.173 | 0.208 | 58.5 | 0 | 0.173 | 0.068 | 58.3 | 0 | 0.173 | 0.153 | 58.1 | 0 | 0.173 | 0.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5452399 | lsdt9 | 54523 | MEADOWL2 | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0 | 0.173 | 0.236 | 58.5 | 0 | 0.173 | 0.163 | 58.3 | 0 | 0.173 | 0.081 | 58.1 | 0 | 0.173 | 0.047 | 58 | 0 | 0.173 | 0.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5452899 | lsdt9 | 54528 | KENNDALE | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0 | 0.173 | 0.238 | 58.7 | 0 | 0.173 | 0.069 | 58.3 | 0 | 0.173 | 0.279 | 58 | 0 | 0.173 | 0.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5452999 | lsdt9 | 54529 | MEADOWL1 | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0 | 0.173 | 0.236 | 58.5 | 0 | 0.173 | 0.163 | 58.3 | 0 | 0.173 | 0.081 | 58.1 | 0 | 0.173 | 0.047 | 58 | 0 | 0.173 | 0.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5453099 | lsdt9 | 54530 | NAMAO 8 | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0 | 0.173 | 0.285 | 58.7 | 0 | 0.173 | 0.202 | 58.3 | 0 | 0.173 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5453299 | lsdt9 | 54532 | STRACONA | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0 | 0.173 | 0.218 | 58.7 | 0 | 0.173 | 0.338 | 58.3 | 0 | 0.173 | 0.075 | 58 | 0 | 0.173 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5453399 | lsdt9 | 54533 | VIC_1 | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.173 | 0.14 | 59.1 | 0 | 0.173 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5453499 | lsdt9 | 54534 | WOODCRF1 | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.173 | 0.119 | 59.3 | 15 | 0.173 | 0.191 | 59.1 | 0 | 0.173 | 0.109 | 58.7 | 0 | 0.173 | 0.127 | 58 | 0 | 0.173 | 0.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5453999 | lsdt9 | 54539 | WOOD 2 | 14.4 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.173 | 0.119 | 59.3 | 15 | 0.173 | 0.191 | 59.1 | 0 | 0.173 | 0.109 | 58.7 | 0 | 0.173 | 0.127 | 58 | 0 | 0.173 | 0.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5454899 | lsdt9 | 54548 | ENMX10S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.389 | 58.3 | 0 | 0.065 | 0.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455099 | lsdt9 | 54550 | ENMX22S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.066 | 58.7 | 0 | 0.065 | 0.154 | 58.3 | 0 | 0.065 | 0.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455199 | lsdt9 | 54551 | ENMX28S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.5 | 0 | 0.065 | 0.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455299 | lsdt9 | 54552 | ENMX21S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.235 | 58.7 | 0 | 0.065 | 0.455 | 58 | 0 | 0.065 | 0.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455499 | lsdt9 | 54554 | ENMX15S8 | 69 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.1 | 0 | 0.065 | 0.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455599 | lsdt9 | 54555 | ENMX14S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.7 | 0 | 0.065 | 0.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455699 | lsdt9 | 54556 | ENMX34S8 | 69 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.1 | 0 | 0.065 | 0.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455799 | lsdt9 | 54557 | ENMX16S8 | 69 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.09 | 58.7 | 0 | 0.065 | 0.155 | 58 | 0 | 0.065 | 0.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455899 | lsdt9 | 54558 | ENMX27S8 | 69 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.341 | 58.3 | 0 | 0.065 | 0.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5455999 | lsdt9 | 54559 | ENMX13S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.163 | 58.9 | 0 | 0.065 | 0.066 | 58.5 | 0 | 0.065 | 0.374 | 58 | 0 | 0.065 | 0.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5456199 | lsdt9 | 54561 | ENMX11S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.3 | 0 | 0.065 | 0.307 | 58 | 0 | 0.065 | 0.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5456499 | lsdt9 | 54564 | ENMX36S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.256 | 58.9 | 0 | 0.065 | 0.106 | 58.1 | 0 | 0.065 | 0.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5456699 | lsdt9 | 54566 | ENMX20S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.5 | 0 | 0.065 | 0.187 | 58.3 | 0 | 0.065 | 0.103 | 58.1 | 0 | 0.065 | 0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457199 | lsdt9 | 54571 | ENMX43S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.5 | 0 | 0.065 | 0.369 | 58.3 | 0 | 0.065 | 0.126 | 58.1 | 0 | 0.065 | 0.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457299 | lsdt9 | 54572 | ENMX39S7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457299 | lsdt9 | 54572 | ENMX39S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.232 | 58.7 | 0 | 0.065 | 0.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457399 | lsdt9 | 54573 | ENMX38S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457399 | lsdt9 | 54573 | ENMX38S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457399 | lsdt9 | 54573 | ENMX38S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457399 | lsdt9 | 54573 | ENMX38S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.7 | 0 | 0.065 | 0.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457399 | lsdt9 | 54573 | ENMX38S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.1 | 0 | 0.065 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457399 | lsdt9 | 54573 | ENMX38S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58 | 0 | 0.065 | 0.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457499 | lsdt9 | 54574 | ENMX37S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 30 | 0.065 | 0.103 | 59.1 | 0 | 0.065 | 0.201 | 58.7 | 0 | 0.065 | 0.109 | 58.1 | 0 | 0.065 | 0.477 | 58 | 0 | 0.065 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457799 | lsdt9 | 54577 | ENMX23S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.293 | 58.9 | 0 | 0.065 | 0.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5457999 | lsdt9 | 54579 | ENMX31S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.434 | 58.9 | 0 | 0.065 | 0.081 | 58.5 | 0 | 0.065 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5458399 | lsdt9 | 54583 | ENMX32S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.5 | 0 | 0.065 | 0.072 | 58.3 | 0 | 0.065 | 0.304 | 58 | 0 | 0.065 | 0.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5458599 | lsdt9 | 54585 | ENMX9S 7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.059 | 59.1 | 0 | 0.065 | 0.197 | 58.7 | 0 | 0.065 | 0.108 | 58.5 | 0 | 0.065 | 0.22 | 58.1 | 0 | 0.065 | 0.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5458799 | lsdt9 | 54587 | ENMX6S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.177 | 58.1 | 0 | 0.065 | 0.429 | 58 | 0 | 0.065 | 0.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5458999 | lsdt9 | 54589 | ENMX26S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 30 | 0.065 | 0.255 | 59.1 | 0 | 0.065 | 0.171 | 58.1 | 0 | 0.065 | 0.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459099 | lsdt9 | 54590 | ENMX24S7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459099 | lsdt9 | 54590 | ENMX24S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 30 | 0.065 | 0.087 | 58.9 | 0 | 0.065 | 0.161 | 58.5 | 0 | 0.065 | 0.163 | 58.3 | 0 | 0.065 | 0.228 | 58 | 0 | 0.065 | 0.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459199 | lsdt9 | 54591 | ENMX40S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.105 | 58.7 | 0 | 0.065 | 0.176 | 58.3 | 0 | 0.065 | 0.151 | 58.1 | 0 | 0.065 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459299 | lsdt9 | 54592 | ENMX41S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.184 | 58.9 | 0 | 0.065 | 0.211 | 58.5 | 0 | 0.065 | 0.098 | 58.1 | 0 | 0.065 | 0.234 | 58 | 0 | 0.065 | 0.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459499 | lsdt9 | 54594 | ENMX33S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.127 | 59.1 | 0 | 0.065 | 0.19 | 58.7 | 0 | 0.065 | 0.183 | 58.5 | 0 | 0.065 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459699 | lsdt9 | 54596 | ENMX7S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459699 | lsdt9 | 54596 | ENMX7S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5459699 | lsdt9 | 54596 | ENMX7S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58 | 0 | 0.065 | 0.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5460099 | lsdt9 | 54600 | ENMAXGIS | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5460099 | lsdt9 | 54600 | ENMAXGIS | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5460099 | lsdt9 | 54600 | ENMAXGIS | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5460099 | lsdt9 | 54600 | ENMAXGIS | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.7 | 0 | 0.065 | 0.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5460099 | lsdt9 | 54600 | ENMAXGIS | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.1 | 0 | 0.065 | 0.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5460099 | lsdt9 | 54600 | ENMAXGIS | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58 | 0 | 0.065 | 0.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5466499 | lsdt9 | 54664 | PIPER CR | 138 | 99 | [6 empty] | : | #9 | 0.101 | 0 | 59.5 | 30 | 0.035 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5466499 | lsdt9 | 54664 | PIPER CR | 138 | 99 | [6 empty] | : | #9 | 0.102 | 0 | 59.3 | 15 | 0.083 | 0.051 | 58.7 | 0 | 0.032 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5467899 | lsdt9 | 54678 | DEERH7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5469199 | lsdt9 | 54691 | LETH241S | 138 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0 | 0.1 | 0.135 | 58.1 | 0 | 0.1 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5469799 | lsdt9 | 54697 | LETH593S | 138 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0 | 0.1 | 0.194 | 58.5 | 0 | 0.1 | 0.107 | 58 | 0 | 0.1 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5469999 | lsdt9 | 54699 | RIVERBN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 30 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5469999 | lsdt9 | 54699 | RIVERBN7 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5471899 | lsdt9 | 54718 | WESWOOD | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5478099 | lsdt9 | 54780 | SYLV_138 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 60 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5478099 | lsdt9 | 54780 | SYLV_138 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5482099 | lsdt9 | 54820 | FICKL TP | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5495599 | lsdt9 | 54955 | PDMAKER1 | 240 | 99 | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0 | 0.173 | 0.063 | 58.3 | 0 | 0.173 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5502299 | lsdt9 | 55022 | BLUMNOR7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.606 | 58 | 0 | 0.045 | 0.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5502899 | lsdt9 | 55028 | RBW LAK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5502899 | lsdt9 | 55028 | RBW LAK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5502899 | lsdt9 | 55028 | RBW LAK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5503199 | lsdt9 | 55031 | RBW 1 | 13.8 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5503199 | lsdt9 | 55031 | RBW 1 | 13.8 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5503199 | lsdt9 | 55031 | RBW 1 | 13.8 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5503299 | lsdt9 | 55032 | RBW 2 | 13.8 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5503299 | lsdt9 | 55032 | RBW 2 | 13.8 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5503299 | lsdt9 | 55032 | RBW 2 | 13.8 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5505399 | lsdt9 | 55053 | RING CK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5507099 | lsdt9 | 55070 | CRANBER7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5507599 | lsdt9 | 55075 | SEAL LK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 0.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5507599 | lsdt9 | 55075 | SEAL LK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5507599 | lsdt9 | 55075 | SEAL LK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5507599 | lsdt9 | 55075 | SEAL LK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 0.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5508599 | lsdt9 | 55085 | PEACE RV | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5509899 | lsdt9 | 55098 | RIMBEY10 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 0.7758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5510099 | lsdt9 | 55100 | RYCROFT7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.351 | 58.3 | 0 | 0.045 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5510499 | lsdt9 | 55104 | KSIT RV7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 0.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5510899 | lsdt9 | 55108 | EUREKA 8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5510999 | lsdt9 | 55109 | MERCER 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.41 | 58.3 | 0 | 0.045 | 0.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5511899 | lsdt9 | 55118 | POPLAR 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 0.439 | 58.1 | 0 | 0.045 | 0.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5511999 | lsdt9 | 55119 | GOODFAR7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5512199 | lsdt9 | 55121 | CRYST L7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.115 | 58.3 | 0 | 0.045 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5512699 | lsdt9 | 55126 | FLYINGS7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5512699 | lsdt9 | 55126 | FLYINGS7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5512699 | lsdt9 | 55126 | FLYINGS7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 0.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5513099 | lsdt9 | 55130 | MUIR-HV | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 0.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5513099 | lsdt9 | 55130 | MUIR-HV | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5513099 | lsdt9 | 55130 | MUIR-HV | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 0.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5515099 | lsdt9 | 55150 | DONNELL7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.406 | 58.1 | 0 | 0.045 | 0.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5515599 | lsdt9 | 55155 | VALLEYV7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5517599 | lsdt9 | 55175 | FOX CRK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5517599 | lsdt9 | 55175 | FOX CRK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5517599 | lsdt9 | 55175 | FOX CRK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5517599 | lsdt9 | 55175 | FOX CRK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 0.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5522632 | lsdt9 | 55226 | WABASCA4 | 240 | 32 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.276 | 58.9 | 0 | 0.045 | 0.046 | 58.5 | 0 | 0.045 | 0.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5522633 | lsdt9 | 55226 | WABASCA4 | 240 | 33 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.276 | 58.9 | 0 | 0.045 | 0.046 | 58.5 | 0 | 0.045 | 0.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5522699 | lsdt9 | 55226 | WABASCA4 | 240 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.276 | 58.9 | 0 | 0.045 | 0.046 | 58.5 | 0 | 0.045 | 0.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5522799 | lsdt9 | 55227 | CROWLK7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5523432 | lsdt9 | 55234 | OTAUWAU7 | 138 | 32 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.245 | 58.3 | 0 | 0.045 | 0.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5523433 | lsdt9 | 55234 | OTAUWAU7 | 138 | 33 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.245 | 58.3 | 0 | 0.045 | 0.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5523499 | lsdt9 | 55234 | OTAUWAU7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.245 | 58.3 | 0 | 0.045 | 0.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5524499 | lsdt9 | 55244 | EDITH L8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 0.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5524499 | lsdt9 | 55244 | EDITH L8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5524499 | lsdt9 | 55244 | EDITH L8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5524499 | lsdt9 | 55244 | EDITH L8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5524499 | lsdt9 | 55244 | EDITH L8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 0.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5524599 | lsdt9 | 55245 | KINOSIS1 | 240 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.558 | 58.7 | 0 | 0.045 | 0.09 | 58.5 | 0 | 0.045 | 0.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5524699 | lsdt9 | 55246 | SPRING10 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5526399 | lsdt9 | 55263 | JOSLYN4 | 240 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5526699 | lsdt9 | 55266 | SARAH L7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5527199 | lsdt9 | 55271 | MORSE RV | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5527299 | lsdt9 | 55272 | FIELDGA7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.341 | 58.7 | 0 | 0.045 | 0.326 | 58 | 0 | 0.045 | 0.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5527599 | lsdt9 | 55275 | VIRGINI7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 0.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5527599 | lsdt9 | 55275 | VIRGINI7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 0.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5527699 | lsdt9 | 55276 | S-SHINE1 | 240 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.206 | 58.3 | 0 | 0.045 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5527899 | lsdt9 | 55278 | KINUSO 8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5528099 | lsdt9 | 55280 | BRINT02 | 240 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.741 | 58.9 | 0 | 0.045 | 0.148 | 58.7 | 0 | 0.045 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5528599 | lsdt9 | 55285 | NIPISI 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5528699 | lsdt9 | 55286 | S-SHINE4 | 240 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.206 | 58.3 | 0 | 0.045 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5531499 | lsdt9 | 55314 | BRIKER1 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5533299 | lsdt9 | 55332 | GRND CTR | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5534499 | lsdt9 | 55344 | BONNY 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.251 | 58.1 | 0 | 0.045 | 0.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5534599 | lsdt9 | 55345 | SEC 605T | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.251 | 58.1 | 0 | 0.045 | 0.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5536299 | lsdt9 | 55362 | WILLING2 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5536499 | lsdt9 | 55364 | CARVEL01 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 0.4956 | 58.5 | 0 | 0.08 | 0.5044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5536699 | lsdt9 | 55366 | VISCOUNT | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5537799 | lsdt9 | 55377 | IRISH C7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.107 | 58.9 | 0 | 0.045 | 0.095 | 58.7 | 0 | 0.045 | 0.086 | 58 | 0 | 0.045 | 0.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5538399 | lsdt9 | 55383 | VERMILO7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5539399 | lsdt9 | 55393 | HILL 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.097 | 58.9 | 0 | 0.045 | 0.522 | 58.1 | 0 | 0.045 | 0.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5540099 | lsdt9 | 55400 | HEISLER8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5540399 | lsdt9 | 55403 | PAINTRT4 | 240 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.769 | 58.3 | 0 | 0.045 | 0.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5540999 | lsdt9 | 55409 | QUIGL1 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 0.421 | 58 | 0 | 0.045 | 0.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5541199 | lsdt9 | 55411 | WADDELL7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5543399 | lsdt9 | 55433 | 3 HILLS7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5545599 | lsdt9 | 55455 | LLOYD 7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5546599 | lsdt9 | 55465 | CORONAT8 | 69 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5546899 | lsdt9 | 55468 | VETERAN7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5546899 | lsdt9 | 55468 | VETERAN7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5547199 | lsdt9 | 55471 | MONITOR7 | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5556999 | lsdt9 | 55569 | ENMX3S 7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.086 | 58.1 | 0 | 0.065 | 0.17 | 58 | 0 | 0.065 | 0.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5557699 | lsdt9 | 55576 | ENMX47S7 | 138 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 30 | 0.065 | 0.172 | 59.1 | 0 | 0.065 | 0.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5562299 | lsdt9 | 55622 | TWR_RD2 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5563099 | lsdt9 | 55630 | BULLPON9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5583999 | lsdt9 | 55839 | OKOTOKS6 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5595499 | lsdt9 | 55954 | 768S_HV | 138 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.492 | 58.3 | 0 | 0.045 | 0.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5619899 | lsdt9 | 56198 | BALZACA8 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 0.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5622499 | lsdt9 | 56224 | HANGSTO1 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5623999 | lsdt9 | 56239 | OKOTOKS8 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5627299 | lsdt9 | 56272 | TABER A9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 0.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5628099 | lsdt9 | 56280 | STIRLIN9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5638899 | lsdt9 | 56388 | KITSCOT9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5656199 | lsdt9 | 56561 | ENMX11C9 | 26 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.3 | 0 | 0.065 | 0.307 | 58 | 0 | 0.065 | 0.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5669099 | lsdt9 | 56690 | COALDAL8 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5701737 | lsdt9 | 57017 | COLD CA9 | 25 | 37 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5711899 | lsdt9 | 57118 | POPLAR 3 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 0.439 | 58.1 | 0 | 0.045 | 0.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5722499 | lsdt9 | 57224 | HANGSTO9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5724399 | lsdt9 | 57243 | HOME OIL | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 0.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5724399 | lsdt9 | 57243 | HOME OIL | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.3 | 15 | 0.045 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5724399 | lsdt9 | 57243 | HOME OIL | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5724399 | lsdt9 | 57243 | HOME OIL | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5724399 | lsdt9 | 57243 | HOME OIL | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 0.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5728699 | lsdt9 | 57286 | ENCHANT8 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5735999 | lsdt9 | 57359 | ACHESON3 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 0.6853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5735999 | lsdt9 | 57359 | ACHESON3 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5739399 | lsdt9 | 57393 | HILL | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.097 | 58.9 | 0 | 0.045 | 0.522 | 58.1 | 0 | 0.045 | 0.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5742399 | lsdt9 | 57423 | NEVIS 9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5744999 | lsdt9 | 57449 | MICH. C9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5747199 | lsdt9 | 57471 | MONITOR9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5757499 | lsdt9 | 57574 | NILREM5 | 138 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5759699 | lsdt9 | 57596 | ENMX7S8 | 26 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5759699 | lsdt9 | 57596 | ENMX7S8 | 26 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5759699 | lsdt9 | 57596 | ENMX7S8 | 26 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58 | 0 | 0.065 | 0.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5767999 | lsdt9 | 57679 | LETH111B | 13.8 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.1 | 0.112 | 59.5 | 60 | 0.1 | 0.075 | 59.1 | 0 | 0.1 | 0.288 | 58.9 | 0 | 0.1 | 0.144 | 58.7 | 0 | 0.1 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5769799 | lsdt9 | 57697 | LTH593S1 | 13.8 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0 | 0.1 | 0.194 | 58.5 | 0 | 0.1 | 0.107 | 58 | 0 | 0.1 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5801737 | lsdt9 | 58017 | COLD CR9 | 25 | 37 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5802099 | lsdt9 | 58020 | HGHLVL/2 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5802099 | lsdt9 | 58020 | HGHLVL/2 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5802099 | lsdt9 | 58020 | HGHLVL/2 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 0.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5802599 | lsdt9 | 58025 | ENTWIST9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5803299 | lsdt9 | 58032 | ONOWAY 9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5804199 | lsdt9 | 58041 | N BARRH9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5807099 | lsdt9 | 58070 | GEN BUS | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 0.8664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5807899 | lsdt9 | 58078 | SEDGEWI9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5810599 | lsdt9 | 58105 | PIGEON 9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.9 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5817799 | lsdt9 | 58177 | AIRDRIE9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 60 | 0.08 | 0.214 | 58 | 0 | 0.08 | 0.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5817899 | lsdt9 | 58178 | AIRDRIE8 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 60 | 0.08 | 0.214 | 58 | 0 | 0.08 | 0.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5818399 | lsdt9 | 58183 | BEARSPWA | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5819899 | lsdt9 | 58198 | BALZACA9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 0.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5820199 | lsdt9 | 58201 | SPLIT-53 | 69 | 99 | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0 | 0.173 | 0.218 | 58.7 | 0 | 0.173 | 0.338 | 58.3 | 0 | 0.173 | 0.075 | 58 | 0 | 0.173 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5822299 | lsdt9 | 58222 | HAYTER19 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5823599 | lsdt9 | 58235 | STAVELY9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5823899 | lsdt9 | 58238 | BLACK D9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5824199 | lsdt9 | 58241 | BLACK D1 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5824699 | lsdt9 | 58246 | SPRING 9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5825699 | lsdt9 | 58256 | BROOKS 9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5826099 | lsdt9 | 58260 | JENNERC9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5827499 | lsdt9 | 58274 | VAUXHAL9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5827599 | lsdt9 | 58275 | TILLEY 9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.5 | 30 | 0.08 | 0.4214 | 58 | 0 | 0.08 | 0.4214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5827699 | lsdt9 | 58276 | W BROOK9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5828699 | lsdt9 | 58286 | ENCHANT9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5830499 | lsdt9 | 58304 | PLAMOND9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5833199 | lsdt9 | 58331 | VIOL GR9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 0.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5835999 | lsdt9 | 58359 | ACHESON9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 0.6853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5835999 | lsdt9 | 58359 | ACHESON9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5836199 | lsdt9 | 58361 | EDGERTO9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5840199 | lsdt9 | 58401 | HAYS 9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 59.1 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5855299 | lsdt9 | 58552 | ENMX21S9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.235 | 58.7 | 0 | 0.065 | 0.455 | 58 | 0 | 0.065 | 0.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5855699 | lsdt9 | 58556 | ENMX34C9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.1 | 0 | 0.065 | 0.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5856199 | lsdt9 | 58561 | ENMX11S9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.3 | 0 | 0.065 | 0.307 | 58 | 0 | 0.065 | 0.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5856499 | lsdt9 | 58564 | ENMX36S9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.256 | 58.9 | 0 | 0.065 | 0.106 | 58.1 | 0 | 0.065 | 0.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5857199 | lsdt9 | 58571 | ENMX43C9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.5 | 0 | 0.065 | 0.369 | 58.3 | 0 | 0.065 | 0.126 | 58.1 | 0 | 0.065 | 0.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5857699 | lsdt9 | 58576 | ENMX47S9 | 26 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 30 | 0.065 | 0.172 | 59.1 | 0 | 0.065 | 0.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5858199 | lsdt9 | 58581 | ENMX12S9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5859499 | lsdt9 | 58594 | ENMX33S9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.127 | 59.1 | 0 | 0.065 | 0.19 | 58.7 | 0 | 0.065 | 0.183 | 58.5 | 0 | 0.065 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5867999 | lsdt9 | 58679 | LETH111C | 13.8 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.1 | 0.112 | 59.5 | 60 | 0.1 | 0.075 | 59.1 | 0 | 0.1 | 0.288 | 58.9 | 0 | 0.1 | 0.144 | 58.7 | 0 | 0.1 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5869299 | lsdt9 | 58692 | N LETHB9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.3 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5869899 | lsdt9 | 58698 | LTH674S1 | 13.8 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.1 | 0.216 | 58.7 | 0 | 0.1 | 0.113 | 58.1 | 0 | 0.1 | 0.234 | 58 | 0 | 0.1 | 0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5896099 | lsdt9 | 58960 | JENNERA9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5898631 | lsdt9 | 58986 | JENNERD9 | 25 | 31 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5899599 | lsdt9 | 58995 | ENMX2S99 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5899599 | lsdt9 | 58995 | ENMX2S99 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5899599 | lsdt9 | 58995 | ENMX2S99 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5899599 | lsdt9 | 58995 | ENMX2S99 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.7 | 0 | 0.065 | 0.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5899599 | lsdt9 | 58995 | ENMX2S99 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.1 | 0 | 0.065 | 0.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5899599 | lsdt9 | 58995 | ENMX2S99 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58 | 0 | 0.065 | 0.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5902099 | lsdt9 | 59020 | HGHLVL/1 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 60 | 0.045 | 0.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5902099 | lsdt9 | 59020 | HGHLVL/1 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5902099 | lsdt9 | 59020 | HGHLVL/1 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 0.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5904099 | lsdt9 | 59040 | N CALDA9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.7 | 0 | 0.08 | 0.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5905099 | lsdt9 | 59050 | HOTCHKS9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5910599 | lsdt9 | 59105 | FRIEDEN9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 0.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5910799 | lsdt9 | 59107 | HINES C9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.3 | 0 | 0.045 | 0.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5913499 | lsdt9 | 59134 | ELMWORT9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.352 | 58.3 | 0 | 0.045 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5914599 | lsdt9 | 59145 | BRDGE C9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.513 | 58.5 | 0 | 0.045 | 0.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5917099 | lsdt9 | 59170 | STURGE10 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.5 | 30 | 0.045 | 0.204 | 58.9 | 0 | 0.045 | 0.259 | 58.1 | 0 | 0.045 | 0.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5920199 | lsdt9 | 59201 | RUTH LK9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5922299 | lsdt9 | 59222 | PARS CR9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 59.1 | 0 | 0.045 | 0.211 | 58.9 | 0 | 0.045 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5925999 | lsdt9 | 59259 | STRATHM2 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58.5 | 0 | 0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5926699 | lsdt9 | 59266 | SARHLK/1 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5928199 | lsdt9 | 59281 | SLAVE L9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5932137 | lsdt9 | 59321 | ETHEL L9 | 25 | 37 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5932199 | lsdt9 | 59321 | ETHEL L9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5937199 | lsdt9 | 59371 | ST. PAU9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5938399 | lsdt9 | 59383 | VERMILA9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.5 | 0 | 0.045 | 0.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5943999 | lsdt9 | 59439 | STETTLE9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5944999 | lsdt9 | 59449 | MICH.C19 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5947499 | lsdt9 | 59474 | OYEN 9 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.9 | 0 | 0.045 | 0.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5955899 | lsdt9 | 59558 | ENMX2799 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.341 | 58.3 | 0 | 0.065 | 0.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5956199 | lsdt9 | 59561 | ENMX11B9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.3 | 0 | 0.065 | 0.307 | 58 | 0 | 0.065 | 0.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5957399 | lsdt9 | 59573 | ENMX38B9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.5 | 60 | 0.065 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5957399 | lsdt9 | 59573 | ENMX38B9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.3 | 15 | 0.065 | 0.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5957399 | lsdt9 | 59573 | ENMX38B9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 59.1 | 0 | 0.065 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5957399 | lsdt9 | 59573 | ENMX38B9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.7 | 0 | 0.065 | 0.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5957399 | lsdt9 | 59573 | ENMX38B9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.1 | 0 | 0.065 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5957399 | lsdt9 | 59573 | ENMX38B9 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58 | 0 | 0.065 | 0.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5958199 | lsdt9 | 59581 | ENMX1299 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.9 | 0 | 0.065 | 0.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5960199 | lsdt9 | 59601 | RUTHLK10 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.1 | 0 | 0.045 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5967999 | lsdt9 | 59679 | LETH111A | 13.8 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.1 | 0.112 | 59.5 | 60 | 0.1 | 0.075 | 59.1 | 0 | 0.1 | 0.288 | 58.9 | 0 | 0.1 | 0.144 | 58.7 | 0 | 0.1 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5969199 | lsdt9 | 59691 | LTH241S2 | 13.8 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0 | 0.1 | 0.135 | 58.1 | 0 | 0.1 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5969899 | lsdt9 | 59698 | LTH674S2 | 13.8 | 99 | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.1 | 0.216 | 58.7 | 0 | 0.1 | 0.113 | 58.1 | 0 | 0.1 | 0.234 | 58 | 0 | 0.1 | 0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5977199 | lsdt9 | 59771 | ST. PAU6 | 25 | 99 | [6 empty] | : | #9 | 0.117 | 0 | 58.7 | 0 | 0.045 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5986099 | lsdt9 | 59860 | JENNERB9 | 25 | 99 | [6 empty] | : | #9 | 0.1 | 0 | 58 | 0 | 0.08 | 0.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5997199 | lsdt9 | 59971 | ENMX4399 | 13.8 | 99 | [6 empty] | : | #9 | 0.13 | 0 | 58.5 | 0 | 0.065 | 0.369 | 58.3 | 0 | 0.065 | 0.126 | 58.1 | 0 | 0.065 | 0.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600151 | lsdt9 | 60015 | ALAMEDA | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0.083 | 58.3 | 0 | 0.05 | 0.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600201 | lsdt9 | 60020 | AMFLS | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 0.37 | 59.3 | 15 | 0 | 0.23 | 59.1 | 0 | 0.05 | 0.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600301 | lsdt9 | 60030 | BLACKFT | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 0.02 | 59.5 | 30 | 0 | 0.052 | 59.3 | 15 | 0 | 0.026 | 58.9 | 0 | 0.05 | 0.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600401 | lsdt9 | 60040 | BOISEBCH | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 0.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600651 | lsdt9 | 60065 | BOMT_138 | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0 | 0.075 | 58.5 | 0 | 0.05 | 0.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601051 | lsdt9 | 60105 | CALDWELL | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 0.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601141 | lsdt9 | 60114 | NORTHVW | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601151 | lsdt9 | 60115 | CLIFF | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 0.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601201 | lsdt9 | 60120 | DALE | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0 | 0.4 | 58.3 | 0 | 0.05 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601351 | lsdt9 | 60135 | EDEN | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 0.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601401 | lsdt9 | 60140 | EMMETT | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 0.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601451 | lsdt9 | 60145 | FREMONT | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602111 | lsdt9 | 60211 | CHESTNUT | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602201 | lsdt9 | 60220 | MCCALL | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602501 | lsdt9 | 60250 | MT HOME | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602601 | lsdt9 | 60260 | ONTARIO | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602611 | lsdt9 | 60261 | ONTO-12.5 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602851 | lsdt9 | 60285 | PAUL | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602911 | lsdt9 | 60291 | PINGREE | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0 | 0.158 | 58.3 | 0 | 0.05 | 0.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603151 | lsdt9 | 60315 | SIPHON | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603152 | lsdt9 | 60315 | SIPHON | 138 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603451 | lsdt9 | 60345 | TWINFALL | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0 | 0.058 | 58.3 | 0 | 0.05 | 0.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60821N1 | lsdt9 | 60821 | IDAHOME | 138 | N1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610111 | lsdt9 | 61011 | CNCL | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 0.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610661 | lsdt9 | 61066 | PAYETTE | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0 | 0.686 | 59.1 | 0 | 0.05 | 0.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610811 | lsdt9 | 61081 | WEISER | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612031 | lsdt9 | 61203 | BLACKCAT | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612071 | lsdt9 | 61207 | BOISE | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 0.345 | 58.7 | 0 | 0.05 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612121 | lsdt9 | 61212 | BUTLER | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 0.161 | 58.3 | 0 | 0.05 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612131 | lsdt9 | 61213 | CALDWELL | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0 | 0.215 | 58.3 | 0 | 0.05 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612411 | lsdt9 | 61241 | GROVE | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0 | 0.096 | 58.7 | 0 | 0.05 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612441 | lsdt9 | 61244 | HILL | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612451 | lsdt9 | 61245 | HIDNSPGS | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612521 | lsdt9 | 61252 | LINDEN | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612541 | lsdt9 | 61254 | LOCUST | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612611 | lsdt9 | 61261 | MORA | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612612 | lsdt9 | 61261 | MORA | 138 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0 | 0.205 | 59.1 | 0 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612671 | lsdt9 | 61267 | SAILOR | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612771 | lsdt9 | 61277 | USTICK | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 0.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612791 | lsdt9 | 61279 | VICTORY | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 0.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614301 | lsdt9 | 61430 | DUFFIN | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0 | 0.502 | 58.7 | 0 | 0.05 | 0.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614302 | lsdt9 | 61430 | DUFFIN | 138 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614491 | lsdt9 | 61449 | HYDRA | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614531 | lsdt9 | 61453 | J CLAWSN | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614532 | lsdt9 | 61453 | J CLAWSN | 138 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614601 | lsdt9 | 61460 | KETCHUM | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 0.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
616381 | lsdt9 | 61638 | HAVN | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
616391 | lsdt9 | 61639 | HIGHLND | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617021 | lsdt9 | 61702 | CADA | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617081 | lsdt9 | 61708 | JOPLIN | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 0.112 | 58.5 | 0 | 0.05 | 0.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617091 | lsdt9 | 61709 | STOD | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.05 | 0.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617151 | lsdt9 | 61715 | STAR | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0 | 0.34 | 58.3 | 0 | 0.05 | 0.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617161 | lsdt9 | 61716 | BNLT | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617201 | lsdt9 | 61720 | TENMILE | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617211 | lsdt9 | 61721 | MIDROSE | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 0.549 | 59.5 | 30 | 0 | 0.206 | 59.3 | 15 | 0.05 | 0.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617371 | lsdt9 | 61737 | BOULDER | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618031 | lsdt9 | 61803 | BCRT | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618381 | lsdt9 | 61838 | LANSING | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 0.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618401 | lsdt9 | 61840 | MERIDIAN | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 0.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618421 | lsdt9 | 61842 | CART | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 0.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618431 | lsdt9 | 61843 | WILLIS | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0 | 0.222 | 58.5 | 0 | 0.05 | 0.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640011 | lsdt9 | 64001 | ADOBE | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64001N | lsdt9 | 64001 | ADOBE | 120 | N | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64001W1 | lsdt9 | 64001 | ADOBE | 120 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640031 | lsdt9 | 64003 | MASON | 63 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.15 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640032 | lsdt9 | 64003 | MASON | 63 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.15 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640221 | lsdt9 | 64022 | BUCKEYE | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640261 | lsdt9 | 64026 | CARSON | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 0.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640391 | lsdt9 | 64039 | EAGLE | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.15 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640392 | lsdt9 | 64039 | EAGLE | 120 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.15 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640651 | lsdt9 | 64065 | KING BCH | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 0.93341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640721 | lsdt9 | 64072 | MEYERS | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640831 | lsdt9 | 64083 | NORTHSTR | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 0.41472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640881 | lsdt9 | 64088 | OVERLAND | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 0.8285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640921 | lsdt9 | 64092 | RND HILL | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641011 | lsdt9 | 64101 | STATELIN | 63 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641021 | lsdt9 | 64102 | STATELIN | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641101 | lsdt9 | 64110 | TAHO CTY | 63 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 0.53385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641221 | lsdt9 | 64122 | TRUCKEE | 63 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 0.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641381 | lsdt9 | 64138 | WINN SUB | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641631 | lsdt9 | 64163 | SQAWVLY2 | 14.4 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641641 | lsdt9 | 64164 | SQAWVLY1 | 14.4 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 0.94365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642411 | lsdt9 | 64241 | PINENUT | 63 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642491 | lsdt9 | 64249 | AIRPORT | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 0.15179 | 59.1 | 0.1 | 0.05 | 0.34177 | 58.5 | 0.1 | 0.05 | 0.2454 | 57.65 | 0.1 | 0.05 | 0.2484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642501 | lsdt9 | 64250 | BELVISTA | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642531 | lsdt9 | 64253 | CAL SUB | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642561 | lsdt9 | 64256 | GLENDALE | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14.71 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642581 | lsdt9 | 64258 | GREGSTRT | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.15 | 0.1 | 0.05 | 0.67462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642601 | lsdt9 | 64260 | MT ROSE | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642611 | lsdt9 | 64261 | MIRA LMA LD | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 0.65514 | 57.65 | 0.1 | 0.05 | 0.34486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642621 | lsdt9 | 64262 | NORTHWST | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642631 | lsdt9 | 64263 | RENO | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.15 | 0.1 | 0.05 | 0.80659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642651 | lsdt9 | 64265 | RUSTY SP | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 0.27419 | 58.15 | 0.1 | 0.05 | 0.084677 | 57.65 | 0.1 | 0.05 | 0.64113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642661 | lsdt9 | 64266 | SILVRLK | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 30 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642681 | lsdt9 | 64268 | SPAN SPG | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642721 | lsdt9 | 64272 | STEAMBT | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 0.59252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642741 | lsdt9 | 64274 | VAL ROAD | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.65 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
643071 | lsdt9 | 64307 | MRKTWAIN | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644021 | lsdt9 | 64402 | SILVRLK2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 30 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644501 | lsdt9 | 64450 | EMERSON | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 0.36928 | 57.65 | 0.1 | 0.05 | 0.27364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644581 | lsdt9 | 64458 | LONELY | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645071 | lsdt9 | 64507 | FAIRVIEW | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645181 | lsdt9 | 64518 | SUGARLF | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647211 | lsdt9 | 64721 | FERNLEY | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647451 | lsdt9 | 64745 | PATRICK | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.65 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649371 | lsdt9 | 64937 | FTSAGELD | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.15 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649631 | lsdt9 | 64963 | CHUKAR | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.65 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650021 | lsdt9 | 65002 | 70TH SO | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650061 | lsdt9 | 65006 | ABAJO | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650161 | lsdt9 | 65016 | 118THSO1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650261 | lsdt9 | 65026 | AMPS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650411 | lsdt9 | 65041 | ANGEL | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.27 | 58.3 | 0.133 | 0.0833 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65166FM | lsdt9 | 65166 | BLACKSFK | 34.5 | FM | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65166TX | lsdt9 | 65166 | BLACKSFK | 34.5 | TX | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
652411 | lsdt9 | 65241 | BUTVILLE | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.7 | 58.3 | 0.133 | 0.0833 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653061 | lsdt9 | 65306 | CASPERPP | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653191 | lsdt9 | 65319 | REFNRY2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653561 | lsdt9 | 65356 | COLUMBIA | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653661 | lsdt9 | 65366 | COTTONWD | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.13 | 58.9 | 0.133 | 0.0833 | 0.28 | 58.7 | 0.133 | 0.0833 | 0.07 | 58.5 | 0.133 | 0.0833 | 0.3 | 58.3 | 0.133 | 0.0833 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654001 | lsdt9 | 65400 | CUTLER | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654261 | lsdt9 | 65426 | DAVEJOHN | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654461 | lsdt9 | 65446 | DC 15 | 13.19 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.26 | 59.5 | 60 | 0.0833 | 0.29 | 59.3 | 15 | 0.0833 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654731 | lsdt9 | 65473 | DUMAS 1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654741 | lsdt9 | 65474 | DUMAS 2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
655021 | lsdt9 | 65502 | ELAYTON1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
655061 | lsdt9 | 65506 | EL MONTE | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
655711 | lsdt9 | 65571 | FRANKLIN | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.17 | 58.7 | 0.133 | 0.0833 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
655951 | lsdt9 | 65595 | GADSBY | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.36 | 58.9 | 0.133 | 0.0833 | 0.27 | 58.7 | 0.133 | 0.0833 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656241 | lsdt9 | 65624 | GATEWAY | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656511 | lsdt9 | 65651 | GILLESPE | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.04 | 59.5 | 60 | 0.0833 | 0.19 | 59.3 | 15 | 0.0833 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656721 | lsdt9 | 65672 | GOSHEN | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657001 | lsdt9 | 65700 | GRACE | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.07 | 58.7 | 0.133 | 0.0833 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657361 | lsdt9 | 65736 | GREENCA | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.38 | 58.3 | 0.133 | 0.0833 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657431 | lsdt9 | 65743 | GV 15 | 13.19 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.83 | 58.3 | 0.133 | 0.0833 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657461 | lsdt9 | 65746 | HALE | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657661 | lsdt9 | 65766 | HILAND | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657671 | lsdt9 | 65767 | HILAND | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657771 | lsdt9 | 65777 | HILLSIDE | 13.19 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
658411 | lsdt9 | 65841 | IVINS | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
658561 | lsdt9 | 65856 | JERUSALM | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
658891 | lsdt9 | 65889 | GLDRSHDB | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659111 | lsdt9 | 65911 | LOST RIV | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659291 | lsdt9 | 65929 | MC 15 | 13.19 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659311 | lsdt9 | 65931 | MCCELAND | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.39 | 58.3 | 0.133 | 0.0833 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6594499 | lsdt9 | 65944 | MIDDLETN | 34.5 | 99 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659561 | lsdt9 | 65956 | MIDWEST | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.01 | 58.5 | 0.133 | 0.0833 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
661361 | lsdt9 | 66136 | OQUIRRH | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.25 | 58.5 | 0.133 | 0.0833 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
662031 | lsdt9 | 66203 | SKYPARK | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
662061 | lsdt9 | 66206 | PARRISH | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.37 | 58.5 | 0.133 | 0.0833 | 0.12 | 58.3 | 0.133 | 0.0833 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
662541 | lsdt9 | 66254 | PLUMTREE | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.47 | 58.3 | 0.133 | 0.0833 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
662851 | lsdt9 | 66285 | RIDING R | 138 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.01 | 59.5 | 60 | 0.0833 | 0.04 | 59.3 | 15 | 0.0833 | 0.04 | 59.1 | 0.133 | 0.0833 | 0.1 | 58.3 | 0.133 | 0.0833 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
662961 | lsdt9 | 66296 | RIGBY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663111 | lsdt9 | 66311 | RIVRDAL | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.72 | 58.7 | 0.133 | 0.0833 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663161 | lsdt9 | 66316 | ROCKSPGS | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663611 | lsdt9 | 66361 | SILVR CR | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663761 | lsdt9 | 66376 | SMITHFIE | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664141 | lsdt9 | 66414 | TAMARISK | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664221 | lsdt9 | 66422 | SG | 13.19 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664301 | lsdt9 | 66430 | SUGARMIL | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664321 | lsdt9 | 66432 | SUGARMIL | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664461 | lsdt9 | 66446 | HW | 13.19 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664621 | lsdt9 | 66462 | SWEBER | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664861 | lsdt9 | 66486 | TANNER | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.11 | 58.9 | 0.133 | 0.0833 | 0.06 | 58.7 | 0.133 | 0.0833 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
665011 | lsdt9 | 66501 | TAYLORSV | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
665251 | lsdt9 | 66525 | TERMINAL | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
665561 | lsdt9 | 66556 | TIMP | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.1 | 58.5 | 0.133 | 0.0833 | 0.1 | 58.3 | 0.133 | 0.0833 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
665621 | lsdt9 | 66562 | TOQUERVL | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
665811 | lsdt9 | 66581 | TL 15 | 13.19 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6663699 | lsdt9 | 66636 | WCEDAR | 34.5 | 99 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
666371 | lsdt9 | 66637 | COMMERCE | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
666621 | lsdt9 | 66662 | WEST GT | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.17 | 58.9 | 0.133 | 0.0833 | 0.23 | 58.5 | 0.133 | 0.0833 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
666951 | lsdt9 | 66695 | WIDFALLS | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667241 | lsdt9 | 66724 | WSTFIELD | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667631 | lsdt9 | 66763 | RND VLLY | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667641 | lsdt9 | 66764 | SO BUTTE | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667651 | lsdt9 | 66765 | SPAR CYN | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670101 | lsdt9 | 67010 | 90TH 6 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670151 | lsdt9 | 67015 | AMFORK | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670181 | lsdt9 | 67018 | ANGEL 1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670191 | lsdt9 | 67019 | ANGEL 3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670251 | lsdt9 | 67025 | ANT MINE | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670321 | lsdt9 | 67032 | BANGERT1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670341 | lsdt9 | 67034 | BANGERT2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670471 | lsdt9 | 67047 | BTLRV2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670691 | lsdt9 | 67069 | CENTENL1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670701 | lsdt9 | 67070 | CENTENL2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670741 | lsdt9 | 67074 | CHAPHILL | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670781 | lsdt9 | 67078 | CHRYWOD2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670801 | lsdt9 | 67080 | CLINTON1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670811 | lsdt9 | 67081 | CLINTON2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670901 | lsdt9 | 67090 | COLDWATR | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670981 | lsdt9 | 67098 | CONDA | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671001 | lsdt9 | 67100 | COPPRHL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67102NA | lsdt9 | 67102 | COTT #9 0.05 0.05 59.29999924 15 0.0833 1 lsdt9 67101 COTT | [8 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671071 | lsdt9 | 67107 | CRHOLLOW | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671091 | lsdt9 | 67109 | CUDAHY | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671121 | lsdt9 | 67112 | DECKLK 2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671141 | lsdt9 | 67114 | DIMPL1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671151 | lsdt9 | 67115 | DIMPL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671221 | lsdt9 | 67122 | E BENCH | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671381 | lsdt9 | 67138 | FARMNGT2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671391 | lsdt9 | 67139 | FIFTH 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671401 | lsdt9 | 67140 | FIFTH 2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671441 | lsdt9 | 67144 | FRANNIE | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671451 | lsdt9 | 67145 | FRANNIE2 | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671471 | lsdt9 | 67147 | GARLAND1 | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671481 | lsdt9 | 67148 | GARLAND2 | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671561 | lsdt9 | 67156 | GORDONAV | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671651 | lsdt9 | 67165 | GROW 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671661 | lsdt9 | 67166 | GROW 2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671741 | lsdt9 | 67174 | HAMMR 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671831 | lsdt9 | 67183 | HILLTP | 34.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671841 | lsdt9 | 67184 | HILLTP | 21 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671881 | lsdt9 | 67188 | HOGGRD 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671891 | lsdt9 | 67189 | HOGGRD 2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672001 | lsdt9 | 67200 | JORDANEL | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672021 | lsdt9 | 67202 | JORDPRK1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672091 | lsdt9 | 67209 | KRNS 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672101 | lsdt9 | 67210 | KRNS 2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672151 | lsdt9 | 67215 | LKPRK 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672231 | lsdt9 | 67223 | MAGNA 1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672251 | lsdt9 | 67225 | MALAD 12 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672281 | lsdt9 | 67228 | MANILA2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672361 | lsdt9 | 67236 | MEADOWB | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672401 | lsdt9 | 67240 | MIDLAND | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672581 | lsdt9 | 67258 | MORT 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672891 | lsdt9 | 67289 | PARKWY 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672901 | lsdt9 | 67290 | PARKWY 2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672991 | lsdt9 | 67299 | PINECYN1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673031 | lsdt9 | 67303 | PIONEER | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.32 | 58.3 | 0.133 | 0.0833 | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673091 | lsdt9 | 67309 | PLEASNTG | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.52 | 58.3 | 0.133 | 0.0833 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673171 | lsdt9 | 67317 | QUARRY1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673181 | lsdt9 | 67318 | QUARRY2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673221 | lsdt9 | 67322 | RIDG 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673231 | lsdt9 | 67323 | RIDG 2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673451 | lsdt9 | 67345 | SARATOGA | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673581 | lsdt9 | 67358 | SILVR CR | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673621 | lsdt9 | 67362 | SMITHFLD | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673691 | lsdt9 | 67369 | SO MTN 2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673721 | lsdt9 | 67372 | SOEAST2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673731 | lsdt9 | 67373 | SOEAST1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673751 | lsdt9 | 67375 | SOJORDN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673761 | lsdt9 | 67376 | SOJORDN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673781 | lsdt9 | 67378 | SOMLFRD1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673901 | lsdt9 | 67390 | SUMMITC | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673921 | lsdt9 | 67392 | SUNRISE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673931 | lsdt9 | 67393 | SUNRISE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673951 | lsdt9 | 67395 | SYRACUS3 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674051 | lsdt9 | 67405 | TAYLRV3 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674061 | lsdt9 | 67406 | TAYLRV4 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674191 | lsdt9 | 67419 | TRICITY | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674211 | lsdt9 | 67421 | SARATOG2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674241 | lsdt9 | 67424 | W JORD 1 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674271 | lsdt9 | 67427 | W OGDEN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674281 | lsdt9 | 67428 | W OGDEN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674321 | lsdt9 | 67432 | WARREN | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674621 | lsdt9 | 67462 | BDO | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674641 | lsdt9 | 67464 | COZYDALE | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674661 | lsdt9 | 67466 | WALNUTGR | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674861 | lsdt9 | 67486 | TERM 2 | 12.47 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674981 | lsdt9 | 67498 | HERRIM1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
675271 | lsdt9 | 67527 | THIRD W2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677081 | lsdt9 | 67708 | CLRFLDS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677091 | lsdt9 | 67709 | CLRFLDS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
678651 | lsdt9 | 67865 | SOPARK | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679451 | lsdt9 | 67945 | OSO OIL | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679911 | lsdt9 | 67991 | TAYLOR | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
680341 | lsdt9 | 68034 | WHITERK | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
680381 | lsdt9 | 68038 | FARMNGT1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
681091 | lsdt9 | 68109 | W LGNCYT | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.133 | 0.0833 | 0.21 | 58.7 | 0.133 | 0.0833 | 0.16 | 58.3 | 0.133 | 0.0833 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688021 | lsdt9 | 68802 | BNTF-MKT | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.44 | 58.7 | 0.133 | 0.0833 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688031 | lsdt9 | 68803 | BNTF-CEN | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.36 | 59.3 | 15 | 0.0833 | 0.32 | 58.9 | 0.133 | 0.0833 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688061 | lsdt9 | 68806 | APSUB | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688081 | lsdt9 | 68808 | BNTFL-NW | 46 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.133 | 0.0833 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68951NA | lsdt9 | 68951 | LOGN #9 0.05 0.05 59.1000 0.133 0.0833 0.71 58.9000 0.1330 0.0833 0.29 lsdt9 68957 LOGN | [8 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.31 | 58.5 | 0.133 | 0.0833 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691251 | lsdt9 | 69125 | CHIMBT69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.133 | 0.0833 | 0.29 | 58.3 | 0.133 | 0.0833 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691261 | lsdt9 | 69126 | EVANS | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691271 | lsdt9 | 69127 | COMUNTY1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 0.47 | 58.7 | 0.133 | 0.0833 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691281 | lsdt9 | 69128 | COMUNTY2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70002WP | lsdt9 | 70002 | BURNTMIL | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.5 | 30 | 0.083 | 0.31 | 59.5 | 60 | 0.083 | 0.27 | 58.3 | 0 | 0.13 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70004WP | lsdt9 | 70004 | GREENHRN | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.9 | 0 | 0.083 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70008P1 | lsdt9 | 70008 | KELIM | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70009YV | lsdt9 | 70009 | CRAIG_YV | 230 | YV | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 0.42784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70023P1 | lsdt9 | 70023 | ALLISON | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.36921 | 58.9 | 0.13333 | 0.1 | 0.34021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70023P2 | lsdt9 | 70023 | ALLISON | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.15932 | 58.7 | 0.13333 | 0.1 | 0.27374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70030WP | lsdt9 | 70030 | APT_PARK | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.3 | 15 | 0.083 | 0.07 | 59.1 | 0 | 0.083 | 0.21 | 58.5 | 0 | 0.133 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70039P1 | lsdt9 | 70039 | ARGO | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70041P1 | lsdt9 | 70041 | ARVADA_PS | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70041P2 | lsdt9 | 70041 | ARVADA_PS | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70045P3 | lsdt9 | 70045 | BANCROFT | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.29676 | 58.3 | 0.13333 | 0.1 | 0.70324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70049WP | lsdt9 | 70049 | BELMONT | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.9 | 0 | 0.13 | 0.31 | 58.7 | 0 | 0.13 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70050P1 | lsdt9 | 70050 | BERGENPK | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70050P2 | lsdt9 | 70050 | BERGENPK | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70051WP | lsdt9 | 70051 | BLENDE | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.5 | 30 | 0.13 | 0.26 | 59.1 | 0 | 0.13 | 0.31 | 58.5 | 0 | 0.13 | 0.29 | 58.3 | 0 | 0.13 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70055TS | lsdt9 | 70055 | BNAVST | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.1 | 0.083 | 0.56 | 58.5 | 0.1 | 0.083 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70058P4 | lsdt9 | 70058 | BOULDER_CN2 | 115 | P4 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.57684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70059P1 | lsdt9 | 70059 | BO_TERM | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70064P2 | lsdt9 | 70064 | BRECKRDG | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70064P3 | lsdt9 | 70064 | BRECKRDG | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 0.34091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70065P1 | lsdt9 | 70065 | BROOMFLD | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70065P3 | lsdt9 | 70065 | BROOMFLD | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.3145 | 58.7 | 0.13333 | 0.1 | 0.3491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70067P1 | lsdt9 | 70067 | BUCKLEY1 | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.3075 | 58.5 | 0.13333 | 0.1 | 0.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70067P2 | lsdt9 | 70067 | BUCKLEY1 | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.69258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70068RP | lsdt9 | 70068 | BURROCYN | 115 | RP | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70068TS | lsdt9 | 70068 | BURROCYN | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70086WP | lsdt9 | 70086 | CANONCTY | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.3 | 15 | 0.1 | 0.13 | 58.5 | 0 | 0.1 | 0.39 | 58.3 | 0 | 0.1 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70091CR | lsdt9 | 70091 | CASTLRCK | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.157 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.155 | 58.5 | 0.2 | 0 | 0.047 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70100P1 | lsdt9 | 70100 | CHATFLD | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.22471 | 58.7 | 0.13333 | 0.1 | 0.77529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70100P2 | lsdt9 | 70100 | CHATFLD | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.76433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70112P1 | lsdt9 | 70112 | CLARK | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.3616 | 58.9 | 0.13333 | 0.1 | 0.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70112P2 | lsdt9 | 70112 | CLARK | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70112P3 | lsdt9 | 70112 | CLARK | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 0.76527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70113P1 | lsdt9 | 70113 | CLIFTON | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70115CR | lsdt9 | 70115 | HPCYN | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0.158 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0.194 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0.195 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70117CR | lsdt9 | 70117 | CRWFTVLY | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0.156 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70124CR | lsdt9 | 70124 | CONIFER | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0.281 | 58.7 | 0.2 | 0 | 0.069 | 58.5 | 0.2 | 0 | 0.146 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70138CR | lsdt9 | 70138 | DANIELPK | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0.265 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70141P1 | lsdt9 | 70141 | DAKOTA | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70142CR | lsdt9 | 70142 | DEERCRK | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0.438 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70150TS | lsdt9 | 70150 | SWALLOWS | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0.05 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70157CR | lsdt9 | 70157 | DIVIDE | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0.171 | 58.3 | 0.2 | 0 | 0.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70160WP | lsdt9 | 70160 | E_CANON | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.3 | 0 | 0.083 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70176WP | lsdt9 | 70176 | FLORENCE | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.9 | 0 | 0.13 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70189P2 | lsdt9 | 70189 | GREENWD | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.28635 | 58.7 | 0.13333 | 0.1 | 0.24481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70189P3 | lsdt9 | 70189 | GREENWD | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.35233 | 58.5 | 0.13333 | 0.1 | 0.32297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70200P3 | lsdt9 | 70200 | GLENNPS | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 0.60749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70209P3 | lsdt9 | 70209 | GREELEY | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70209P4 | lsdt9 | 70209 | GREELEY | 115 | P4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70212P1 | lsdt9 | 70212 | GREENWD | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70214GV | lsdt9 | 70214 | GRANDJCT | 69 | GV | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.34673 | 58.9 | 0.13333 | 0.1 | 0.35008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70217P2 | lsdt9 | 70217 | HAVANA2 | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70217P3 | lsdt9 | 70217 | HAVANA2 | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 0.41449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70218P1 | lsdt9 | 70218 | HENDERPS | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70233P1 | lsdt9 | 70233 | HORIZON | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70236WP | lsdt9 | 70236 | HYDEPARK | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.3 | 15 | 0.083 | 0.29 | 59.1 | 0 | 0.083 | 0.41 | 58.7 | 0 | 0.083 | 0.14 | 58.5 | 0 | 0.083 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70239P2 | lsdt9 | 70239 | JEWELL2 | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70239P3 | lsdt9 | 70239 | JEWELL2 | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 0.29304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70240P1 | lsdt9 | 70240 | JOHNSTN | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70242P2 | lsdt9 | 70242 | KENDRICK | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.55387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70242P2 | lsdt9 | 70242 | KENDRICK | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.54111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70242P1 | lsdt9 | 70242 | KENDRICK | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 0.24135 | 58.3 | 0.13333 | 0.1 | 0.41538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70244P2 | lsdt9 | 70244 | LAFAYETT | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70244P3 | lsdt9 | 70244 | LAFAYETT | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.46401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70252P2 | lsdt9 | 70252 | LAKEWOD2 | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70259P1 | lsdt9 | 70259 | LEETSDAL | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70259P2 | lsdt9 | 70259 | LEETSDAL | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70261P1 | lsdt9 | 70261 | LEGGETT | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70261P2 | lsdt9 | 70261 | LEGGETT | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 0.54553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70269P2 | lsdt9 | 70269 | LOUISVIL | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70278P1 | lsdt9 | 70278 | MARCY | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70278P2 | lsdt9 | 70278 | MARCY | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70278P3 | lsdt9 | 70278 | MARCY | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.33303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70280P2 | lsdt9 | 70280 | MARTIN_2 | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 0.43921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70283P1 | lsdt9 | 70283 | MEADOWHL | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.52275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70283P2 | lsdt9 | 70283 | MEADOWHL | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.74059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70284P1 | lsdt9 | 70284 | SURREYRG | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.34853 | 58.7 | 0.13333 | 0.1 | 0.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70284P2 | lsdt9 | 70284 | SURREYRG | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.29189 | 58.5 | 0.13333 | 0.1 | 0.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70287P1 | lsdt9 | 70287 | MILL | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.70825 | 58.9 | 0.13333 | 0.1 | 0.29164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70287P2 | lsdt9 | 70287 | MILL | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.70825 | 58.9 | 0.13333 | 0.1 | 0.29164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70293WP | lsdt9 | 70293 | NCANON | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.9 | 0 | 0.13 | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70295P1 | lsdt9 | 70295 | NCAR | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70295P2 | lsdt9 | 70295 | NCAR | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70298P1 | lsdt9 | 70298 | NORTH_PS | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70298P2 | lsdt9 | 70298 | NORTH_PS | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.82609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70301WP | lsdt9 | 70301 | NTHRIDGE | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.7 | 0 | 0.13 | 0.47 | 58.7 | 0 | 0.13 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70305WP | lsdt9 | 70305 | OVERTON | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.1 | 0 | 0.13 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70313CR | lsdt9 | 70313 | ORCHARD | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0.067 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.099 | 58.5 | 0.2 | 0 | 0.057 | 58.3 | 0.2 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70323P3 | lsdt9 | 70323 | PRAIRIE3 | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.45201 | 59.3 | 15 | 0.1 | 0.11985 | 58.5 | 0.13333 | 0.1 | 0.20859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70324P1 | lsdt9 | 70324 | LACOMBE | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.43322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70324P2 | lsdt9 | 70324 | LACOMBE | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.26064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70325TS | lsdt9 | 70325 | PLAZA | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.3 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70331P1 | lsdt9 | 70331 | PRAIRIE1 | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.72234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70331P2 | lsdt9 | 70331 | PRAIRIE1 | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.29565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70333TS | lsdt9 | 70333 | PROWERS | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.3 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70340P1 | lsdt9 | 70340 | QUAKER1 | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70341P2 | lsdt9 | 70341 | QUAKER2 | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70362P1 | lsdt9 | 70362 | RIVERDAL | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.34349 | 59.3 | 15 | 0.1 | 0.30418 | 58.5 | 0.13333 | 0.1 | 0.35233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70365P1 | lsdt9 | 70365 | SULLIVN2 | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.67643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70365P2 | lsdt9 | 70365 | SULLIVN2 | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.26553 | 58.9 | 0.13333 | 0.1 | 0.73447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70366WP | lsdt9 | 70366 | ROCKYFRD | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.7 | 0 | 0.13 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70368P1 | lsdt9 | 70368 | ROSEDALE | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70368P2 | lsdt9 | 70368 | ROSEDALE | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70369P1 | lsdt9 | 70369 | RUSSELL | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70369P2 | lsdt9 | 70369 | RUSSELL | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70370WP | lsdt9 | 70370 | SCANON | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.3 | 0 | 0.13 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70377P1 | lsdt9 | 70377 | SANDOWN | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70377P2 | lsdt9 | 70377 | SANDOWN | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70377P3 | lsdt9 | 70377 | SANDOWN | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.7594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70378WP | lsdt9 | 70378 | AREQUGCH | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.3 | 0 | 0.13 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70382P1 | lsdt9 | 70382 | SEMPER | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70382P2 | lsdt9 | 70382 | SEMPER | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.75444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70390WP | lsdt9 | 70390 | SKALA | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.7 | 0 | 0.13 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70394TS | lsdt9 | 70394 | SMELTER | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70396P3 | lsdt9 | 70396 | SMOKYHIL | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.31972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70401P1 | lsdt9 | 70401 | SOUTH_1 | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70405WP | lsdt9 | 70405 | ST.CHAS | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.5 | 60 | 0.1 | 0.55 | 58.5 | 0 | 0.1 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70413TS | lsdt9 | 70413 | STMBEACH | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70415WP | lsdt9 | 70415 | STONEMOOR | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.7 | 0 | 0.13 | 0.16 | 58.5 | 0 | 0.13 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70416CR | lsdt9 | 70416 | STRASBRG | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.079 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.101 | 58.5 | 0.2 | 0 | 0.116 | 58.3 | 0.2 | 0 | 0.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70419CR | lsdt9 | 70419 | LKGRGE | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.274 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.464 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70422WP | lsdt9 | 70422 | SUNSETPK | 69 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 58.5 | 0 | 0.13 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70423P3 | lsdt9 | 70423 | BOULDER_CN1 | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.57684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70424P1 | lsdt9 | 70424 | SUNSHINE | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.57684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70428P1 | lsdt9 | 70428 | TECH_CTR | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.3797 | 58.5 | 0.13333 | 0.1 | 0.27331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70428P2 | lsdt9 | 70428 | TECH_CTR | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70429CR | lsdt9 | 70429 | TINYTOWN | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.356 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0.029 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70432P1 | lsdt9 | 70432 | TOWER | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.36572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70432P2 | lsdt9 | 70432 | TOWER | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.11426 | 58.5 | 0.13333 | 0.1 | 0.59583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70436GV | lsdt9 | 70436 | UINTAH | 69 | GV | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70441P1 | lsdt9 | 70441 | UNIVERS1 | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70441P3 | lsdt9 | 70441 | UNIVERS1 | 115 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.62726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70449WP | lsdt9 | 70449 | DESRTCV | 115 | WP | [6 empty] | : | #9 | 0.1 | 0.1 | 59.5 | 30 | 0.083 | 0.11 | 59.1 | 0 | 0.083 | 0.096 | 58.9 | 0 | 0.083 | 0.16 | 58.3 | 0 | 0.083 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70458TS | lsdt9 | 70458 | WALSENBG | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70461P1 | lsdt9 | 70461 | WASHINGT | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 0.58129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70461P2 | lsdt9 | 70461 | WASHINGT | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.46177 | 58.7 | 0.13333 | 0.1 | 0.53823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70461P3 | lsdt9 | 70461 | WASHINGT | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.43252 | 58.7 | 0.13333 | 0.1 | 0.30732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70471P4 | lsdt9 | 70471 | WELD_PS | 230 | P4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70475P1 | lsdt9 | 70475 | ARROWHLK | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.34189 | 58.5 | 0.13333 | 0.1 | 0.65811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70476CR | lsdt9 | 70476 | WOODLAND | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.236 | 58.5 | 0.2 | 0 | 0.024 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70480P1 | lsdt9 | 70480 | WESTPS | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 0.43265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70481P1 | lsdt9 | 70481 | MONACO12 | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.57405 | 59.3 | 15 | 0.1 | 0.12837 | 59.1 | 0.13333 | 0.1 | 0.13791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70491P1 | lsdt9 | 70491 | TOLGATE | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.72737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70491P2 | lsdt9 | 70491 | TOLGATE | 230 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.13333 | 0.1 | 0.81375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70491P3 | lsdt9 | 70491 | TOLGATE | 230 | P3 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.37879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70512P1 | lsdt9 | 70512 | JEWELL1 | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.65552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70513CR | lsdt9 | 70513 | HOMESTEA | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0.098 | 59.3 | 15 | 0 | 0.166 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70514CR | lsdt9 | 70514 | PLUMCRK | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.1 | 58.9 | 0.2 | 0 | 0.064 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70515CR | lsdt9 | 70515 | DAVIDSON | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.129 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.26 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70516CR | lsdt9 | 70516 | PONDERSA | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.033 | 58.5 | 0.2 | 0 | 0.15 | 58.3 | 0.2 | 0 | 0.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70517CR | lsdt9 | 70517 | PARKERPS | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0.064 | 58.3 | 0.2 | 0 | 0.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70518CR | lsdt9 | 70518 | BAYOU | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.088 | 58.9 | 0.2 | 0 | 0.095 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70519CR | lsdt9 | 70519 | WOLFSBRG | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.064 | 58.5 | 0.2 | 0 | 0.003 | 58.3 | 0.2 | 0 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70521CR | lsdt9 | 70521 | PEAKVIEW | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.106 | 58.9 | 0.2 | 0 | 0.106 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70522CR | lsdt9 | 70522 | ROXBOROU | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0.32 | 58.7 | 0.2 | 0 | 0.122 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70524CR | lsdt9 | 70524 | SULPHUR | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.102 | 58.9 | 0.2 | 0 | 0.187 | 58.7 | 0.2 | 0 | 0.182 | 58.5 | 0.2 | 0 | 0.082 | 58.3 | 0.2 | 0 | 0.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70527P1 | lsdt9 | 70527 | SANTEFE | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 0.75739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70530P1 | lsdt9 | 70530 | PICADIL | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.20334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70533CR | lsdt9 | 70533 | LEMON | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0.15 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70534P1 | lsdt9 | 70534 | BERTHOUD | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70535HC | lsdt9 | 70535 | COOLEYMA | 230 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70537P1 | lsdt9 | 70537 | FITZSMNS | 115 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.2281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70537P2 | lsdt9 | 70537 | FITZSMNS | 115 | P2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.20636 | 58.9 | 0.13333 | 0.1 | 0.40647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70540HC | lsdt9 | 70540 | BASLTDST | 115 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.17143 | 58.9 | 0.13333 | 0.1 | 0.35714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70542HC | lsdt9 | 70542 | SNOWMASS | 115 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.1 | 0.15984 | 58.3 | 0.13333 | 0.1 | 0.04479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70544P1 | lsdt9 | 70544 | ISABELLE | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.13333 | 0.1 | 0.726 | 58.5 | 0.13333 | 0.1 | 0.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70547CR | lsdt9 | 70547 | BENNETT | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0.485 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70551P1 | lsdt9 | 70551 | MURPHY | 230 | P1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.31531 | 58.5 | 0.13333 | 0.1 | 0.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70571CR | lsdt9 | 70571 | KIOWA | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70581CR | lsdt9 | 70581 | GRNDVIEW | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0.195 | 59.3 | 15 | 0 | 0.167 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0.175 | 58.7 | 0.2 | 0 | 0.133 | 58.5 | 0.2 | 0 | 0.154 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70582CR | lsdt9 | 70582 | GREENLND | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.445 | 58.9 | 0.2 | 0 | 0.414 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70583CR | lsdt9 | 70583 | ELIZABTH | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0.186 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0 | 58.5 | 0.2 | 0 | 0.137 | 58.3 | 0.2 | 0 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70584CR | lsdt9 | 70584 | CRYSTVA | 12.5 | CR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0 | 59.3 | 15 | 0 | 0 | 59.3 | 15 | 0 | 0 | 58.9 | 0.2 | 0 | 0 | 58.7 | 0.2 | 0 | 0.118 | 58.5 | 0.2 | 0 | 0.304 | 58.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70604TS | lsdt9 | 70604 | PARKWAY | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.05 | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70609TS | lsdt9 | 70609 | SILVSADL | 230 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72000TS | lsdt9 | 72000 | CAREY_LM | 12.5 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72019TS | lsdt9 | 72019 | BROMLEY | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.083 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72025TS | lsdt9 | 72025 | PRARI_TS | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72026TS | lsdt9 | 72026 | REUNION | 230 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72107TS | lsdt9 | 72107 | SLATERTS | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72108TS | lsdt9 | 72108 | STERLING | 69 | TS | [6 empty] | : | #9 | 0 | 0 | 58.7 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72147TS | lsdt9 | 72147 | CHLKBLFF | 12.5 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72191TS | lsdt9 | 72191 | GATEWY | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72208TS | lsdt9 | 72208 | DELCAMIN | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.083 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72209TS | lsdt9 | 72209 | DELCAMIN | 12.5 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.083 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72419TS | lsdt9 | 72419 | PALMRDIV | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72789TS | lsdt9 | 72789 | NORWOOD | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72817TS | lsdt9 | 72817 | BADWATER | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72819TS | lsdt9 | 72819 | WL_CHILD | 34.5 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72953TS | lsdt9 | 72953 | MAVERICK | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73040TS | lsdt9 | 73040 | CARTERMT | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73047TS | lsdt9 | 73047 | DEERINGL | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.04 | 0.05 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73063MU | lsdt9 | 73063 | FRENCHCK | 115 | MU | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73063TS | lsdt9 | 73063 | FRENCHCK | 115 | TS | [6 empty] | : | #9 | 0 | 0 | 58.9 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73069TS | lsdt9 | 73069 | GLENDO | 115 | TS | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73072MP | lsdt9 | 73072 | GOREPASS | 138 | MP | [6 empty] | : | #9 | 0.03 | 0 | 58.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73072TS | lsdt9 | 73072 | GOREPASS | 138 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73077BH | lsdt9 | 73077 | HAPPYJCK | 115 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.5 | 60 | 0.1 | 0.68 | 59.3 | 15 | 0.1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73092TS | lsdt9 | 73092 | JACINTO | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73095TS | lsdt9 | 73095 | KERSEYTP | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73114TS | lsdt9 | 73114 | LONETREE | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73126TS | lsdt9 | 73126 | LYMAN | 115 | TS | [6 empty] | : | #9 | 0 | 0 | 59.3 | 15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73139TS | lsdt9 | 73139 | MYERS | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.04 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73141WM | lsdt9 | 73141 | N.CODY | 69 | WM | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0 | 0.083 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73152TS | lsdt9 | 73152 | PINEBLUF | 115 | TS | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0 | 0.083 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73152WM | lsdt9 | 73152 | PINEBLUF | 115 | WM | [6 empty] | : | #9 | 0 | 0 | 58.3 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73153TS | lsdt9 | 73153 | PODOLAK | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.05 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73168BA | lsdt9 | 73168 | Reno | 230 | BA | [6 empty] | : | #9 | 0.5 | 0.5 | 59.1 | 0.1425 | 0.0833 | 0.38 | 58.7 | 0.1425 | 0.0833 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73179MU | lsdt9 | 73179 | SIDNEY | 115 | MU | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0 | 0.083 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73183BH | lsdt9 | 73183 | SKYLINE | 115 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.9 | 0 | 0.1 | 0.31 | 58.5 | 0 | 0.1 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73187PP | lsdt9 | 73187 | SPRINGCK | 115 | PP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73202MU | lsdt9 | 73202 | TORRNGTN | 115 | MU | [6 empty] | : | #9 | 0 | 0 | 58.5 | 0 | 0.083 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73219MP | lsdt9 | 73219 | WINDYGAP | 69 | MP | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73219TS | lsdt9 | 73219 | WINDYGAP | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73244BH | lsdt9 | 73244 | CEMETERY | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73246BH | lsdt9 | 73246 | CUSTER | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.5 | 60 | 0.1 | 0.23 | 58.7 | 0 | 0.1 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73252BH | lsdt9 | 73252 | WESTHILL | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 0.2 | 58.7 | 0 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73257BH | lsdt9 | 73257 | MERILLAT | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.3 | 15 | 0.1 | 0.27 | 58.7 | 0 | 0.1 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73262BH | lsdt9 | 73262 | PLSNTVLY | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.3 | 0 | 0.1 | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73263BH | lsdt9 | 73263 | PLUMA | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 0.39 | 58.7 | 0 | 0.1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73266BH | lsdt9 | 73266 | LANGE | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73278BH | lsdt9 | 73278 | WESTBLVD | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.3 | 15 | 0.1 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73280BH | lsdt9 | 73280 | WHITEWOOD | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.7 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73281BH | lsdt9 | 73281 | WNDYFLAT | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73286BH | lsdt9 | 73286 | ANAMOSA | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.9 | 0 | 0.1 | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73287BH | lsdt9 | 73287 | 4TH ST | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 0.25 | 58.7 | 0 | 0.1 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73290BH | lsdt9 | 73290 | EASTNRTH | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.5 | 30 | 0.1 | 0.16 | 59.3 | 15 | 0.1 | 0.069 | 58.5 | 0 | 0.1 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73318TS | lsdt9 | 73318 | LIMON | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.7 | 0.1 | 0.083 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73326TS | lsdt9 | 73326 | ROBB | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73331MU | lsdt9 | 73331 | WRAYWAPA | 115 | MU | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73331TS | lsdt9 | 73331 | WRAYWAPA | 115 | TS | [6 empty] | : | #9 | 0 | 0 | 59.1 | 0 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73348BH | lsdt9 | 73348 | CORLETT | 115 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.3 | 0 | 0.1 | 0.06 | 59.1 | 0 | 0.1 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73354PP | lsdt9 | 73354 | JACKLOPE | 115 | PP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73367PP | lsdt9 | 73367 | FTSANDER | 115 | PP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.133 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73378TS | lsdt9 | 73378 | FMN | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73379MU | lsdt9 | 73379 | FMWEST | 115 | MU | [6 empty] | : | #9 | 0 | 0 | 59.5 | 30 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73391CS | lsdt9 | 73391 | CTTNWD N | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73393CS | lsdt9 | 73393 | CTTNWD S | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73395CS | lsdt9 | 73395 | CTTNWD S | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 0.2554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73396CS | lsdt9 | 73396 | DRAKE E | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 0.53646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73398CS | lsdt9 | 73398 | DRAKE S | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14.933 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73399CS | lsdt9 | 73399 | DRAKE W | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 0.52332 | 58.7 | 0.1 | 0.0667 | 0.46655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73402TS | lsdt9 | 73402 | FALCONMV | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73404CS | lsdt9 | 73404 | FOUNTAIN S | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 0.14901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73405TS | lsdt9 | 73405 | GEESEN | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73408CS | lsdt9 | 73408 | KELKER E | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73409CS | lsdt9 | 73409 | KELKER W | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 59.933 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73410CS | lsdt9 | 73410 | KETTLECK S | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73414TS | lsdt9 | 73414 | FOXRUN | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73420CS | lsdt9 | 73420 | ROCKISLD | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.0667 | 0.49099 | 58.5 | 0.1 | 0.0667 | 0.50901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73425CS | lsdt9 | 73425 | WOODMEN S | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 29.933 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73430CS | lsdt9 | 73430 | FAIRVWCS | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73463TS | lsdt9 | 73463 | PADDOCK | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.1 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73480BH | lsdt9 | 73480 | CROWCRK | 115 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 0.15 | 58.7 | 0 | 0.1 | 0.06 | 58.3 | 0 | 0.1 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73492TS | lsdt9 | 73492 | HDOME | 69 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.05 | 0.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73514BH | lsdt9 | 73514 | E.MEADE | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73519BH | lsdt9 | 73519 | 44TH ST | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73521BH | lsdt9 | 73521 | BFRNCH26 | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 0.15 | 58.3 | 0 | 0.1 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73523BH | lsdt9 | 73523 | CROSS ST | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 0.55 | 58.7 | 0 | 0.1 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73547TS | lsdt9 | 73547 | GOSH COUNTY | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73565CS | lsdt9 | 73565 | KELKER W | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 0.15332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73566CS | lsdt9 | 73566 | ROCKISLD | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 0.33114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73567CS | lsdt9 | 73567 | BRADLEY S | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.0667 | 0.65902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73597TS | lsdt9 | 73597 | OWL_CRK | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73600PS | lsdt9 | 73600 | COBBLAKE | 115 | PS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.38083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73620PP | lsdt9 | 73620 | LARAMIE 1 | 13.2 | PP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73621PP | lsdt9 | 73621 | LARAMIE 2 | 13.2 | PP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73701CS | lsdt9 | 73701 | BRADLEY N | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 0.21947 | 58.3 | 0.1 | 0.0667 | 0.32875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73702CS | lsdt9 | 73702 | BRADLEY N | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 0.3486 | 58.5 | 0.1 | 0.0667 | 0.32796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73709CS | lsdt9 | 73709 | RAMPART N | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 0.12617 | 58.5 | 0.1 | 0.0667 | 0.38882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74000BH | lsdt9 | 74000 | STURGIS | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.3 | 30 | 0.1 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74013BH | lsdt9 | 74013 | PEDMNT | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.5 | 30 | 0.1 | 0.17 | 58.7 | 0 | 0.1 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74019BH | lsdt9 | 74019 | GILLETTS | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.9 | 0 | 0.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74028BH | lsdt9 | 74028 | RCSOUTH2 | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.3 | 15 | 0.1 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74041BH | lsdt9 | 74041 | EB PARK | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.7 | 0 | 0.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74055BH | lsdt9 | 74055 | CLEVLD_ST | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 58.3 | 0 | 0.1 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76315BA | lsdt9 | 76315 | Teckla 1 | 69 | BA | [6 empty] | : | #9 | 0.5 | 0.5 | 58.9 | 0.1425 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76315BA | lsdt9 | 76315 | Teckla 1 | 69 | BA | [6 empty] | : | #9 | 0.5 | 0.5 | 59.3 | 14.86 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76315BA | lsdt9 | 76315 | Teckla 1 | 69 | BA | [6 empty] | : | #9 | 0.5 | 0.5 | 59.5 | 29.86 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76316BA | lsdt9 | 76316 | Teckla 2 | 69 | BA | [6 empty] | : | #9 | 0.5 | 0.5 | 58.5 | 0.1425 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76401BA | lsdt9 | 76401 | BarberCrk | 230 | BA | [6 empty] | : | #9 | 0.5 | 0.5 | 58.3 | 0.1425 | 0.05 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76502BH | lsdt9 | 76502 | SPFSHPRK | 69 | BH | [6 empty] | : | #9 | 0.067 | 0.1 | 59.1 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78076PR | lsdt9 | 78076 | DIXONCK | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.066667 | 0.083333 | 0.36279 | 58.5 | 0.066667 | 0.083333 | 0.11163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78076PR | lsdt9 | 78076 | DIXON CK | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0667 | 0.0833 | 0.4089 | 58.5 | 0.0667 | 0.0833 | 0.07839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78077PR | lsdt9 | 78077 | DRAKERD | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.066667 | 0.083333 | 0.095982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78077PR | lsdt9 | 78077 | DRAKE RD | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0667 | 0.0833 | 0.099778 | 59.5 | 15 | 0.0833 | 0.13304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78082PR | lsdt9 | 78082 | LINDEN | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.083333 | 0.16702 | 58.9 | 0.033333 | 0.083333 | 0.16916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78082PR | lsdt9 | 78082 | LINDEN | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.0833 | 0.16453 | 58.9 | 0.0333 | 0.0833 | 0.12249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78086PR | lsdt9 | 78086 | TIMBERLN | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.033333 | 0.083333 | 0.14098 | 58.5 | 0.033333 | 0.083333 | 0.49508 | 58.3 | 0.033333 | 0.11667 | 0.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78086PR | lsdt9 | 78086 | TIMBERLN | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0333 | 0.0833 | 0.11551 | 58.5 | 0.0667 | 0.0833 | 0.45545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78088PR | lsdt9 | 78088 | HARMONY | 230 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.066667 | 0.05 | 0.036329 | 58.3 | 0.066667 | 0.083333 | 0.23614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78088PR | lsdt9 | 78088 | HARMONY | 230 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0667 | 0.0833 | 0.049724 | 58.3 | 0.0667 | 0.0833 | 0.21705 | 59.5 | 15 | 0.0833 | 0.10208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78089PR | lsdt9 | 78089 | PORTNER | 230 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.033333 | 0.083333 | 0.51452 | 58.9 | 0.1 | 0.083333 | 0.43983 | 58.7 | 0.033333 | 0.083333 | 0.045643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78089PR | lsdt9 | 78089 | PORTNER | 230 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0333 | 0.0833 | 0.31855 | 58.9 | 0.0333 | 0.0833 | 0.38306 | 58.7 | 0.0667 | 0.0833 | 0.31452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78091PR | lsdt9 | 78091 | HORSESHO | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.08 | 0.045 | 0.13712 | 58.7 | 0.083333 | 0.05 | 0.14184 | 58.5 | 0.083333 | 0.05 | 0.15366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78091PR | lsdt9 | 78091 | HORSESHO | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.08 | 0.045 | 0.14681 | 58.7 | 0.0833 | 0.05 | 0.19848 | 58.5 | 0.0833 | 0.05 | 0.18936 | 59.3 | 30 | 0.05 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78094PR | lsdt9 | 78094 | VALLEYLM | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.08 | 0.045 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78094PR | lsdt9 | 78094 | VALLEYLM | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.08 | 0.045 | 0.33333 | 58.3 | 0.0833 | 0.05 | 0.21526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78098PR | lsdt9 | 78098 | CROSSRDS | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.083333 | 0.05 | 0.17164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78098PR | lsdt9 | 78098 | CROSSRDS | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.05 | 0.45479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78099PR | lsdt9 | 78099 | LOVEE | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.46667 | 0.11667 | 0.23133 | 58.9 | 0.08 | 0.053333 | 0.14786 | 58.7 | 0.083333 | 0.05 | 0.1012 | 58.5 | 0.08 | 0.045 | 0.096386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78099PR | lsdt9 | 78099 | LOVEE | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.4667 | 0.1167 | 0.21429 | 58.9 | 0.08 | 0.045 | 0.063616 | 58.7 | 0.0833 | 0.05 | 0.076786 | 58.5 | 0.0833 | 0.05 | 0.027232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78111PR | lsdt9 | 78111 | HARVARD | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 0.31225 | 58.3 | 0.1 | 0.05 | 0.25692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78111PR | lsdt9 | 78111 | HARVARD | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 0.15625 | 58.7 | 0.1 | 0.05 | 0.19531 | 58.3 | 0.1 | 0.05 | 0.25391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78116PR | lsdt9 | 78116 | CNTYLINE | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 0.6215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78116PR | lsdt9 | 78116 | CNTYLINE | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 0.040323 | 58.5 | 0.1 | 0.05 | 0.43548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78119PR | lsdt9 | 78119 | TERRY | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 0.23045 | 58.3 | 0.1 | 0.05 | 0.14198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78119PR | lsdt9 | 78119 | TERRY | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 0.15333 | 58.5 | 0.1 | 0.05 | 0.088889 | 58.3 | 0.1 | 0.05 | 0.13556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78121PR | lsdt9 | 78121 | FORDHAM | 115 | PR | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 0.098039 | 58.9 | 0.1 | 0.05 | 0.11983 | 59.5 | 60 | 0.05 | 0.28322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78506CS | lsdt9 | 78506 | DRAKE E | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 0.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78511CS | lsdt9 | 78511 | ROCKISLD | 34.5 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 0.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78654CS | lsdt9 | 78654 | BRADLEY N | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 0.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78658CS | lsdt9 | 78658 | CTTNWD N | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78659CS | lsdt9 | 78659 | CTTNWD S | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78662CS | lsdt9 | 78662 | DRAKE S | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14.933 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78663CS | lsdt9 | 78663 | FAIRVWCS | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78670CS | lsdt9 | 78670 | KELKER E | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78671CS | lsdt9 | 78671 | KELKER W | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 59.933 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78677CS | lsdt9 | 78677 | ROCKISLD | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0667 | 0.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78682CS | lsdt9 | 78682 | WOODMEN N | 115 | CS | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 29.933 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79002TS | lsdt9 | 79002 | AXIAL | 138 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.9 | 0.083 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79006HC | lsdt9 | 79006 | BEAVERCU | 115 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 0.32665 | 58.5 | 0.13333 | 0.1 | 0.26443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79018HC | lsdt9 | 79018 | CRYSTLPS | 115 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79056P5 | lsdt9 | 79056 | RIFLE_CU | 138 | P5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.13333 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79062WA | lsdt9 | 79062 | Shiprock | 115 | WA | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79065YV | lsdt9 | 79065 | STEAMBT | 230 | YV | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.17721 | 58.5 | 0.13333 | 0.1 | 0.07944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79066HC | lsdt9 | 79066 | VAIL | 115 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.72255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79069HC | lsdt9 | 79069 | WOLCOTT | 230 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.13333 | 0.1 | 0.73559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79075TS | lsdt9 | 79075 | EMPIRETS | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79077TS | lsdt9 | 79077 | BAYFIELD | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79078TS | lsdt9 | 79078 | BODO | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79079TS | lsdt9 | 79079 | BULLOCK | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.05 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79081TS | lsdt9 | 79081 | CRSTBUTT | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79084TS | lsdt9 | 79084 | LAKECITY | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79086TS | lsdt9 | 79086 | PAGOSA | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79092HC | lsdt9 | 79092 | AVON | 115 | HC | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.13333 | 0.1 | 0.67496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79135TS | lsdt9 | 79135 | HAPPYCAN | 46 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 30 | 0.083 | 0.32 | 59.5 | 60 | 0.083 | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79137TS | lsdt9 | 79137 | HOTCHKIS | 46 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.3 | 15 | 0.05 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79192TS | lsdt9 | 79192 | SOCANAL | 115 | TS | [6 empty] | : | #9 | 0.03 | 0 | 59.5 | 60 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79603FA | lsdt9 | 79603 | ANIMAS | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 58.3 | 0 | 0.05 | 0.042442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79605FA | lsdt9 | 79605 | AZTEC | 69 | FA | [6 empty] | : | #9 | 0.075 | 999 | 58.5 | 0 | 0.05 | 0.010571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79606FA | lsdt9 | 79606 | AZTEC_D | 69 | FA | [6 empty] | : | #9 | 0.075 | 999 | 58.5 | 0 | 0.05 | 0.031977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79609FA | lsdt9 | 79609 | BERGIN | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 58.7 | 0 | 0.05 | 0.013497 | 58.3 | 0 | 0.05 | 0.004908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79614FA | lsdt9 | 79614 | BLUFVIEW | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.3 | 15 | 0.05 | 0.0023256 | 58.9 | 0 | 0.05 | 0.011047 | 58.5 | 0 | 0.05 | 0.0046512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79616FA | lsdt9 | 79616 | COLLEG | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 58.5 | 0 | 0.05 | 0.023837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79624FA | lsdt9 | 79624 | FRUITLND | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.3 | 15 | 0.05 | 0.0079755 | 58.7 | 0 | 0.05 | 0.023313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79630FA | lsdt9 | 79630 | HARTCYN | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.3 | 15 | 0.05 | 0.002907 | 58.9 | 0 | 0.05 | 0.0081395 | 58.7 | 0 | 0.05 | 0.012209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79635FA | lsdt9 | 79635 | LAKEVIEW | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.5 | 30 | 0.05 | 0.02093 | 58.5 | 0 | 0.05 | 0.0011628 | 58.3 | 0 | 0.05 | 0.013372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79637FA | lsdt9 | 79637 | LEE_ACRES | 69 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.5 | 0 | 0.05 | 0.06411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79638FA | lsdt9 | 79638 | MESA FM | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.5 | 0 | 0.05 | 0.037209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79644FA | lsdt9 | 79644 | PINE RIVER | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.3 | 15 | 0.05 | 0.003681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79652FA | lsdt9 | 79652 | PRAXAIR | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 58.9 | 0 | 0.05 | 0.061963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79653FA | lsdt9 | 79653 | PUMP_CYN | 69 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.5 | 60 | 0.05 | 0.03681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79655FA | lsdt9 | 79655 | SAN JUAN | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.3 | 15 | 0.05 | 0.012209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79657FA | lsdt9 | 79657 | TURLY_S | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.5 | 60 | 0.05 | 0.0042945 | 58.9 | 0 | 0.05 | 0.0042945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79659FA | lsdt9 | 79659 | VISTA FEUS | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 59.5 | 0 | 0.05 | 0.007362 | 59.3 | 15 | 0.05 | 0.053374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79664FA | lsdt9 | 79664 | COTTONWOOD | 115 | FA | [6 empty] | : | #9 | 0.075 | 999 | 58.7 | 0 | 0.05 | 0.059264 | 58.5 | 0 | 0.05 | 0.016687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800101 | lsdt9 | 80010 | DVM 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800141 | lsdt9 | 80014 | SFU 12T1 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800151 | lsdt9 | 80015 | SFU 12T2 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800251 | lsdt9 | 80025 | SWP .6 | 0.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.04 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800351 | lsdt9 | 80035 | LF1 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800371 | lsdt9 | 80037 | RSR 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800521 | lsdt9 | 80052 | UNS 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800551 | lsdt9 | 80055 | NEL 12A | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 0.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800561 | lsdt9 | 80056 | NEL 12C | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800571 | lsdt9 | 80057 | SCP 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1117 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800581 | lsdt9 | 80058 | UNY 12A | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800591 | lsdt9 | 80059 | UNY 12B | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800601 | lsdt9 | 80060 | NXC 12B | 12 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800611 | lsdt9 | 80061 | JRI 12 | 12 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800621 | lsdt9 | 80062 | NXC 12A | 12 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800671 | lsdt9 | 80067 | WCF 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.0417 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800681 | lsdt9 | 80068 | VDK 12 | 12 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800781 | lsdt9 | 80078 | YVR 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.05 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801011 | lsdt9 | 80101 | LNH 2 | 2.4 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801081 | lsdt9 | 80108 | TMO 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801091 | lsdt9 | 80109 | DPT 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801181 | lsdt9 | 80118 | CBN 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1333 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801191 | lsdt9 | 80119 | WTL 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801201 | lsdt9 | 80120 | BCI 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801211 | lsdt9 | 80121 | CAN 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801221 | lsdt9 | 80122 | WHY 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801231 | lsdt9 | 80123 | SYH 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801241 | lsdt9 | 80124 | MLN 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.0833 | 0.0833 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801251 | lsdt9 | 80125 | SYH 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1333 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801421 | lsdt9 | 80142 | HSY 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 56 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801481 | lsdt9 | 80148 | HSY 12A | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801491 | lsdt9 | 80149 | ESQ 12A | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.7 | 60 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801561 | lsdt9 | 80156 | NEX 13T1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801611 | lsdt9 | 80161 | BVC 13 | 13.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.05 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801821 | lsdt9 | 80182 | RTI 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.0833 | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801911 | lsdt9 | 80191 | SGP 35 | 35 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802091 | lsdt9 | 80209 | HSK 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802141 | lsdt9 | 80214 | GBW 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1333 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802191 | lsdt9 | 80219 | KGP 66 | 66 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802341 | lsdt9 | 80234 | HCR 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.16 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802391 | lsdt9 | 80239 | QRP 13B | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802401 | lsdt9 | 80240 | NLV 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802411 | lsdt9 | 80241 | TXB 25 | 25 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.1333 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802431 | lsdt9 | 80243 | TFP 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802451 | lsdt9 | 80245 | FBO 13X1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.0833 | 0.1 | 0.3333 | 59 | 0.0833 | 0.1 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802461 | lsdt9 | 80246 | LAP 13T1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.0383 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802481 | lsdt9 | 80248 | AWL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.05 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802491 | lsdt9 | 80249 | BLM 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802511 | lsdt9 | 80251 | FBO 13T3 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.2 | 0.0833 | 0.1 | 0.3333 | 59 | 0.0833 | 0.1 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802531 | lsdt9 | 80253 | LGW 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802731 | lsdt9 | 80273 | LF2 2 | 2.4 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802761 | lsdt9 | 80276 | STM 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802771 | lsdt9 | 80277 | BLP 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802781 | lsdt9 | 80278 | FPS 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802791 | lsdt9 | 80279 | REG 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802801 | lsdt9 | 80280 | CPL 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.09 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802901 | lsdt9 | 80290 | AFN 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802921 | lsdt9 | 80292 | RVS 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802931 | lsdt9 | 80293 | FCO 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802971 | lsdt9 | 80297 | TIL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802991 | lsdt9 | 80299 | TOK 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803101 | lsdt9 | 80310 | LCC 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803111 | lsdt9 | 80311 | CMO 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803131 | lsdt9 | 80313 | GRH 66 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803171 | lsdt9 | 80317 | FRO 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803201 | lsdt9 | 80320 | LCC 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803291 | lsdt9 | 80329 | 45904 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803341 | lsdt9 | 80334 | SSQ 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1667 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803381 | lsdt9 | 80338 | HPS 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803391 | lsdt9 | 80339 | WHP 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803401 | lsdt9 | 80340 | PKP 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803471 | lsdt9 | 80347 | CSQ 12B | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.0833 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803481 | lsdt9 | 80348 | CSQ 12C | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.0833 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803491 | lsdt9 | 80349 | CSQ 12D | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.0833 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803501 | lsdt9 | 80350 | CSQ 12E | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.0833 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803601 | lsdt9 | 80360 | POW 6X6 | 6.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803621 | lsdt9 | 80362 | POW 6X18 | 6.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803631 | lsdt9 | 80363 | POW 6X16 | 6.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803641 | lsdt9 | 80364 | POW 6X19 | 6.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803701 | lsdt9 | 80370 | POW 6X17 | 6.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803711 | lsdt9 | 80371 | POW 6X24 | 6.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803741 | lsdt9 | 80374 | POW 1X9 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803761 | lsdt9 | 80376 | POW 6X4 | 6.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804251 | lsdt9 | 80425 | EKO 4B | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804261 | lsdt9 | 80426 | EKO 13B | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804271 | lsdt9 | 80427 | EKO 4A | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1333 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805111 | lsdt9 | 80511 | MAN 12A | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1333 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805201 | lsdt9 | 80520 | COK 25A | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.0833 | 0.1333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805211 | lsdt9 | 80521 | COK 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805221 | lsdt9 | 80522 | COK 25C | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.0833 | 0.1333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805231 | lsdt9 | 80523 | COK 25D | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0833 | 0.1333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805241 | lsdt9 | 80524 | MAN 12B | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805641 | lsdt9 | 80564 | LCS 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805851 | lsdt9 | 80585 | HMC 13T1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.05 | 0.4 | 58.8 | 0.0833 | 0.05 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805861 | lsdt9 | 80586 | HMC 13T2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.05 | 0.4 | 58.8 | 0.0833 | 0.05 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805871 | lsdt9 | 80587 | FCC 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1167 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805991 | lsdt9 | 80599 | HML 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806031 | lsdt9 | 80603 | HML 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1667 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806051 | lsdt9 | 80605 | NHS 13T1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.07 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806061 | lsdt9 | 80606 | PRG 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806081 | lsdt9 | 80608 | NHS 13T2 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.07 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806111 | lsdt9 | 80611 | TBN 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806121 | lsdt9 | 80612 | WPN 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806131 | lsdt9 | 80613 | TWT 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806141 | lsdt9 | 80614 | WQL 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.07 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806151 | lsdt9 | 80615 | NGL 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1333 | 0.5 | 58.9 | 0.1 | 0.1333 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806161 | lsdt9 | 80616 | WFQ 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806171 | lsdt9 | 80617 | NOS 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806181 | lsdt9 | 80618 | WWL 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.12 | 0.07 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806191 | lsdt9 | 80619 | DKY 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.0833 | 0.0833 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806241 | lsdt9 | 80624 | HVC 13TP | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806251 | lsdt9 | 80625 | HVC 13TN | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806261 | lsdt9 | 80626 | TMT 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806271 | lsdt9 | 80627 | HVC 4F/B/A | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806281 | lsdt9 | 80628 | HVC 4XE | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806291 | lsdt9 | 80629 | LLD 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806311 | lsdt9 | 80631 | BLE 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806331 | lsdt9 | 80633 | BDM 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806341 | lsdt9 | 80634 | HVC 13TC | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806351 | lsdt9 | 80635 | HVC 13XE | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806521 | lsdt9 | 80652 | EQU 69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806531 | lsdt9 | 80653 | QNT 13 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806541 | lsdt9 | 80654 | TMM 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.0833 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806571 | lsdt9 | 80657 | HSP 13T1 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.7 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806581 | lsdt9 | 80658 | HSP 13T4 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806631 | lsdt9 | 80663 | STL 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806641 | lsdt9 | 80664 | CUM 27B1 | 27 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806651 | lsdt9 | 80665 | HVC 13TG | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806801 | lsdt9 | 80680 | FLW 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806961 | lsdt9 | 80696 | EKO 13A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
807431 | lsdt9 | 80743 | BRB 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808571 | lsdt9 | 80857 | MML 25T1 | 25 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.0333 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809381 | lsdt9 | 80938 | WKA 25 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809421 | lsdt9 | 80942 | PLD 25T1 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809751 | lsdt9 | 80975 | MTP 4T1 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.025 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809761 | lsdt9 | 80976 | MTP 4T3 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809791 | lsdt9 | 80979 | POW 1X24 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809871 | lsdt9 | 80987 | ARN 25B | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809951 | lsdt9 | 80995 | BJK 4 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809981 | lsdt9 | 80998 | GBR 4A | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1333 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810651 | lsdt9 | 81065 | QBS 12 | 12.6 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810721 | lsdt9 | 81072 | RTI 13A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.0833 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810821 | lsdt9 | 81082 | QRP 13A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810841 | lsdt9 | 81084 | QRP 13C | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811121 | lsdt9 | 81112 | TLB 13A | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811131 | lsdt9 | 81113 | TLB 13B | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811301 | lsdt9 | 81130 | CFT 13C | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811311 | lsdt9 | 81131 | CFT 13H | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811331 | lsdt9 | 81133 | CFT 13T5 | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.1 | 0.75 | 58.3 | 0.0833 | 0.1 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811341 | lsdt9 | 81134 | CFT 13D | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811381 | lsdt9 | 81138 | CFT 13E | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811401 | lsdt9 | 81140 | CFT 13G | 13.8 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.0833 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811511 | lsdt9 | 81151 | CHF 25T10 | 25.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.0833 | 0.1333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84289AP | lsdt9 | 84289 | GRNITRF | 69 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.46983 | 58.9 | 0.1 | 0.0833 | 0.14645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84454AP | lsdt9 | 84454 | WILLISAZ | 69 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.50243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85002AP | lsdt9 | 85002 | ADOBE 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.98668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85003AP | lsdt9 | 85003 | ADOBE 19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.16802 | 59.3 | 15 | 0.0833 | 0.73143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85004AP | lsdt9 | 85004 | ARROYO 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.84331 | 57.9 | 0.1 | 0.0833 | 0.11898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85010AP | lsdt9 | 85010 | CC 28 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.53216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85011AP | lsdt9 | 85011 | CHERYL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.50008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85013AP | lsdt9 | 85013 | DEADMN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.28554 | 58.5 | 0.1 | 0.0833 | 0.67723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85014AP | lsdt9 | 85014 | DEADMN11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.26474 | 58.3 | 0.1 | 0.0833 | 0.16012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85015AP | lsdt9 | 85015 | DURNGO 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.36562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85016AP | lsdt9 | 85016 | DURNGO11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.68231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85017AP | lsdt9 | 85017 | DV 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.72752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85018AP | lsdt9 | 85018 | DV 19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.25886 | 57.9 | 0.1 | 0.0833 | 0.41702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85019AP | lsdt9 | 85019 | ENCANT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.5156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85023AP | lsdt9 | 85023 | FORTIP 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.28967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85024AP | lsdt9 | 85024 | FORTIP11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.059101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85030AP | lsdt9 | 85030 | GRISWLD | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.90923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85032AP | lsdt9 | 85032 | HARBOR19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.070492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85033AP | lsdt9 | 85033 | HARBOR27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.38822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85035AP | lsdt9 | 85035 | HONYWL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.63403 | 57.9 | 0.1 | 0.0833 | 0.34958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85040AP | lsdt9 | 85040 | JCKSON20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.26152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85041AP | lsdt9 | 85041 | JCKSON28 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.18943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85046AP | lsdt9 | 85046 | LINWST11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.30895 | 57.9 | 0.1 | 0.0833 | 0.38956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85051AP | lsdt9 | 85051 | LOMVST19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85052AP | lsdt9 | 85052 | LOOKOT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.87919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85053AP | lsdt9 | 85053 | LOOKOT11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.62854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85054AP | lsdt9 | 85054 | MCDWEL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.60747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85055AP | lsdt9 | 85055 | MCDWEL19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.37991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85057AP | lsdt9 | 85057 | MDOWBK11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.27353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85066AP | lsdt9 | 85066 | NEWRVR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.96971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85068AP | lsdt9 | 85068 | NVALEY 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.46666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85069AP | lsdt9 | 85069 | NVALEY11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.27479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85070AP | lsdt9 | 85070 | ORNGWD51 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.33881 | 58.7 | 0.1 | 0.0833 | 0.26119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85071AP | lsdt9 | 85071 | ORNGWD52 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.33962 | 58.3 | 0.1 | 0.0833 | 0.33648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85072AP | lsdt9 | 85072 | ORNGWD53 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.35903 | 57.9 | 0.1 | 0.0833 | 0.60568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85073AP | lsdt9 | 85073 | PIONER19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.62827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85077AP | lsdt9 | 85077 | SHAW 52 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.45345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85080AP | lsdt9 | 85080 | SUNYSL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.51345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85081AP | lsdt9 | 85081 | SUNYSL19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.66862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85082AP | lsdt9 | 85082 | TURF 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.96314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85084AP | lsdt9 | 85084 | U-HILL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.44882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85085AP | lsdt9 | 85085 | U-HILL19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.74016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85086AP | lsdt9 | 85086 | WPHX 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.51405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85089AP | lsdt9 | 85089 | WPHX 17 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.81146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85090AP | lsdt9 | 85090 | GATEWY19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.36842 | 58.7 | 0.1 | 0.0833 | 0.33337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85091AP | lsdt9 | 85091 | SHAW 53 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.77927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85092AP | lsdt9 | 85092 | STOUT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.62168 | 57.9 | 0.1 | 0.0833 | 0.28812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85093AP | lsdt9 | 85093 | STOUT 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.4467 | 58.3 | 0.1 | 0.0833 | 0.41935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85094AP | lsdt9 | 85094 | PIONER3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.18724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85095AP | lsdt9 | 85095 | DAISYMTN | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.40082 | 57.9 | 0.1 | 0.0833 | 0.43004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85099AP | lsdt9 | 85099 | YALE 19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.64757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85100AP | lsdt9 | 85100 | YALE 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.15198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85101AP | lsdt9 | 85101 | NORTRRAN 10 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.63556 | 57.9 | 0.1 | 0.0833 | 0.36444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85102AP | lsdt9 | 85102 | NORTRRA20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.72842 | 57.9 | 0.1 | 0.0833 | 0.27158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85105AP | lsdt9 | 85105 | DV 27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.49197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85106AP | lsdt9 | 85106 | HARBOR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.33403 | 57.9 | 0.1 | 0.0833 | 0.38723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85193AP | lsdt9 | 85193 | HATFELD3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.19667 | 57.9 | 0.1 | 0.0833 | 0.28999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85194AP | lsdt9 | 85194 | HATFED11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.26086 | 58.7 | 0.1 | 0.0833 | 0.26112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85195AP | lsdt9 | 85195 | EGL 30 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85200AP | lsdt9 | 85200 | ACOMA 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.46852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85201AP | lsdt9 | 85201 | ACOMA 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.50477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85202AP | lsdt9 | 85202 | ALTADN51 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.9671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85203AP | lsdt9 | 85203 | ALTADN52 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.69347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85206AP | lsdt9 | 85206 | BLVD 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.62059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85207AP | lsdt9 | 85207 | BLVD 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.75621 | 59.3 | 15 | 0.0833 | 0.24379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85208AP | lsdt9 | 85208 | BUFALO 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.46613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85209AP | lsdt9 | 85209 | BUFALO11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.28889 | 58.5 | 0.1 | 0.0833 | 0.16542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85211AP | lsdt9 | 85211 | BUTTE 19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.40173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85212AP | lsdt9 | 85212 | BUTTE 27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.34216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85215AP | lsdt9 | 85215 | CACTUS35 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.5127 | 58.3 | 0.1 | 0.0833 | 0.26845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85217AP | lsdt9 | 85217 | CAMLBK11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.18065 | 58.5 | 0.1 | 0.0833 | 0.32178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85218AP | lsdt9 | 85218 | CAMLBK19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.47065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85219AP | lsdt9 | 85219 | CAMLBK27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.45906 | 57.9 | 0.1 | 0.0833 | 0.41624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85222AP | lsdt9 | 85222 | CENTRY12 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.95371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85223AP | lsdt9 | 85223 | CENTRY20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85224AP | lsdt9 | 85224 | CHAPRL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85225AP | lsdt9 | 85225 | CHAPRL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.31076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85226AP | lsdt9 | 85226 | CHNDLR 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.59753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85227AP | lsdt9 | 85227 | CHNDLR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.7292 | 57.9 | 0.1 | 0.0833 | 0.23369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85228AP | lsdt9 | 85228 | CLGRND11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.69177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85229AP | lsdt9 | 85229 | CLGRND19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.75303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85230AP | lsdt9 | 85230 | DALE 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.16863 | 58.5 | 0.1 | 0.0833 | 0.38588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85231AP | lsdt9 | 85231 | DALE 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.31906 | 58.5 | 0.1 | 0.0833 | 0.32518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85232AP | lsdt9 | 85232 | DESPNG 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.96145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85233AP | lsdt9 | 85233 | DESPNG11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.96176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85234AP | lsdt9 | 85234 | DIXILT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.27086 | 57.9 | 0.1 | 0.0833 | 0.70281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85235AP | lsdt9 | 85235 | DIXILT11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.96762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85236AP | lsdt9 | 85236 | DOUBLT51 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.65899 | 59.5 | 60 | 0.0833 | 0.31186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85238AP | lsdt9 | 85238 | DOWNIN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.43417 | 57.9 | 0.1 | 0.0833 | 0.31547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85239AP | lsdt9 | 85239 | DOWNIN11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.10798 | 58.3 | 0.1 | 0.0833 | 0.59611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85240AP | lsdt9 | 85240 | DSRTRG 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85241AP | lsdt9 | 85241 | DSRTRG11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.6209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85242AP | lsdt9 | 85242 | EASTRN11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.97822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85243AP | lsdt9 | 85243 | GAVILN43 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.62578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85244AP | lsdt9 | 85244 | EASTEN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.27911 | 59.5 | 60 | 0.0833 | 0.24077 | 58.3 | 0.1 | 0.0833 | 0.32697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85245AP | lsdt9 | 85245 | GILBRT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.57359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85246AP | lsdt9 | 85246 | GILBRT11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.34142 | 58.7 | 0.1 | 0.0833 | 0.42579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85247AP | lsdt9 | 85247 | HDGPTH 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.34424 | 58.3 | 0.1 | 0.0833 | 0.5312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85248AP | lsdt9 | 85248 | HDGPTH11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.67188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85249AP | lsdt9 | 85249 | INDBND 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85250AP | lsdt9 | 85250 | INDBND11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85252AP | lsdt9 | 85252 | JOMAX 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.30315 | 58.5 | 0.1 | 0.0833 | 0.32583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85253AP | lsdt9 | 85253 | EASTRN19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85254AP | lsdt9 | 85254 | LONEPK11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.66086 | 59.3 | 15 | 0.0833 | 0.3019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85255AP | lsdt9 | 85255 | MCCORM 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.49653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85256AP | lsdt9 | 85256 | MCCORM11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.96122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85257AP | lsdt9 | 85257 | MUMYMT51 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.41764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85258AP | lsdt9 | 85258 | MUMYMT53 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.9332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85259AP | lsdt9 | 85259 | PAPAGO 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.6023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85260AP | lsdt9 | 85260 | PAPAGO 7 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.48422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85261AP | lsdt9 | 85261 | PARDSE 4 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.96439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85262AP | lsdt9 | 85262 | PARDSE12 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.96367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85263AP | lsdt9 | 85263 | RAINTR 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.18193 | 58.9 | 0.1 | 0.0833 | 0.27662 | 58.3 | 0.1 | 0.0833 | 0.25092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85264AP | lsdt9 | 85264 | RAINTR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.27561 | 59.5 | 60 | 0.0833 | 0.26225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85265AP | lsdt9 | 85265 | RAWHID 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.52235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85266AP | lsdt9 | 85266 | RAWHID11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.35775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85269AP | lsdt9 | 85269 | REACH 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.56811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85270AP | lsdt9 | 85270 | RAINTR19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85271AP | lsdt9 | 85271 | RSG 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.34353 | 58.3 | 0.1 | 0.0833 | 0.35766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85272AP | lsdt9 | 85272 | RSG 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.51933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85273AP | lsdt9 | 85273 | SHEA 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.35218 | 58.7 | 0.1 | 0.0833 | 0.55701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85274AP | lsdt9 | 85274 | SHEA 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.45603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85275AP | lsdt9 | 85275 | STAGCH51 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.28718 | 58.9 | 0.1 | 0.0833 | 0.40379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85276AP | lsdt9 | 85276 | STAGCH52 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.24475 | 57.9 | 0.1 | 0.0833 | 0.37754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85277AP | lsdt9 | 85277 | TEMPE 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.80567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85279AP | lsdt9 | 85279 | THOMPK 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.96111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85280AP | lsdt9 | 85280 | THOMPK11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.96713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85281AP | lsdt9 | 85281 | RIOSAL19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.31478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85282AP | lsdt9 | 85282 | RIOSAL27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.18942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85283AP | lsdt9 | 85283 | DOVEVY 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.96343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85284AP | lsdt9 | 85284 | VIADON 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85285AP | lsdt9 | 85285 | VIADON11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85286AP | lsdt9 | 85286 | TEMPE 27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.41891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85289AP | lsdt9 | 85289 | DOVEVY11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.43072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85292AP | lsdt9 | 85292 | PARDSE20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.98514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85293AP | lsdt9 | 85293 | DOWNIN21 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.46898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85296AP | lsdt9 | 85296 | CLGRND 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.99562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85300AP | lsdt9 | 85300 | ARROWH 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.82025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85301AP | lsdt9 | 85301 | ARROWH11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.97743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85302AP | lsdt9 | 85302 | BEARDSLY | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.44395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85303AP | lsdt9 | 85303 | BELL 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.96944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85304AP | lsdt9 | 85304 | BELL 19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.67903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85305AP | lsdt9 | 85305 | DELRIO 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.96529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85307AP | lsdt9 | 85307 | DYSART11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.72537 | 58.3 | 0.1 | 0.0833 | 0.26955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85308AP | lsdt9 | 85308 | DYSART19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.55641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85309AP | lsdt9 | 85309 | EL SOL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.31716 | 57.9 | 0.1 | 0.0833 | 0.61218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85310AP | lsdt9 | 85310 | EL SOL19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.42797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85311AP | lsdt9 | 85311 | ET 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.34594 | 57.9 | 0.1 | 0.0833 | 0.33626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85313AP | lsdt9 | 85313 | GLENDL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85314AP | lsdt9 | 85314 | GLENDL15 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.63207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85316AP | lsdt9 | 85316 | GRNBRR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.71958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85319AP | lsdt9 | 85319 | HUMBUG11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.74304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85321AP | lsdt9 | 85321 | JAVELN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.26927 | 57.9 | 0.1 | 0.0833 | 0.73073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85322AP | lsdt9 | 85322 | JAVELN11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.99424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85327AP | lsdt9 | 85327 | MCMICKN3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.26912 | 58.5 | 0.1 | 0.0833 | 0.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85328AP | lsdt9 | 85328 | MCMICK11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.75762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85329AP | lsdt9 | 85329 | MTVIEW 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85330AP | lsdt9 | 85330 | MTVIEW11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.73035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85331AP | lsdt9 | 85331 | PEORIA 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85332AP | lsdt9 | 85332 | PEORIA11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.57018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85334AP | lsdt9 | 85334 | RIOVST 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.67733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85335AP | lsdt9 | 85335 | RIOVST11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.1857 | 58.9 | 0.1 | 0.0833 | 0.35865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85336AP | lsdt9 | 85336 | SKUNCK 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.70835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85337AP | lsdt9 | 85337 | SKUNCK11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.58741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85338AP | lsdt9 | 85338 | SPNGRD 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.67639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85339AP | lsdt9 | 85339 | SPNGRD11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.35607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85342AP | lsdt9 | 85342 | SURPRS11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.0833 | 0.37403 | 57.9 | 0.1 | 0.0833 | 0.37743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85343AP | lsdt9 | 85343 | SURPRS 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.22812 | 59.5 | 30 | 0.0833 | 0.34904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85349AP | lsdt9 | 85349 | COLWTR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.26233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85350AP | lsdt9 | 85350 | COLWTR19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85351AP | lsdt9 | 85351 | LTCHFL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.97835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85352AP | lsdt9 | 85352 | LTCHFL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.41428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85353AP | lsdt9 | 85353 | PIMA 20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.16494 | 57.9 | 0.1 | 0.0833 | 0.24928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85354AP | lsdt9 | 85354 | PIMA 10 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.46283 | 57.9 | 0.1 | 0.0833 | 0.53717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85355AP | lsdt9 | 85355 | SARVAL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.21932 | 58.7 | 0.1 | 0.0833 | 0.32057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85356AP | lsdt9 | 85356 | SARVAL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.54006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85358AP | lsdt9 | 85358 | COLTER 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85359AP | lsdt9 | 85359 | COLTER11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.42923 | 59.3 | 15 | 0.0833 | 0.10689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85362AP | lsdt9 | 85362 | TUTHIL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.35325 | 58.3 | 0.1 | 0.0833 | 0.2263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85363AP | lsdt9 | 85363 | BULARD 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.65216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85365AP | lsdt9 | 85365 | WLDFLR 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.36334 | 58.9 | 0.1 | 0.0833 | 0.39827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85366AP | lsdt9 | 85366 | TUTHIL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.43861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85367AP | lsdt9 | 85367 | WADDEL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.27112 | 58.3 | 0.1 | 0.0833 | 0.63099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85368AP | lsdt9 | 85368 | WADDEL19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.32013 | 58.3 | 0.1 | 0.0833 | 0.63153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85369AP | lsdt9 | 85369 | WLDFLR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.29715 | 58.9 | 0.1 | 0.0833 | 0.26744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85370AP | lsdt9 | 85370 | CLDRWD 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.38001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85371AP | lsdt9 | 85371 | CLDRWD11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.29741 | 57.9 | 0.1 | 0.0833 | 0.28605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85372AP | lsdt9 | 85372 | DYSART27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.6811 | 58.7 | 0.1 | 0.0833 | 0.3189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85376AP | lsdt9 | 85376 | PEBCRK 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.27782 | 59.3 | 15 | 0.0833 | 0.38723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85377AP | lsdt9 | 85377 | SURPRS20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.5273 | 58.7 | 0.1 | 0.0833 | 0.17153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85378AP | lsdt9 | 85378 | PEBCRK11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.65641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85379AP | lsdt9 | 85379 | HEARN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.53084 | 57.9 | 0.1 | 0.0833 | 0.46916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85380AP | lsdt9 | 85380 | HEARN 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.28904 | 58.5 | 0.1 | 0.0833 | 0.43854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85381AP | lsdt9 | 85381 | WSTWNG19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.42325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85382AP | lsdt9 | 85382 | FESTIV10 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.60862 | 58.9 | 0.1 | 0.0833 | 0.39138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85384AP | lsdt9 | 85384 | PLMVLY21 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.83228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85389AP | lsdt9 | 85389 | GRNWAY19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.56527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85390AP | lsdt9 | 85390 | VARNEY 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.84291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85391AP | lsdt9 | 85391 | VARNEY 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.32734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85392AP | lsdt9 | 85392 | PLMVLY25 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.59283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85399AP | lsdt9 | 85399 | CELEBORN20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85400AP | lsdt9 | 85400 | CELEBORN30 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.91674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85405AP | lsdt9 | 85405 | BUCKEYE | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.46557 | 58.5 | 0.1 | 0.0833 | 0.53443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85407AP | lsdt9 | 85407 | COTNCT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.86963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85408AP | lsdt9 | 85408 | FLYINGE | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.98187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85409AP | lsdt9 | 85409 | GILABD11 | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.079387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85411AP | lsdt9 | 85411 | GILLWEST | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85415AP | lsdt9 | 85415 | MORISTWN | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.71027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85419AP | lsdt9 | 85419 | PERRY 20 | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.63601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85421AP | lsdt9 | 85421 | SADDLEMT | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.99788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85422AP | lsdt9 | 85422 | TONOPAH | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.96735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85428AP | lsdt9 | 85428 | WINTRBRG | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.94664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85429AP | lsdt9 | 85429 | WATSON 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85431AP | lsdt9 | 85431 | EGGRCH11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.96499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85438AP | lsdt9 | 85438 | WATSON11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.33681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85439AP | lsdt9 | 85439 | FLORES | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.97473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85440AP | lsdt9 | 85440 | COTNCT11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.84303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85441AP | lsdt9 | 85441 | WESTPA20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85447AP | lsdt9 | 85447 | FAL 20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.54541 | 58.3 | 0.1 | 0.0833 | 0.45459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85503AP | lsdt9 | 85503 | COCNIN15 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.4353 | 58.9 | 0.1 | 0.0833 | 0.5647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85504AP | lsdt9 | 85504 | COCNIN21 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.71583 | 58.5 | 0.1 | 0.0833 | 0.28417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85512AP | lsdt9 | 85512 | SANDVG 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.58527 | 58.3 | 0.1 | 0.0833 | 0.38795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85513AP | lsdt9 | 85513 | SANDVG11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.58219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85515AP | lsdt9 | 85515 | SWITZR19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.12235 | 58.3 | 0.1 | 0.0833 | 0.87765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85516AP | lsdt9 | 85516 | TUBACITY | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.52902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85520AN | lsdt9 | 85520 | WILIAMS | 4.2 | AN | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.13967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85521AP | lsdt9 | 85521 | WMT 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.63906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85522AP | lsdt9 | 85522 | ELDEN 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.0833 | 0.49107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85524AP | lsdt9 | 85524 | PAULDN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.71841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85525AP | lsdt9 | 85525 | GREYBERS | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.96442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85599AP | lsdt9 | 85599 | ANTLOP27 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.52506 | 58.7 | 0.1 | 0.0833 | 0.47494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85600AP | lsdt9 | 85600 | ANTLOP19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.44678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85601AP | lsdt9 | 85601 | BALDMT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.41635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85602AP | lsdt9 | 85602 | BALDMT11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.44891 | 58.3 | 0.1 | 0.0833 | 0.34574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85603AP | lsdt9 | 85603 | CAPBUT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.94187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85606AP | lsdt9 | 85606 | CHNVLY11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.86213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85607AP | lsdt9 | 85607 | COPCYN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.98403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85608AP | lsdt9 | 85608 | COPCYN11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85612AP | lsdt9 | 85612 | DELANO 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.60876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85613AP | lsdt9 | 85613 | DELANO11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.51285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85614AP | lsdt9 | 85614 | DEWEY 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.52231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85618AP | lsdt9 | 85618 | LONEVL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.36541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85619AP | lsdt9 | 85619 | LONEVL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85628AP | lsdt9 | 85628 | PRCITY20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.55418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85629AP | lsdt9 | 85629 | QUAIL 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85630AP | lsdt9 | 85630 | SEDONA 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.92038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85631AP | lsdt9 | 85631 | SEDONA11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85632AP | lsdt9 | 85632 | STRMRG11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85634AP | lsdt9 | 85634 | WHTSPR11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.96808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85637AP | lsdt9 | 85637 | SUNDOG11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.69139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85638AP | lsdt9 | 85638 | CHNVLY 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.70839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85639AP | lsdt9 | 85639 | QUAIL 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85641AP | lsdt9 | 85641 | WHTSPR 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85642AP | lsdt9 | 85642 | CAPBUT11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.96954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85643AP | lsdt9 | 85643 | DEWEY 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.40848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85646AP | lsdt9 | 85646 | BAGDAD | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85670AP | lsdt9 | 85670 | DUPONT3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.52489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85704AP | lsdt9 | 85704 | SHOWLW12 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 0.61939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85706AP | lsdt9 | 85706 | SF 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85707AP | lsdt9 | 85707 | SF 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.84051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85714AP | lsdt9 | 85714 | PRECHCYN | 20.8 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.38207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85717AP | lsdt9 | 85717 | TONTO 11 | 20.8 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.68081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85722AP | lsdt9 | 85722 | MAZATEMP | 20.8 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.62368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85723AP | lsdt9 | 85723 | CORNVIL | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.96844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85742AP | lsdt9 | 85742 | SHOWLW20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85809AP | lsdt9 | 85809 | 32STRE11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.27108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85813AP | lsdt9 | 85813 | COCOPA 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.63804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85814AP | lsdt9 | 85814 | COCOPA11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.72717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85815AP | lsdt9 | 85815 | FOOTHL11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.64172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85816AP | lsdt9 | 85816 | FOOTHL19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.64027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85817AP | lsdt9 | 85817 | IVALON 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.2843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85818AP | lsdt9 | 85818 | IVALON11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.42916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85821AP | lsdt9 | 85821 | MAB 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.66004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85824AP | lsdt9 | 85824 | QUECHA19 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.65134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85827AP | lsdt9 | 85827 | SANLUS11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.42837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85829AP | lsdt9 | 85829 | TENTHST5 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.96549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85830AP | lsdt9 | 85830 | TENTHST8 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.96535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85832AP | lsdt9 | 85832 | RIVSIDE11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.96556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85835AP | lsdt9 | 85835 | CGAPS 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.28398 | 57.9 | 0.1 | 0.0833 | 0.27095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85836AP | lsdt9 | 85836 | TR 10 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 0.57734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85837AP | lsdt9 | 85837 | EASTGT 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.73374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85853AP | lsdt9 | 85853 | TOLTEC 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.85155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85854AP | lsdt9 | 85854 | VISTA 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.46464 | 58.5 | 0.1 | 0.0833 | 0.4917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85857AP | lsdt9 | 85857 | AGUILA | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85858AP | lsdt9 | 85858 | QUARTSIT | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.74851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85859AP | lsdt9 | 85859 | SALOME 2 | 12 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.51972 | 58.3 | 0.1 | 0.0833 | 0.44522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85860AP | lsdt9 | 85860 | UTTING10 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.82641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85862AP | lsdt9 | 85862 | PALOMNAS | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.96418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85863AP | lsdt9 | 85863 | UTTING20 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.1 | 0.0833 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85866AP | lsdt9 | 85866 | PICKET 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.62305 | 57.9 | 0.1 | 0.0833 | 0.34997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85872AP | lsdt9 | 85872 | PINAL | 21.6 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.0833 | 0.39827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85873AP | lsdt9 | 85873 | ARABY 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.0833 | 0.25605 | 58.5 | 0.1 | 0.0833 | 0.32499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85876AP | lsdt9 | 85876 | SANLUS 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.7513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85882AP | lsdt9 | 85882 | VISTA 11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.0833 | 0.88873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85888AP | lsdt9 | 85888 | MERRIL | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.0833 | 0.26796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85894AP | lsdt9 | 85894 | COOLIG T | 12.47 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.64433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85897AP | lsdt9 | 85897 | ARICA 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.76832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85995AP | lsdt9 | 85995 | CNTYLN11 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.1 | 0.0833 | 0.29207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85996AP | lsdt9 | 85996 | CNTYLN 3 | 12.5 | AP | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.0833 | 0.32589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1516082 | lsdt9 | 151608 | TURPEN2 | 69 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160406TP | lsdt9 | 160406 | EAST_LOOP | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57.9 | 0.1 | 0.065 | 0.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160411TP | lsdt9 | 160411 | IRVINGTON | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57 | 0.1 | 0.065 | 0.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160416TP | lsdt9 | 160416 | NORTH_LOOP2 | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160417TP | lsdt9 | 160417 | NORTH_EAST_4 | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57.4 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160418TP | lsdt9 | 160418 | NORTH_EAST_2 | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160425M | lsdt9 | 160425 | SOUTH | 47.2 | M | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 0.129 | 57 | 0.1 | 0.065 | 0.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160425TP | lsdt9 | 160425 | SOUTH | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 0.129 | 57 | 0.1 | 0.065 | 0.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160426TP | lsdt9 | 160426 | TUCSON | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.065 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160605TP | lsdt9 | 160605 | CIENEGA1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160614TP | lsdt9 | 160614 | DEL_CERRO1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160617TP | lsdt9 | 160617 | DMP6 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160618TP | lsdt9 | 160618 | DMP7 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160619TP | lsdt9 | 160619 | DREXEL1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 0.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160620TP | lsdt9 | 160620 | DREXEL2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160621TP | lsdt9 | 160621 | DREXEL3 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 0.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160623TP | lsdt9 | 160623 | EAST_LOOP2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 0.416 | 58.5 | 0.1 | 0.065 | 0.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160624TP | lsdt9 | 160624 | EAST_LOOP3 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160625TP | lsdt9 | 160625 | EAST_LOOP4 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57.4 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160629TP | lsdt9 | 160629 | GREENVALLEY1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 0.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160631TP | lsdt9 | 160631 | HARRISON1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160635TP | lsdt9 | 160635 | IRVINGTON1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 0.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160636TP | lsdt9 | 160636 | KINO1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57.9 | 0.1 | 0.065 | 0.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160638TP | lsdt9 | 160638 | LA_CANADA1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 0.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160639TP | lsdt9 | 160639 | LA_CANADA2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160641TP | lsdt9 | 160641 | LOS_REALES1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160642TP | lsdt9 | 160642 | LOS_REALES2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160647TP | lsdt9 | 160647 | MIDVALE1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.065 | 0.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160648TP | lsdt9 | 160648 | MIDVALE2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.065 | 0.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160650TP | lsdt9 | 160650 | NORTH_LOOP1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 0.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160651TP | lsdt9 | 160651 | NORTH_LOOP2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 0.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160654TP | lsdt9 | 160654 | NORTH_EAST1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57.4 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160655TP | lsdt9 | 160655 | NORTH_EAST2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160656TP | lsdt9 | 160656 | ORANGEGROVE1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 0.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160658TP | lsdt9 | 160658 | PANTANO1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160660TP | lsdt9 | 160660 | RANCHOVISTO1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 0.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160661TP | lsdt9 | 160661 | RANCHOVISTO2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 0.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160662TP | lsdt9 | 160662 | RANCHOVISTO3 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 60 | 0.065 | 0.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160665TP | lsdt9 | 160665 | RB_WILMOT1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 0.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160667TP | lsdt9 | 160667 | RILLITO1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 0.279 | 58.3 | 0.1 | 0.065 | 0.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160668TP | lsdt9 | 160668 | RILLITO2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.462 | 58.5 | 0.1 | 0.065 | 0.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160669TP | lsdt9 | 160669 | RILLITO3 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 0.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160671TP | lsdt9 | 160671 | ROBERTS1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160672TP | lsdt9 | 160672 | ROBERTS2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160674TP | lsdt9 | 160674 | SPANIS_TRL1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.065 | 0.427 | 58.9 | 0.1 | 0.065 | 0.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160675TP | lsdt9 | 160675 | SPANIS_TRL2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160677TP | lsdt9 | 160677 | SANTA_CRUZ1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 0.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160678TP | lsdt9 | 160678 | SANTA_CRUZ2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160680TP | lsdt9 | 160680 | SNYDER1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57.9 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160681TP | lsdt9 | 160681 | SNYDER2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 57.9 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160682TP | lsdt9 | 160682 | SNYDER3 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.3 | 15 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160683TP | lsdt9 | 160683 | SOUTH1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160691TP | lsdt9 | 160691 | TUCSON1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 0.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160692TP | lsdt9 | 160692 | TUCSON2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160693TP | lsdt9 | 160693 | TWENTY_SEC1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160694TP | lsdt9 | 160694 | TWENTY_SEC2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 59.5 | 30 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160698TP | lsdt9 | 160698 | VAIL2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.132 | 58.3 | 0.1 | 0.065 | 0.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160699TP | lsdt9 | 160699 | VAIL3 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160700TP | lsdt9 | 160700 | WEST_INA1 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.7 | 0.1 | 0.065 | 0.401 | 58.3 | 0.1 | 0.065 | 0.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160701TP | lsdt9 | 160701 | WEST_INA2 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.36 | 58.5 | 0.1 | 0.065 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160702TP | lsdt9 | 160702 | WEST_INA3 | 13.8 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.5 | 0.1 | 0.065 | 0.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160912TP | lsdt9 | 160912 | NORTH_LOOP1 | 47.2 | TP | [6 empty] | : | #9 | 0.05 | 0 | 58.3 | 0.1 | 0.065 | 0 | 57.9 | 0.1 | 0.065 | 0.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162200UE | lsdt9 | 162200 | HARRIS_UES | 230 | UE | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162400UE | lsdt9 | 162400 | DAVIS_UES | 69 | UE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.066666 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162903UE | lsdt9 | 162903 | GRIFFITH_WG | 69 | UE | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162903UM | lsdt9 | 162903 | GRIFFITH_WG | 69 | UM | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163400UE | lsdt9 | 163400 | BLACK_MESA1 | 69 | UE | [6 empty] | : | #9 | 0.05 | 0 | 58.9 | 0.1 | 0.065 | 0.192 | 58.5 | 0.1 | 0.065 | 0.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174001AE | lsdt9 | 174001 | DC-GCEC | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174002AE | lsdt9 | 174002 | SAFFORD | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174003AE | lsdt9 | 174003 | THATCHER | 69 | AE | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.2 | 0.083 | 0.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800121 | lsdt9 | 180012 | GOOD SPR1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800131 | lsdt9 | 180013 | GRN VAL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800141 | lsdt9 | 180014 | GRN VAL3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800151 | lsdt9 | 180015 | HAC PP | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800261 | lsdt9 | 180026 | SHADOW3 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800311 | lsdt9 | 180031 | SPR VAL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800321 | lsdt9 | 180032 | SPR VAL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800331 | lsdt9 | 180033 | WATER3 | 4.16 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800341 | lsdt9 | 180034 | ALTA3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800351 | lsdt9 | 180035 | ALTA4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800361 | lsdt9 | 180036 | ALTA5 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800371 | lsdt9 | 180037 | ANDREWS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800381 | lsdt9 | 180038 | ANTHEM1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800421 | lsdt9 | 180042 | AVERA1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800481 | lsdt9 | 180048 | LEAVITT3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800491 | lsdt9 | 180049 | LEAVITT1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800501 | lsdt9 | 180050 | BURNHAM1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800511 | lsdt9 | 180051 | CABANA1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800521 | lsdt9 | 180052 | CABANA3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800551 | lsdt9 | 180055 | CAREY8 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800561 | lsdt9 | 180056 | CAREY5 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800571 | lsdt9 | 180057 | CAREY7 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800581 | lsdt9 | 180058 | CHEYENNE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800591 | lsdt9 | 180059 | CHEYENNE3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800601 | lsdt9 | 180060 | CLAYMNT1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800611 | lsdt9 | 180061 | CLAYMNT2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800621 | lsdt9 | 180062 | CLAYMNT3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800631 | lsdt9 | 180063 | CLAYMNT4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800641 | lsdt9 | 180064 | CRAIG1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800651 | lsdt9 | 180065 | DEBUONO1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800661 | lsdt9 | 180066 | DEBUONO2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800671 | lsdt9 | 180067 | DECATUR3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800701 | lsdt9 | 180070 | ELCAPTN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800711 | lsdt9 | 180071 | ELRNCHO1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800721 | lsdt9 | 180072 | ELRNCHO2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800731 | lsdt9 | 180073 | FORD2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800741 | lsdt9 | 180074 | EXCALIB1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800751 | lsdt9 | 180075 | EXCALIB3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800761 | lsdt9 | 180076 | FAULKNR3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800771 | lsdt9 | 180077 | FLMINGO1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800781 | lsdt9 | 180078 | FLMINGO3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800791 | lsdt9 | 180079 | FORD1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800801 | lsdt9 | 180080 | GARCES2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800811 | lsdt9 | 180081 | HAVEN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800821 | lsdt9 | 180082 | HIGHLND1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800831 | lsdt9 | 180083 | HIGHLND3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800851 | lsdt9 | 180085 | HUALPAI1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800861 | lsdt9 | 180086 | JEAN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800871 | lsdt9 | 180087 | GARCES4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800891 | lsdt9 | 180089 | LVWASH1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800892 | lsdt9 | 180089 | LVWASH1 | 12.5 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800911 | lsdt9 | 180091 | LINDELL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800921 | lsdt9 | 180092 | LINDELL3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800931 | lsdt9 | 180093 | LNQUIST1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800941 | lsdt9 | 180094 | LORENZI1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800951 | lsdt9 | 180095 | LORENZI3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800961 | lsdt9 | 180096 | LYNNWOD1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800971 | lsdt9 | 180097 | MAYFAIR2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800981 | lsdt9 | 180098 | MAYFAIR3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800991 | lsdt9 | 180099 | MCDONLD3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801001 | lsdt9 | 180100 | MCDONLD4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801031 | lsdt9 | 180103 | MICHAEL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801041 | lsdt9 | 180104 | MICHAEL3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801051 | lsdt9 | 180105 | MILLER3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801081 | lsdt9 | 180108 | NELLIS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801091 | lsdt9 | 180109 | NELLIS3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801121 | lsdt9 | 180112 | NWEST5 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801131 | lsdt9 | 180113 | NWEST4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801141 | lsdt9 | 180114 | OASIS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801151 | lsdt9 | 180115 | OLIVE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801161 | lsdt9 | 180116 | OQUENDO1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801171 | lsdt9 | 180117 | OQUENDO3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801191 | lsdt9 | 180119 | PAWNEE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801221 | lsdt9 | 180122 | PEBBLE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801231 | lsdt9 | 180123 | PEBBLE3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801241 | lsdt9 | 180124 | POLARIS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801261 | lsdt9 | 180126 | QUAIL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801281 | lsdt9 | 180128 | RAINBOW1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801291 | lsdt9 | 180129 | RAINBOW3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801351 | lsdt9 | 180135 | SAHARA1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801361 | lsdt9 | 180136 | SAHARA3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801381 | lsdt9 | 180138 | SFN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801391 | lsdt9 | 180139 | SFS3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801401 | lsdt9 | 180140 | SHADOW4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801411 | lsdt9 | 180141 | SKELTON1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801441 | lsdt9 | 180144 | SPR MTN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801451 | lsdt9 | 180145 | SUMMRLN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801471 | lsdt9 | 180147 | SUZANNE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801481 | lsdt9 | 180148 | TAM1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801491 | lsdt9 | 180149 | TAM2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801501 | lsdt9 | 180150 | TENAYA1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801511 | lsdt9 | 180151 | TENAYA3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801521 | lsdt9 | 180152 | TOLSON 3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801531 | lsdt9 | 180153 | TONOPAH1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801541 | lsdt9 | 180154 | TONOPAH3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801551 | lsdt9 | 180155 | VALVIEW1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801561 | lsdt9 | 180156 | VALVIEW2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801571 | lsdt9 | 180157 | VEGAS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801591 | lsdt9 | 180159 | WARMSPR1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801601 | lsdt9 | 180160 | WARMSPR3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801611 | lsdt9 | 180161 | WASHBRN3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801621 | lsdt9 | 180162 | WASHTN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801631 | lsdt9 | 180163 | WASHTN3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801641 | lsdt9 | 180164 | WATER1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801651 | lsdt9 | 180165 | WESTSID5 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801661 | lsdt9 | 180166 | WESTSID6 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801691 | lsdt9 | 180169 | WIGWAM1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801701 | lsdt9 | 180170 | WIGWAM3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801711 | lsdt9 | 180171 | WILSON1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801721 | lsdt9 | 180172 | WINTRWD1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801731 | lsdt9 | 180173 | WINTRWD3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801741 | lsdt9 | 180174 | TRUMAN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801771 | lsdt9 | 180177 | ELKHORN3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801781 | lsdt9 | 180178 | SPEEDWY2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801791 | lsdt9 | 180179 | PEACE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801801 | lsdt9 | 180180 | BURNHAM3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801811 | lsdt9 | 180181 | HAVEN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801821 | lsdt9 | 180182 | HUALPAI3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801831 | lsdt9 | 180183 | SUMMRLN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801841 | lsdt9 | 180184 | TOLSON 4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801851 | lsdt9 | 180185 | STRIP1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801861 | lsdt9 | 180186 | CNCOURS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801871 | lsdt9 | 180187 | CNCOURS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801881 | lsdt9 | 180188 | WASHBRN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801891 | lsdt9 | 180189 | VEGAS3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801901 | lsdt9 | 180190 | IRONMTN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801911 | lsdt9 | 180191 | CACTUS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801921 | lsdt9 | 180192 | IRONMTN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801931 | lsdt9 | 180193 | PROCYON2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801961 | lsdt9 | 180196 | LONEMTN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801971 | lsdt9 | 180197 | GILMORE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801981 | lsdt9 | 180198 | BICENT1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801991 | lsdt9 | 180199 | TOMSIK2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802001 | lsdt9 | 180200 | CAMERO2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802011 | lsdt9 | 180201 | ROBINDL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802021 | lsdt9 | 180202 | VILAGE19 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802031 | lsdt9 | 180203 | ELKHORN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802041 | lsdt9 | 180204 | MTNEDGE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802051 | lsdt9 | 180205 | TROPICAL1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802061 | lsdt9 | 180206 | TROPICAL3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802071 | lsdt9 | 180207 | AVERA2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802091 | lsdt9 | 180209 | FAULKNR5 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802121 | lsdt9 | 180212 | ALTA6 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802141 | lsdt9 | 180214 | RAILRD1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802151 | lsdt9 | 180215 | RILEY2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802171 | lsdt9 | 180217 | LINCOLN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802181 | lsdt9 | 180218 | SPARTA2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802191 | lsdt9 | 180219 | COMMRCE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802201 | lsdt9 | 180220 | RAILRD3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802211 | lsdt9 | 180221 | ANTHEM3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802221 | lsdt9 | 180222 | FRIAS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802231 | lsdt9 | 180223 | GRTETON2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802241 | lsdt9 | 180224 | PECOS6 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802251 | lsdt9 | 180225 | ROBINDL3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802271 | lsdt9 | 180227 | SINATRA1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802281 | lsdt9 | 180228 | SINATRA2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802291 | lsdt9 | 180229 | COMMRCE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802301 | lsdt9 | 180230 | WESTSID3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802341 | lsdt9 | 180234 | REDROCK1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802351 | lsdt9 | 180235 | BELTWAY4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802361 | lsdt9 | 180236 | CRAIG3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802371 | lsdt9 | 180237 | OASIS3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802381 | lsdt9 | 180238 | PEACE3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802391 | lsdt9 | 180239 | POLARIS3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802401 | lsdt9 | 180240 | SKELTON2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802411 | lsdt9 | 180241 | SUZANNE3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802421 | lsdt9 | 180242 | WILSON2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802431 | lsdt9 | 180243 | STRIP2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802441 | lsdt9 | 180244 | QUAIL3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802451 | lsdt9 | 180245 | DECATUR4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802471 | lsdt9 | 180247 | ALLEN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802481 | lsdt9 | 180248 | ALLEN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802491 | lsdt9 | 180249 | WINTRWD7 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802501 | lsdt9 | 180250 | KEEHN1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802511 | lsdt9 | 180251 | ELCAPTN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802521 | lsdt9 | 180252 | FAULKNR4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802531 | lsdt9 | 180253 | GREENWAY1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802571 | lsdt9 | 180257 | GREENWAY4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802591 | lsdt9 | 180259 | PROCYON3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802601 | lsdt9 | 180260 | FRIAS1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802611 | lsdt9 | 180261 | RILEY3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802651 | lsdt9 | 180265 | BELTWAY3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802661 | lsdt9 | 180266 | LVWASH2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802662 | lsdt9 | 180266 | LVWASH2 | 12.5 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803001 | lsdt9 | 180300 | ALLEN3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803011 | lsdt9 | 180301 | ANDREWS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803021 | lsdt9 | 180302 | ANTHEM2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803051 | lsdt9 | 180305 | BICENT2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803061 | lsdt9 | 180306 | BURNHAM2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803071 | lsdt9 | 180307 | CABANA2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803081 | lsdt9 | 180308 | CACTUS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803091 | lsdt9 | 180309 | CAREY6 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803101 | lsdt9 | 180310 | CAREY9 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803111 | lsdt9 | 180311 | CHEYENNE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803121 | lsdt9 | 180312 | CNCOURS3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803131 | lsdt9 | 180313 | CRAIG2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803141 | lsdt9 | 180314 | DEBUONO3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803151 | lsdt9 | 180315 | DECATUR7 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803161 | lsdt9 | 180316 | DECATUR5 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803181 | lsdt9 | 180318 | ELRNCHO3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803191 | lsdt9 | 180319 | ELKHORN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803201 | lsdt9 | 180320 | EXCALIB2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803211 | lsdt9 | 180321 | EXCALIB4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803221 | lsdt9 | 180322 | FLMINGO2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803231 | lsdt9 | 180323 | FRIAS3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803241 | lsdt9 | 180324 | GARCES3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803251 | lsdt9 | 180325 | GILMORE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803261 | lsdt9 | 180326 | GRN VAL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803271 | lsdt9 | 180327 | GREENWAY2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803281 | lsdt9 | 180328 | HAVEN3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803291 | lsdt9 | 180329 | HIGHLND2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803311 | lsdt9 | 180331 | HUALPAI2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803321 | lsdt9 | 180332 | KEEHN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803331 | lsdt9 | 180333 | LEAVITT2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803341 | lsdt9 | 180334 | LINCOLN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803351 | lsdt9 | 180335 | LINDELL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803361 | lsdt9 | 180336 | LNQUIST2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803371 | lsdt9 | 180337 | LONEMTN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803381 | lsdt9 | 180338 | LORENZI2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803391 | lsdt9 | 180339 | LYNNWOD2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803401 | lsdt9 | 180340 | MAYFAIR4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803411 | lsdt9 | 180341 | MICHAEL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803421 | lsdt9 | 180342 | MILLER4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803451 | lsdt9 | 180345 | MTNEDGE3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803461 | lsdt9 | 180346 | NELLIS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803471 | lsdt9 | 180347 | OASIS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.4 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803481 | lsdt9 | 180348 | OQUENDO2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803491 | lsdt9 | 180349 | PAWNEE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803501 | lsdt9 | 180350 | PEACE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803521 | lsdt9 | 180352 | PEBBLE2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803531 | lsdt9 | 180353 | POLARIS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803551 | lsdt9 | 180355 | QUAIL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803561 | lsdt9 | 180356 | RAILRD2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803571 | lsdt9 | 180357 | RAINBOW2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803581 | lsdt9 | 180358 | REDROCK2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803591 | lsdt9 | 180359 | ROBINDL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803621 | lsdt9 | 180362 | SAHARA4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803631 | lsdt9 | 180363 | SAHARA2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803641 | lsdt9 | 180364 | SFN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803651 | lsdt9 | 180365 | SFS4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803661 | lsdt9 | 180366 | SHADOW5 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.2 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803681 | lsdt9 | 180368 | SPR VAL4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803691 | lsdt9 | 180369 | SPR VAL3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803701 | lsdt9 | 180370 | SUZANNE1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803711 | lsdt9 | 180371 | TAM3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803721 | lsdt9 | 180372 | TOMSIK3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803731 | lsdt9 | 180373 | TONOPAH2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803741 | lsdt9 | 180374 | TRUMAN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803751 | lsdt9 | 180375 | VALVIEW3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803761 | lsdt9 | 180376 | WARMSPR2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803771 | lsdt9 | 180377 | WASHBRN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803781 | lsdt9 | 180378 | WASHTN2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803791 | lsdt9 | 180379 | WASHTN4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803801 | lsdt9 | 180380 | WATER2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803831 | lsdt9 | 180383 | WIGWAM2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803841 | lsdt9 | 180384 | WINTRWD2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803851 | lsdt9 | 180385 | WINTRWD8 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.1 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803861 | lsdt9 | 180386 | ELKHORN4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803891 | lsdt9 | 180389 | BICENT3 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.6 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803921 | lsdt9 | 180392 | TOMSIK1 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1804001 | lsdt9 | 180400 | TENAYA2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1804011 | lsdt9 | 180401 | TROPICAL2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1804021 | lsdt9 | 180402 | VEGAS2 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1804031 | lsdt9 | 180403 | WESTSID7 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.8 | 0.15 | 0.066667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890035 | lsdt9 | 189003 | BE-MBUS | 24.94 | 5 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890067 | lsdt9 | 189006 | PA-MBUS | 24.94 | 7 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890068 | lsdt9 | 189006 | PA-MBUS | 24.94 | 8 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890092 | lsdt9 | 189009 | SA-MBUS | 24.94 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890121 | lsdt9 | 189012 | VA-MBUS | 24.94 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890122 | lsdt9 | 189012 | VA-MBUS | 24.94 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890231 | lsdt9 | 189023 | TH-MBUS | 24.94 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890232 | lsdt9 | 189023 | TH-MBUS | 24.94 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890233 | lsdt9 | 189023 | TH-MBUS | 24.94 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.21667 | 0.016667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3320411 | lsdt9 | 332041 | POTRERO D | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.1 | 0.14 | 58.7 | 0.1 | 0.1 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33204110 | lsdt9 | 332041 | POTRERO D | 115 | 10 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3320412 | lsdt9 | 332041 | POTRERO D | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 0.21 | 58.7 | 0.1 | 0.1 | 0.27 | 58.5 | 0.1 | 0.1 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3360081 | lsdt9 | 336008 | VICTOR | 60 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3390001 | lsdt9 | 339000 | PEORIA | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.1 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3390002 | lsdt9 | 339000 | PEORIA | 115 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.1 | 0.5 | 58.3 | 0.1 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3653421 | lsdt9 | 365342 | MRGNHILL_D1 | 21 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.1 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6024501 | lsdt9 | 602450 | MLNR-69 | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6100711 | lsdt9 | 610071 | CARO-12.5 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 0.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6107811 | lsdt9 | 610781 | VALE-12.5 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 0.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6121511 | lsdt9 | 612151 | CACK-34.5 | 35 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0 | 0.05 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6123311 | lsdt9 | 612331 | GARY-12.5 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0 | 0.05 | 0.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6140811 | lsdt9 | 614081 | BUGU-34.5_1 | 35 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.05 | 0.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6171211 | lsdt9 | 617121 | KUNA-12.5 | 13 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0 | 0.257 | 58.9 | 0 | 0 | 0.344 | 58.7 | 0 | 0.05 | 0.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6171811 | lsdt9 | 617181 | EKRT-34.5 | 35 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6210091 | lsdt9 | 621009 | ANACONDACITY | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
621009FX | lsdt9 | 621009 | ANACONDACITY | 100 | FX | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6210131 | lsdt9 | 621013 | DEER LODGE | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.13333 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
621022FX | lsdt9 | 621022 | BTE CONCENTR | 100 | FX | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 0.21 | 58.5 | 0.1 | 0.13333 | 0.11 | 58.3 | 0.1 | 0.13333 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6210231 | lsdt9 | 621023 | BTE MONT ST | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 0.24 | 58.5 | 0.1 | 0.13333 | 0.07 | 58.3 | 0.1 | 0.13333 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6210621 | lsdt9 | 621062 | DILLON CITY | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.13333 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6210821 | lsdt9 | 621082 | BTE INDUSTPK | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6210831 | lsdt9 | 621083 | BTE CONTDRIV | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.13333 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
621202FX | lsdt9 | 621202 | GOLDENSUNLGT | 161 | FX | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6220091 | lsdt9 | 622009 | GTF NO.WEST | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.13333 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6220131 | lsdt9 | 622013 | GTF CITY | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.13333 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6220141 | lsdt9 | 622014 | GTF EASTSIDE | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.13333 | 0.89 | 58.3 | 0.1 | 0.13333 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6221101 | lsdt9 | 622110 | GTF NO.EAST | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6221201 | lsdt9 | 622120 | GTF RIVERVW | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.13333 | 0.25 | 58.9 | 0.1 | 0.13333 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
622120PM | lsdt9 | 622120 | GTF RIVERVW | 100 | PM | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230081 | lsdt9 | 623008 | BLG RIMROCK | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 0.72 | 58.3 | 0.1 | 0.13333 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230091 | lsdt9 | 623009 | BLG STEAMPLT | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.13333 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230101 | lsdt9 | 623010 | BLG EIGHT ST | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 0.36 | 58.5 | 0.1 | 0.13333 | 0.43 | 58.3 | 0.1 | 0.13333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230331 | lsdt9 | 623033 | BLG MERIDIAN | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.13333 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230351 | lsdt9 | 623035 | BLG CITY | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.13333 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230431 | lsdt9 | 623043 | PARK CITY | 50 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230731 | lsdt9 | 623073 | BLG BELLROCK | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.13333 | 0.33 | 58.9 | 0.1 | 0.13333 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6230791 | lsdt9 | 623079 | BLG WICKS LN | 230 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6231001 | lsdt9 | 623100 | BLG KING AVE | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6231121 | lsdt9 | 623112 | COLSTRIP 115 | 115 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.13333 | 0.25 | 58.7 | 0.1 | 0.13333 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6231311 | lsdt9 | 623131 | BLG SHILOH | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.13333 | 0.16 | 59.1 | 0.1 | 0.13333 | 0.44 | 58.7 | 0.1 | 0.13333 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6231581 | lsdt9 | 623158 | RED LODGE | 50 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.1 | 0.13333 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6231801 | lsdt9 | 623180 | BLG EASTSIDE | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.13333 | 0.16 | 59.1 | 0.1 | 0.13333 | 0.39 | 58.7 | 0.1 | 0.13333 | 0.08 | 58.5 | 0.1 | 0.13333 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
623193BW | lsdt9 | 623193 | COLSTRIP | 69 | BW | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
623193R1 | lsdt9 | 623193 | COLSTRIP | 69 | R1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6240581 | lsdt9 | 624058 | LEWISTN BLVD | 50 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.13333 | 0.08 | 58.9 | 0.1 | 0.13333 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
626009FX | lsdt9 | 626009 | TRIDENT PLNT | 100 | FX | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6260241 | lsdt9 | 626024 | BZM EGALLATN | 50 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6260321 | lsdt9 | 626032 | BZM SOURDGH | 50 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6260781 | lsdt9 | 626078 | BZM RIVRSIDE | 50 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6261231 | lsdt9 | 626123 | BELGRADEWEST | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6261281 | lsdt9 | 626128 | BZM JCKRABIT | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6270011 | lsdt9 | 627001 | EAST HELENA | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6270151 | lsdt9 | 627015 | HLN VALLEY | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.13333 | 0.33 | 58.3 | 0.1 | 0.13333 | 0.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6270341 | lsdt9 | 627034 | HLN GOLFCOUR | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.13333 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6270351 | lsdt9 | 627035 | HLN WESTSIDE | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.13333 | 0.21 | 58.3 | 0.1 | 0.13333 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6270451 | lsdt9 | 627045 | HLN SO.SIDE | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6271311 | lsdt9 | 627131 | HLN EASTSIDE | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6290073 | lsdt9 | 629007 | MSL CITY | 100 | 3 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.13333 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6290074 | lsdt9 | 629007 | MSL CITY | 100 | 4 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.13333 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6290221 | lsdt9 | 629022 | MSL RUSSELL | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
629023FX | lsdt9 | 629023 | MSL INDUSTRL | 100 | FX | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6290421 | lsdt9 | 629042 | MSL HILLVIEW | 100 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.13333 | 0.48 | 58.7 | 0.1 | 0.13333 | 0.08 | 58.5 | 0.1 | 0.13333 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6291151 | lsdt9 | 629115 | HAMILTON SS | 69 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.13333 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
630021W1 | lsdt9 | 630021 | ROSEBUD MDU | 57 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.015 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
630031W1 | lsdt9 | 630031 | CUSTER WAPA | 69 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.083 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
630031W1 | lsdt9 | 630031 | CUSTER WAPA | 69 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 30 | 0.083 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
631053W1 | lsdt9 | 631053 | HAVRE WAPAT1 | 12.47 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.015 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
631060W1 | lsdt9 | 631060 | RUDYARD WAPA | 115 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
631072W1 | lsdt9 | 631072 | TIBER GEN | 12.47 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.015 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
631080W1 | lsdt9 | 631080 | VERONA HCE | 161 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.3 | 0.015 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6320041 | lsdt9 | 632004 | ASSINIBOINE | 161 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.015 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
632004W1 | lsdt9 | 632004 | ASSINIBOINE | 161 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.015 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
632082W1 | lsdt9 | 632082 | WHATLEY | 69 | W1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.5 | 60 | 0.083 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6400051 | lsdt9 | 640005 | MULLER | 120 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6400282 | lsdt9 | 640028 | BRUNSWCKBNK3 | 24.9 | 2 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6400291 | lsdt9 | 640029 | BRUNSWCKBNK4 | 12.5 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6400701 | lsdt9 | 640070 | GREGSTRT2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.7 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6400971 | lsdt9 | 640097 | SLVR SPG | 13.2 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401501 | lsdt9 | 640150 | AIRPORT2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 0.45437 | 59.1 | 0.1 | 0.05 | 0.12267 | 57.65 | 0.1 | 0.05 | 0.42296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401511 | lsdt9 | 640151 | BELVISTA2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.65 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401521 | lsdt9 | 640152 | GLENDALE2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 14.71 | 0.05 | 0.89588 | 59.3 | 15 | 0.05 | 0.10419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401531 | lsdt9 | 640153 | GREGSTRT3 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 15 | 0.05 | 0.3299 | 58.7 | 0.1 | 0.05 | 0.148 | 58.15 | 0.1 | 0.05 | 0.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401541 | lsdt9 | 640154 | MT ROSE2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401551 | lsdt9 | 640155 | NORTHWST2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.1 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401561 | lsdt9 | 640156 | RENO2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.5 | 0.1 | 0.05 | 0.82316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401571 | lsdt9 | 640157 | SPAN SPG2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401581 | lsdt9 | 640158 | STEAMBT2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 58.9 | 0.1 | 0.05 | 0.6575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401591 | lsdt9 | 640159 | VAL ROAD2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 57.65 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401601 | lsdt9 | 640160 | SUGARLF2 | 24.9 | 1 | [6 empty] | : | #9 | 0.05 | 0.05 | 59.3 | 0.1 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ensure this column is text. (Convert to text if necessary, =text(a2,0)

## mdf_tlin1 (hidden)
unique_ID | no. | bus | name | kv | ID | st | area | zone | Mbase | MbaseR | MODEL_LID | Input | Tf | Flag | Nfar | v1 | t1 | tcb1 | Sbus | signal1 | signal2
11011111031 | 1 | 11011 | ANTHONY | 115 | 1 | 11031 | BORDER | 115 | 1 | 1 | 0 | 0.05 | 0 | 11031 | 58.5 | 0.1 | 0.1 | 11011 | 2 | 0
11075111005 | 2 | 11075 | FELIPE | 69 | 1 | 11005 | ALAMO_R | 69 | 1 | 1 | 0 | 0.05 | 2 | 11129 | 58.3 | 0.1 | 0.1 | 11075 | 2 | 0
12087112105 | 3 | 12087 | WILLARD | 115 | 1 | 12105 | TORRANCE | 115 | 1 | 1 | 0 | 0 | 2 | 12105 | 59.5 | 60 | 0.083 | 12087 | 1 | 81
12100112167 | 4 | 12100 | GLADSTON | 115 | 1 | 12167 | HESS_TAP | 115 | 1 | 1 | 0 | 0 | 2 | 12116 | 58.9 | 0.1 | 0.083 | 12100 | 1 | 81
14002114077 | 5 | 14002 | MOENKOPI | 500 | 1 | 14077 | MOEN-ELD SC1 | 500 | 1 | 1 | 0 | 0 | 0 | 14077 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
14077114078 | 6 | 14077 | MOEN-ELD SC1 | 500 | 1 | 14078 | MOEN-ELD SC2 | 500 | 1 | 1 | 0 | 0 | 0 | 14078 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
14078114079 | 7 | 14078 | MOEN-ELD SC2 | 500 | 1 | 14079 | MOEN-ELD SC3 | 500 | 1 | 1 | 0 | 0 | 0 | 14079 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
14079124042 | 8 | 14079 | MOEN-ELD SC3 | 500 | 1 | 24042 | ELDORDO | 500 | 1 | 1 | 0 | 0 | 0 | 24042 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
15021129250 | 9 | 15021 | PALOVRDE | 500 | 1 | 29250 | PV_CLRVR_11 | 500 | 1 | 1 | 0 | 0 | 0 | 29250 | 57.9 | 1 | 0.0667 | 24900 | 0 | 0
15211114278 | 10 | 15211 | PINPKSRP | 230 | 1 | 14278 | PPAPS N | 230 | 1 | 1 | 0 | 0 | 1 | 14278 | 57.8 | 0.1 | 0.05 | 15211 | 2 | 0
15211214278 | 11 | 15211 | PINPKSRP | 230 | 2 | 14278 | PPAPS N | 230 | 2 | 1 | 0 | 0 | 1 | 14278 | 57.8 | 0.1 | 0.05 | 15211 | 2 | 0
18055119011 | 12 | 18055 | BC TAP | 230 | 1 | 19011 | MEAD N | 230 | 1 | 1 | 0 | 0 | 1 | 18003 | 57.9 | 1 | 0.067 | 19011 | 0 | 0
18450124572 | 13 | 18450 | H ALLEN | 500 | 1 | 24572 | HAE SVC | 500 | 1 | 1 | 0 | 0 | 0 | 24572 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
18461124097 | 14 | 18461 | LAUGHLIN1 | 500 | 1 | 24097 | MOHAVE | 500 | 1 | 1 | 0 | 0 | 0 | 24097 | 57.9 | 1 | 0.0833 | 24097 | 0 | 0
18462124097 | 15 | 18462 | LAUGHLIN2 | 500 | 1 | 24097 | MOHAVE | 500 | 2 | 1 | 0 | 0 | 0 | 24097 | 57.9 | 1 | 0.0667 | 24097 | 0 | 0
18505119011 | 16 | 18505 | AMARGOSA T1 | 230 | 1 | 19011 | MEAD N | 230 | 1 | 1 | 0 | 0 | 1 | 18006 | 57.9 | 1 | 0.067 | 19011 | 0 | 0
19011118004 | 17 | 19011 | MEAD N | 230 | 1 | 18004 | Arden | 230 | 1 | 1 | 0 | 0 | 1 | 18004 | 57.9 | 1 | 0.067 | 19011 | 0 | 0
19011218600 | 18 | 19011 | MEAD N | 230 | 2 | 18600 | EQUEST | 230 | 2 | 1 | 0 | 0 | 1 | 18600 | 57.9 | 1 | 0.067 | 19011 | 0 | 0
19012118600 | 19 | 19012 | MEAD S | 230 | 1 | 18600 | EQUEST | 230 | 1 | 1 | 0 | 0 | 1 | 18600 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
19012118674 | 20 | 19012 | MEAD S | 230 | 1 | 18674 | Greenway | 230 | 1 | 1 | 0 | 0 | 1 | 18674 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
19012119973 | 21 | 19012 | MEAD S | 230 | 1 | 19973 | MEAD B | 69 | 1 | 1 | 0 | 0 | 1 | 19973 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
19012119974 | 22 | 19012 | MEAD S | 230 | 1 | 19974 | MEAD A | 69 | 1 | 1 | 0 | 0 | 1 | 19974 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
19012124041 | 23 | 19012 | MEAD S | 230 | 1 | 24041 | ELDORDO | 230 | 1 | 1 | 0 | 0 | 1 | 24041 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
190122240015 | 24 | 19012 | MEAD S | 230 | 2 | 240015 | ELDORDO_C | 230 | 2 | 1 | 0 | 0 | 1 | 240015 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
19012E24019 | 25 | 19012 | MEAD S | 230 | E | 24019 | CAMINO | 230 | E | 1 | 0 | 0 | 1 | 24019 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
19012W24019 | 26 | 19012 | MEAD S | 230 | W | 24019 | CAMINO | 230 | W | 1 | 0 | 0 | 1 | 24019 | 57.9 | 1 | 0.067 | 19012 | 0 | 0
19020124017 | 27 | 19020 | Blythe | 161 | 1 | 24017 | Blythe-sc | 161 | 1 | 1 | 0 | 0 | 1 | 24017 | 57.9 | 1 | 0.067 | 19020 | 0 | 0
19022126046 | 28 | 19022 | DAVIS | 230 | 1 | 26046 | MCCULLGH | 230 | 1 | 1 | 0 | 0 | 1 | 19022 | 57.9 | 1 | 0.067 | 26046 | 0 | 0
19038118450 | 29 | 19038 | MEAD | 500 | 1 | 18450 | Harry Allen | 500 | 1 | 1 | 0 | 0 | 1 | 18450 | 57.9 | 1 | 0.067 | 19038 | 0 | 0
19042125402 | 30 | 19042 | Parker | 230 | 1 | 25402 | Gene | 230 | 1 | 1 | 0 | 0 | 1 | 25402 | 57.9 | 1 | 0.067 | 19042 | 0 | 0
19052114231 | 31 | 19052 | Liberty | 230 | 1 | 14231 | WESTWNGW | 230 | 1 | 1 | 0 | 0 | 1 | 14231 | 57.9 | 1 | 0.067 | 19052 | 0 | 0
19052215230 | 32 | 19052 | Liberty | 230 | 2 | 15230 | Rudd | 230 | 2 | 1 | 0 | 0 | 1 | 15230 | 57.9 | 1 | 0.067 | 19052 | 0 | 0
20075120078 | 33 | 20075 | KON-115 | 115 | 1 | 20078 | TRI-115 | 115 | 1 | 1 | 0 | 0 | 1 | 20075 | 58.5 | 0.1 | 0.08333 | 20075 | 0 | 0
20118122358 | 34 | 20118 | ROA-230 | 230 | 1 | 22358 | IMPRLVLY | 230 | 1 | 1 | 0 | 0 | 1 | 22358 | 57.9 | 0.03333 | 0.08333 | 20118 | 0 | 0
20149122609 | 35 | 20149 | TJI-230 | 230 | 1 | 22609 | OTAYMESA | 230 | 1 | 1 | 0 | 0 | 1 | 22609 | 57.9 | 0 | 0.08333 | 20149 | 0 | 0
22356121025 | 36 | 22356 | IMPRLVLY | 230 | 1 | 21025 | ELCENTSW | 230 | 1 | 1 | 0 | 0 | 0 | 21025 | 57.9 | 1 | 0.05 | 22356 | 0 | 0
22358120118 | 37 | 22358 | IV PFC | 230 | 1 | 20118 | ROA-230 | 230 | 1 | 1 | 0 | 0 | 0 | 20118 | 57.9 | 1 | 0.05 | 22358 | 0 | 0
22360122536 | 38 | 22360 | IMPRLVLY | 500 | 1 | 22536 | N.GILA | 500 | 1 | 1 | 0 | 0 | 0 | 22536 | 57.9 | 1 | 0.05 | 22360 | 0 | 0
22609120149 | 39 | 22609 | OTAYMESA | 230 | 1 | 20149 | TJI-230 | 230 | 1 | 1 | 0 | 0 | 0 | 20149 | 57.9 | 1 | 0.05 | 22609 | 0 | 0
24041118032 | 40 | 24041 | ELDORDO | 230 | 1 | 18032 | MAGNOLIA | 230 | 1 | 1 | 0 | 0 | 0 | 18032 | 57.9 | 1 | 0.0667 | 24041 | 0 | 0
24041225100 | 41 | 24041 | ELDORDO | 230 | 2 | 25100 | MERCHANT | 230 | 2 | 1 | 0 | 0 | 0 | 25100 | 57.9 | 1 | 0.0667 | 24041 | 0 | 0
24042126048 | 42 | 24042 | ELDORDO | 500 | 1 | 26048 | MCCULLGH | 500 | 1 | 1 | 0 | 0 | 0 | 26048 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
24076126269 | 43 | 24076 | LAGUBELL | 230 | 1 | 26269 | VEL G | 230 | 1 | 1 | 0 | 0 | 0 | 26269 | 57.9 | 1 | 0.0667 | 24076 | 0 | 0
24086126105 | 44 | 24086 | LUGO | 500 | 1 | 26105 | VICTORVL | 500 | 1 | 1 | 0 | 0 | 0 | 26105 | 57.9 | 1 | 0.0667 | 24086 | 0 | 0
24572124573 | 45 | 24572 | HAE SVC | 500 | 1 | 24573 | HAE SVCL | 500 | 1 | 1 | 0 | 0 | 0 | 24573 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
24573124042 | 46 | 24573 | HAE SVCL | 500 | 1 | 24042 | ELDORDO | 500 | 1 | 1 | 0 | 0 | 0 | 24042 | 57.9 | 1 | 0.0667 | 24042 | 0 | 0
24722124867 | 47 | 24722 | CONTROL | 55 | 1 | 24867 | TAP642 | 55 | 1 | 1 | 0 | 0 | 0 | 24867 | 57.9 | 1 | 0.0833 | 24722 | 0 | 0
24722124868 | 48 | 24722 | CONTROL | 55 | 1 | 24868 | TAP643 | 55 | 1 | 1 | 0 | 0 | 0 | 24868 | 57.9 | 1 | 0.0833 | 24722 | 0 | 0
24723124728 | 49 | 24723 | CONTROL | 115 | 1 | 24728 | INYO | 115 | 1 | 1 | 0 | 0 | 0 | 24728 | 57.9 | 1 | 0.0833 | 24723 | 0 | 0
24730124728 | 50 | 24730 | INYO PS | 115 | 1 | 24728 | INYO | 115 | 1 | 1 | 0 | 0 | 1 | 24728 | 57.9 | 1 | 0.083 | 24728 | 2 | 0
24806121007 | 51 | 24806 | MIRAGE | 230 | 1 | 21007 | CVSUB230 | 230 | 1 | 1 | 0 | 0 | 0 | 21007 | 57.9 | 1 | 0.0667 | 24806 | 0 | 0
24806121076 | 52 | 24806 | MIRAGE | 230 | 1 | 21076 | RAMON | 230 | 1 | 1 | 0 | 0 | 0 | 21076 | 57.9 | 1 | 0.0667 | 24806 | 0 | 0
24865124723 | 53 | 24865 | TAP188 | 115 | 1 | 24723 | CONTROL | 115 | 1 | 1 | 0 | 0 | 0 | 24723 | 57.9 | 1 | 0.0833 | 24723 | 0 | 0
24866124723 | 54 | 24866 | TAP189 | 115 | 1 | 24723 | CONTROL | 115 | 1 | 1 | 0 | 0 | 0 | 24723 | 57.9 | 1 | 0.0833 | 24723 | 0 | 0
25402125431 | 55 | 25402 | ! | ! | 1 | 25431 | GENE LX1 | 230 | 1X | 1 | 0 | 0 | 2 | 25413 | 59.3 | 0.7 | 0.1333 | 25413 | 0 | 0
25402125432 | 56 | 25402 | ! | ! | 1 | 25432 | GENE LX2 | 230 | 2X | 1 | 0 | 0 | 2 | 25414 | 59.3 | 0.7 | 0.1333 | 25414 | 0 | 0
25409125416 | 57 | 25409 | ! | ! | 1 | 25416 | INTAKEP2 | 6.9 | 2 | 1 | 0 | 0 | 2 | 25416 | 59.3 | 0.7 | 0.1333 | 25416 | 0 | 0
25410125415 | 58 | 25410 | ! | ! | 1 | 25415 | INTAKEP1 | 6.9 | 1 | 1 | 0 | 0 | 2 | 25415 | 59.3 | 0.7 | 0.1333 | 25415 | 0 | 0
25613125605 | 59 | 25613 | ! | ! | 1 | 25605 | EDMON1AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25605 | 59.3 | 0.1 | 0.05 | 25605 | 0 | 0
25613125606 | 60 | 25613 | ! | ! | 1 | 25606 | EDMON2AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25606 | 59.3 | 0.1 | 0.05 | 25606 | 0 | 0
25613125607 | 61 | 25613 | ! | ! | 1 | 25607 | EDMON3AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25607 | 59.3 | 0.1 | 0.05 | 25607 | 0 | 0
25613125608 | 62 | 25613 | ! | ! | 1 | 25608 | EDMON4AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25608 | 59.3 | 0.1 | 0.05 | 25608 | 0 | 0
25613125609 | 63 | 25613 | ! | ! | 1 | 25609 | EDMON5AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25609 | 59.3 | 0.1 | 0.05 | 25609 | 0 | 0
25613125610 | 64 | 25613 | ! | ! | 1 | 25610 | EDMON6AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25610 | 59.3 | 0.1 | 0.05 | 25610 | 0 | 0
25613125611 | 65 | 25613 | ! | ! | 1 | 25611 | EDMON7AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25611 | 59.3 | 0.1 | 0.05 | 25611 | 0 | 0
25613125612 | 66 | 25613 | ! | ! | 1 | 25612 | EDMON8AP | 14.4 | 1 | 1 | 0 | 0 | 2 | 25612 | 59.3 | 0.1 | 0.05 | 25612 | 0 | 0
25616125617 | 67 | 25616 | ! | ! | 1 | 25617 | PEARBMAP | 13.8 | 1 | 1 | 0 | 0 | 2 | 25617 | 59.3 | 0.1 | 0.05 | 25617 | 0 | 0
25616125618 | 68 | 25616 | ! | ! | 1 | 25618 | PEARBMBP | 13.8 | 1 | 1 | 0 | 0 | 2 | 25618 | 59.3 | 0.1 | 0.05 | 25618 | 0 | 0
25616125619 | 69 | 25616 | ! | ! | 1 | 25619 | PEARBMCP | 13.8 | 1 | 1 | 0 | 0 | 2 | 25619 | 59.3 | 0.1 | 0.05 | 25619 | 0 | 0
25616125620 | 70 | 25616 | ! | ! | 1 | 25620 | PEARBMDP | 13.8 | 1 | 1 | 0 | 0 | 2 | 25620 | 59.3 | 0.1 | 0.05 | 25620 | 0 | 0
25621125614 | 71 | 25621 | ! | ! | 1 | 25614 | OSO A P | 13.2 | 1 | 1 | 0 | 0 | 2 | 25614 | 59.3 | 0.1 | 0.05 | 25614 | 0 | 0
25621125615 | 72 | 25621 | ! | ! | 1 | 25615 | OSO B P | 13.2 | 1 | 1 | 0 | 0 | 2 | 25615 | 59.3 | 0.1 | 0.05 | 25615 | 0 | 0
26041164056 | 73 | 26041 | INTERMT | 230 | 1 | 64056 | GONDER | 345 | 1 | 1 | 0 | 0 | 1 | 64056 | 57.9 | 1 | 0.083 | 64056 | 2 | 0
26043165995 | 74 | 26043 | INTERMT | 345 | 1 | 65995 | MONA | 345 | 1 | 1 | 0 | 0 | 1 | 65995 | 57.9 | 1 | 0.083 | 65995 | 2 | 0
26043265995 | 75 | 26043 | INTERMT | 345 | 2 | 65995 | MONA | 345 | 2 | 1 | 0 | 0 | 1 | 65995 | 57.9 | 1 | 0.083 | 65995 | 2 | 0
26044119038 | 76 | 26044 | MARKETPL | 500 | 1 | 19038 | MEAD | 500 | 1 | 1 | 0 | 0 | 1 | 19038 | 57.9 | 1 | 0.083 | 19038 | 2 | 0
26046119022 | 77 | 26046 | MCCULLGH | 230 | 1 | 19022 | DAVIS | 230 | 1 | 1 | 0 | 0 | 1 | 19022 | 57.9 | 1 | 0.083 | 19022 | 2 | 0
26048124042 | 78 | 26048 | MCCULLGH | 500 | 1 | 24042 | ELDORADO | 500 | 1 | 1 | 0 | 0 | 1 | 24042 | 57.9 | 1 | 0.083 | 24042 | 2 | 0
26094E24147 | 79 | 26094 | SYLMARLA | 230 | E | 24147 | SYLMAR S | 230 | E | 1 | 0 | 0 | 1 | 24147 | 57.9 | 1 | 0.083 | 24147 | 2 | 0
26094F24147 | 80 | 26094 | SYLMARLA | 230 | F | 24147 | SYLMAR S | 230 | F | 1 | 0 | 0 | 1 | 24147 | 57.9 | 1 | 0.083 | 24147 | 2 | 0
26098124114 | 81 | 26098 | SYLMAR220 | 230 | 1 | 24114 | PARDEE | 230 | 1 | 1 | 0 | 0 | 0 | 24114 | 57.9 | 1 | 0.0667 | 26098 | 0 | 0
26098124114 | 82 | 26098 | SYLMAR220 | 230 | 1 | 24114 | PARDEE | 230 | 2 | 1 | 0 | 0 | 0 | 24114 | 57.9 | 1 | 0.0667 | 26098 | 0 | 0
26098124036 | 83 | 26098 | SYLMAR220 | 230 | 1 | 24036 | EAGLROCK | 230 | 1 | 1 | 0 | 0 | 0 | 24036 | 57.9 | 1 | 0.0667 | 26098 | 0 | 0
26098124059 | 84 | 26098 | SYLMAR220 | 230 | 1 | 24059 | GOULD | 230 | 1 | 1 | 0 | 0 | 0 | 24059 | 57.9 | 1 | 0.0667 | 26098 | 0 | 0
26105124086 | 85 | 26105 | VICTORVL | 500 | 1 | 24086 | LUGO | 500 | 1 | 1 | 0 | 0 | 1 | 24086 | 57.9 | 1 | 0.083 | 24086 | 2 | 0
26123114003 | 86 | 26123 | CRYSTAL | 500 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | 0 | 0 | 1 | 14003 | 57.9 | 1 | 0.083 | 14003 | 2 | 0
26268E27248 | 87 | 26268 | TOL E | 230 | E | 27248 | Toluca69 | 69 | E | 1 | 0 | 0 | 1 | 27248 | 57.9 | 1 | 0.083 | 27248 | 2 | 0
26268F27248 | 88 | 26268 | TOL E | 230 | F | 27248 | Toluca69 | 69 | F | 1 | 0 | 0 | 1 | 27248 | 57.9 | 1 | 0.083 | 27248 | 2 | 0
273615327338 | 89 | 27361 | Airway 1 | 69 | 53 | 27338 | Kellog | 69 | 53 | 1 | 0 | 0 | 1 | 27338 | 57.9 | 1 | 0.083 | 27338 | 2 | 0
273625427338 | 90 | 27362 | Airway 2 | 69 | 54 | 27338 | Kellog | 69 | 54 | 1 | 0 | 0 | 1 | 27338 | 57.9 | 1 | 0.083 | 27338 | 2 | 0
273635527338 | 91 | 27363 | Airway 3 | 69 | 55 | 27338 | Kellog | 69 | 55 | 1 | 0 | 0 | 1 | 27338 | 57.9 | 1 | 0.083 | 27338 | 2 | 0
29250129251 | 92 | 29250 | PV_CLRVR_11 | 500 | 1 | 29251 | PV_CLRVR_12 | 500 | 1 | 1 | 0 | 0 | 0 | 29251 | 57.9 | 1 | 0.0667 | 24900 | 0 | 0
29251124900 | 93 | 29251 | PV_CLRVR_12 | 500 | 1 | 24900 | COLRIVER | 500 | 1 | 1 | 0 | 0 | 0 | 24900 | 57.9 | 1 | 0.0667 | 24900 | 0 | 0
40025140494 | 94 | 40025 | ALBANY | 115 | 1 | 40494 | HALSEY_MI_1 # | 115 | 1 | 1 | 0 | 40494 | 59.5 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
40047147087 | 95 | 40047 | ALVEY_N | 115 | 1 | 47087 | TENTH_ST | 115 | 1 | 1 | 0 | 0.05 | 2 | 47087 | 59 | 0.177 | 0.05 | 0 | 0 | 0
40048141013 | 96 | 40048 | ALVEY_S | 115 | 1 | 41013 | SPRINGFIELD | 115 | 1 | 1 | 0 | 0.05 | 2 | 41013 | 59 | 0.177 | 0.05 | 0 | 0 | 0
40087140113 | 97 | 40087 | BELL | 115 | 1 | 40113 | BIGELOW+ | 115 | 2 | 1 | 0 | 0.05 | 2 | 40113 | 59 | 0 | 0.05 | 0 | 0 | 0
40203147135 | 98 | 40203 | CHEHALIS | 115 | 1 | 47135 | CHEHALIS # | 115 | 1 | 1 | 0 | 47135 | 59.5 | 60 | 0.05 | 0 | 0 | 0 | 0 | 0
40247141039 | 99 | 40247 | COLUMBIA_F | 115 | 1 | 41039 | STILLWATER+ | 115 | 1 | 1 | 0 | 0.05 | 2 | 41039 | 59 | 0.1 | 0.05 | 0 | 0 | 0
40387140385 | 100 | 40387 | ELLENSBUR | 115 | 1 | 40385 | E_ELLENSBUR # | 115 | 1 | 1 | 0 | 40385 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0
40387142389 | 101 | 40387 | ELLENSBUR | 115 | 1 | 42389 | CLYMER | 115 | 1 | 1 | 0 | 0.05 | 2 | 42389 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0
40395140815 | 102 | 40395 | EUGENE | 115 | 1 | 40815 | VA_PARKER+ | 115 | 1 | 1 | 0 | 0.05 | 2 | 40815 | 58.8 | 0.1 | 0.05 | 0 | 0 | 0
40401147293 | 103 | 40401 | FAIRMOUNT | 115 | 1 | 47293 | DISCOVERY_B # | 115 | 1 | 1 | 0 | 47293 | 59 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0
40415140416 | 104 | 40415 | FIDALGO | 69 | 1 | 40416 | DECATUR # | 69 | EQ | 1 | 0 | 41233 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0
40440141405 | 105 | 40440 | FRANKLIN_E | 115 | 1 | 41405 | HEDGES1 # | 115 | 1 | 1 | 0 | 41405 | 59.3 | 0.12 | 0.05 | 0 | 0 | 0 | 0 | 0
40442141406 | 106 | 40442 | FRANKLIN_W | 115 | 1 | 41406 | HEDGES2 # | 115 | 2 | 1 | 0 | 41406 | 59.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0
40649147414 | 107 | 40649 | LEXINGTON | 115 | 1 | 47414 | JOHN_ST | 115 | 1 | 1 | 0 | 0.05 | 2 | 47414 | 59.3 | 0.1 | 0.05 | 0 | 0 | 0
40649147430 | 108 | 40649 | LEXINGTON | 115 | 1 | 47430 | OLY_PIPE # | 115 | 1 | 1 | 0 | 47430 | 59.3 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0
406871300002 | 109 | 40687 | MALIN | 500 | 1 | 300002 | MN_RM_11 | 500 | 1 | 1 | 0 | 0 | 1 | 40687 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
406871300004 | 110 | 40687 | MALIN | 500 | 1 | 300004 | MN_RM_21 | 500 | 2 | 1 | 0 | 0 | 1 | 40687 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
40843147565 | 111 | 40843 | PORT_ANG | 115 | 1 | 47565 | LIBERTY_STAT | 115 | 1 | 1 | 0 | 0.05 | 2 | 47562 | 59.5 | 30 | 0.05 | 0 | 0 | 0
40885141069 | 112 | 40885 | RICHLAND | 115 | 1 | 41069 | THAYER+ | 115 | 1 | 1 | 0 | 0.05 | 2 | 41069 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0
40893147048 | 113 | 40893 | ROGUE | 115 | 1 | 47048 | GLDBCHL1 | 115 | 1 | 1 | 0 | 0.05 | 2 | 47048 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0
40893147064 | 114 | 40893 | ROGUE | 115 | 1 | 47064 | GLDBCHL2 # | 115 | 2 | 1 | 0 | 47064 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0
40897147163 | 115 | 40897 | ROSS | 115 | 1 | 47163 | GRAND | 115 | 1 | 1 | 0 | 0.05 | 2 | 47163 | 58.8 | 0.083 | 0.05 | 0 | 0 | 0
40897147242 | 116 | 40897 | ROSS | 115 | 1 | 47242 | SW52 | 115 | 1 | 1 | 0 | 0.05 | 2 | 47242 | 59.3 | 0.083 | 0.05 | 0 | 0 | 0
40985147220 | 117 | 40985 | SILVER_CK | 69 | 1 | 47220 | SALKUM+ | 69 | 1 | 1 | 0 | 0.05 | 2 | 47220 | 59.3 | 0.1 | 0.05 | 0 | 0 | 0
41089140113 | 118 | 41089 | TRENTWOOD | 115 | 1 | 40113 | BIGELOW+ | 115 | 2 | 1 | 0 | 0.05 | 2 | 40113 | 59 | 0 | 0.05 | 0 | 0 | 0
41089141117 | 119 | 41089 | TRENTWOOD | 115 | 1 | 41117 | VERA # | 115 | 1 | 1 | 0 | 41117 | 59 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
41147147375 | 120 | 41147 | WHITE_BLUF_1 | 115 | 1 | 47375 | GATEWAY | 115 | 1 | 1 | 0 | 0.05 | 2 | 41009 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0
41148147271 | 121 | 41148 | WHITE_BLUF_2 | 115 | 1 | 47271 | SAND_HILL+ | 115 | 1 | 1 | 0 | 0.05 | 2 | 47271 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0
42110142189 | 122 | 42110 | FREDONIA | 115 | 1 | 42189 | WILSON P | 115 | 1 | 1 | 0 | 0 | 2 | 42189 | 58.6 | 0.1 | 0.05 | 42110 | 0 | 0
42118141235 | 123 | 42118 | FIDALGO | 115 | 1 | 41235 | LOPEZ4 | 115 | 4 | 1 | 0 | 0.05 | 2 | 41235 | 58.6 | 0.1 | 0.05 | 0 | 0 | 0
42200142231 | 124 | 42200 | WHIDBY N | 115 | 1 | 42231 | SWANTOWN | 115 | 1 | 1 | 0 | 0 | 0 | 42201 | 58.8 | 0.1 | 0.05 | 0 | 0.1 | 0
42200142231 | 125 | 42200 | WHIDBY N | 115 | 1 | 42231 | SWANTOWN | 115 | 1 | 1 | 0 | 0.05 | 0 | 42201 | 0.91 | 5 | 0.1 | 0 | 0 | 0
42202142222 | 126 | 42202 | WHIDBY S | 115 | 1 | 42222 | COUPVILL | 115 | 1 | 1 | 0 | 0 | 0 | 42201 | 58.8 | 0.1 | 0.05 | 0 | 0.1 | 0
42202142222 | 127 | 42202 | WHIDBY S | 115 | 1 | 42222 | COUPVILL | 115 | 1 | 1 | 0 | 0.05 | 0 | 42201 | 0.91 | 5 | 0.1 | 0 | 0 | 0
42303142388 | 128 | 42303 | LAKESIDE | 115 | 1 | 42388 | COLLEGEP | 115 | 1 | 1 | 0 | 0 | 0 | 42415 | 58.6 | 0.1 | 0.05 | 0 | 0.1 | 0
42303142452 | 129 | 42303 | LAKESIDE | 115 | 1 | 42452 | SOMERSET | 115 | 1 | 1 | 0 | 0 | 0 | 42524 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42305142381 | 130 | 42305 | NOVELTY | 115 | 1 | 42381 | AMESLKTP | 115 | 1 | 1 | 0 | 0 | 0 | 42307 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42307142424 | 131 | 42307 | LKTRAD | 115 | 1 | 42424 | MIRRORNT | 115 | 1 | 1 | 0 | 0 | 0 | 42508 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42307142440 | 132 | 42307 | LKTRAD | 115 | 1 | 42440 | PINELAKE | 115 | 1 | 1 | 0 | 0 | 0 | 42305 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42310142403 | 133 | 42310 | COTAGEBR | 115 | 1 | 42403 | HOLLYWD | 115 | 1 | 1 | 0 | 0 | 0 | 42325 | 59.3 | 15.2333 | 0.05 | 42310 | 0 | 0
42325142463 | 134 | 42325 | MORLANDS | 115 | 1 | 42463 | WAYNE | 115 | 1 | 1 | 0 | 0 | 0 | 42310 | 59.3 | 15.2333 | 0.05 | 42325 | 0 | 0
42415142413 | 135 | 42415 | ARDMORE | 115 | 1 | 42413 | LAKEHILL | 115 | 1 | 1 | 0 | 0 | 0 | 42303 | 58.6 | 0.1 | 0.05 | 0 | 0.1 | 0
42502142656 | 136 | 42502 | TALBOT | 115 | 1 | 42656 | VICTORIA | 115 | 1 | 1 | 0 | 0 | 0 | 42504 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42504142614 | 137 | 42504 | OBRIEN | 115 | 1 | 42614 | LIQ. AIR | 115 | 1 | 1 | 0 | 0 | 0 | 42502 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42504142657 | 138 | 42504 | OBRIEN | 115 | 1 | 42657 | W.AUBURN | 115 | 1 | 1 | 0 | 0 | 0 | 42701 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42506142588 | 139 | 42506 | CHRISTOP | 115 | 1 | 42588 | CAMBRIDG | 115 | 1 | 1 | 0 | 0 | 0 | 42520 | 59.5 | 60.2333 | 0.05 | 42506 | 0 | 0
42508142617 | 140 | 42508 | BERRYDAL | 115 | 1 | 42617 | LKMERIDI | 115 | 1 | 1 | 0 | 0 | 0 | 42511 | 59.2 | 0.1 | 0.05 | 0 | 0.1 | 0
42508142618 | 141 | 42508 | BERRYDAL | 115 | 1 | 42618 | LKWILDR | 115 | 1 | 1 | 0 | 0 | 0 | 42307 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42508142651 | 142 | 42508 | BERRYDAL | 115 | 1 | 42651 | SOOSCRK | 115 | 1 | 1 | 0 | 0 | 0 | 42701 | 59.2 | 0.1 | 0.05 | 0 | 0.1 | 0
42509142510 | 143 | 42509 | KRAINCOR | 115 | 1 | 42510 | KRAINCOR | 57.5 | 1 | 1 | 0 | 0.05 | 0 | 42532 | 0.9 | 3.5 | 0.1 | 0 | 0 | 0
42510142532 | 144 | 42510 | KRAINCOR | 57.5 | 1 | 42532 | STEVNSON | 57.5 | 1 | 1 | 0 | 0 | 0 | 42706 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42510142579 | 145 | 42510 | KRAINCOR | 57.5 | 1 | 42579 | WABASH | 57.5 | 1 | 1 | 0 | 0 | 0 | 42702 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42511142643 | 146 | 42511 | TALBOT N | 115 | 1 | 42643 | ROLLHLS | 115 | 1 | 1 | 0 | 0 | 0 | 42508 | 59.2 | 0.1 | 0.05 | 0 | 0.1 | 0
42513142599 | 147 | 42513 | OBRIEN N | 115 | 1 | 42599 | FALCON | 115 | 1 | 1 | 0 | 0 | 0 | 42525 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42514142645 | 148 | 42514 | OBRIEN S | 115 | 1 | 42645 | S.DMOINE | 115 | 1 | 1 | 0 | 0 | 0 | 42950 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42520142588 | 149 | 42520 | MIDWAYP | 115 | 1 | 42588 | CAMBRIDG | 115 | 1 | 1 | 0 | 0 | 0 | 42506 | 59.5 | 60.2333 | 0.05 | 42520 | 0 | 0
42520142662 | 150 | 42520 | MIDWAYP | 115 | 1 | 42662 | ZENITH | 115 | 1 | 1 | 0 | 0 | 0 | 42530 | 59.5 | 30.2333 | 0.05 | 42520 | 0 | 0
42524142592 | 151 | 42524 | SHUF115W | 115 | 1 | 42592 | EARLGTON | 115 | 1 | 1 | 0 | 0 | 0 | 42513 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42525142622 | 152 | 42525 | SHUF115E | 115 | 1 | 42622 | MER.IS.T | 115 | 1 | 1 | 0 | 0 | 0 | 42303 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42530142612 | 153 | 42530 | STARWOOD | 115 | 1 | 42612 | LAKOTA | 115 | 1 | 1 | 0 | 0 | 0 | 42520 | 59.5 | 30.2333 | 0.05 | 42530 | 0 | 0
42701142595 | 154 | 42701 | WHITRV N | 115 | 1 | 42595 | ELLNGTAP | 115 | 1 | 1 | 0 | 0 | 0 | 42504 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42701142650 | 155 | 42701 | WHITRV N | 115 | 1 | 42650 | SHERWD T | 115 | 1 | 1 | 0 | 0 | 0 | 42508 | 59.2 | 0.1 | 0.05 | 0 | 0.1 | 0
42701142753 | 156 | 42701 | WHITRV N | 115 | 1 | 42753 | EDGEWOOD | 115 | 1 | 1 | 0 | 0 | 0 | 42704 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42702142765 | 157 | 42702 | WHITE RV | 57.5 | 1 | 42765 | LK.TAPPS | 57.5 | 1 | 1 | 0 | 0 | 0 | 42510 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42704142778 | 158 | 42704 | ALDERTON | 115 | 1 | 42778 | STEWART | 115 | 1 | 1 | 0 | 0 | 0 | 42701 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
42705142706 | 159 | 42705 | ELECTHTS | 115 | 1 | 42706 | ELECTHTS | 57.5 | 1 | 1 | 0 | 0.05 | 0 | 42532 | 0.86 | 3.5 | 0.1 | 0 | 0 | 0
42706142786 | 160 | 42706 | ELECTHTS | 57.5 | 1 | 42786 | WILKNSON | 57.5 | 1 | 1 | 0 | 0 | 0 | 42510 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42805142885 | 161 | 42805 | ST CLR E | 115 | 1 | 42885 | TANGLEWD | 115 | 1 | 1 | 0 | 0 | 0 | 42809 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42809142876 | 162 | 42809 | OLY P N | 115 | 1 | 42876 | MCKINLY | 115 | 1 | 1 | 0 | 0 | 0 | 42805 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42809142877 | 163 | 42809 | OLY P N | 115 | 1 | 42877 | MOTTMAN | 115 | 1 | 1 | 0 | 0 | 0 | 42815 | 59.2 | 0.1 | 0.05 | 0 | 0.1 | 0
42815142866 | 164 | 42815 | WEST OLY | 115 | 1 | 42866 | ELDINLET | 115 | 1 | 1 | 0 | 0 | 0 | 42809 | 59.2 | 0.1 | 0.05 | 0 | 0.1 | 0
42896142873 | 165 | 42896 | PL.GLADE | 115 | 1 | 42873 | PLG_TAP | 115 | 1 | 1 | 0 | 0 | 0 | 42873 | 59 | 0.1 | 0.05 | 0 | 0.1 | 0
42902142953 | 166 | 42902 | BREMERTN | 115 | 1 | 42953 | MCWILLY | 115 | 1 | 1 | 0 | 0 | 0 | 42905 | 58.8 | 0.1 | 0.05 | 0 | 0.1 | 0
42905140077 | 167 | 42905 | FOSSCNRS | 115 | 1 | 40077 | BANGOR | 115 | 1 | 1 | 0 | 0 | 0 | 40611 | 58.8 | 0.1 | 0.05 | 0 | 0.1 | 0
42907142933 | 168 | 42907 | VALLYJCT | 115 | 1 | 42933 | C KITSAP | 115 | 1 | 1 | 0 | 0 | 0 | 40612 | 58.8 | 0.1 | 0.05 | 0 | 0.1 | 0
42907142981 | 169 | 42907 | VALLYJCT | 115 | 1 | 42981 | TRACYTON | 115 | 1 | 1 | 0 | 0 | 0 | 42910 | 58.8 | 0.1 | 0.05 | 0 | 0.1 | 0
42950142942 | 170 | 42950 | LONG LK | 115 | 1 | 42942 | FRAGARIA | 115 | 1 | 1 | 0 | 0 | 0 | 42514 | 59.3 | 0.1 | 0.05 | 0 | 0.1 | 0
450351450351 | 171 | 45035 | CAPTJACK | 500 | 1 | 450351 | CJ_OL_11 | 500 | 1 | 1 | 0 | 0 | 1 | 45035 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
47171147233 | 172 | 47171 | HAZEL_DEL_CC | 115 | 1 | 47233 | SW1 | 115 | 1 | 1 | 0 | 0.05 | 2 | 47233 | 59.3 | 15 | 0.05 | 0 | 0 | 0
48029148194 | 173 | 48029 | BEACON S | 115 | 1 | 48194 | LOCUST | 115 | 1 | 1 | 0 | 0.05 | 2 | 48165 | 59.2 | 0.13333 | 0.05 | 48029 | 0 | 0
48165148237 | 174 | 48165 | IRVIN | 115 | 1 | 48237 | MILLWOOD | 115 | 1 | 1 | 0 | 0.05 | 2 | 48237 | 59.2 | 0.133 | 0.05 | 48165 | 0 | 0
48165148238 | 175 | 48165 | IRVIN | 115 | 1 | 48238 | MILLWOOD_E | 115 | 1 | 1 | 0 | 0.05 | 2 | 48237 | 59.2 | 0.133 | 0.05 | 48165 | 0 | 0
48261148087 | 176 | 48261 | NEZPERCE | 115 | 1 | 48087 | COTTNWDT | 115 | 1 | 1 | 0 | 0.05 | 2 | 40383 | 59.2 | 0.133 | 0.05 | 48261 | 0 | 0
48261148171 | 177 | 48261 | NEZPERCE | 115 | 1 | 48171 | KAMIAH | 115 | 1 | 1 | 0 | 0.05 | 2 | 48177 | 59.3 | 0.13333 | 0.05 | 48261 | 0 | 0
50781150776 | 178 | 50781 | NTL VR | 138 | 1 | 50776 | NTL138 | 138 | 1 | 1 | 0 | 0 | 1 | 50776 | 0.842 | 0.5 | 0.0333 | 50781 | 0 | 0
50791154158 | 179 | 50791 | CBK500 | 500 | 1 | 54158 | LANGDON | 500 | 1 | 1 | 0 | 0 | 1 | 54158 | 0.85 | 0.25 | 0.0333 | 54158 | 0 | 0
60813160817 | 180 | 60813 | BRIDGE | 138 | 1 | 60817 | GROUSE_CR # | 138 | 1 | 1 | 0 | 60817 | 58.6 | 0.12 | 0.033 | 0 | 0 | 0 | 0 | 0
64019164242 | 181 | 64019 | BRUNSWCK | 63 | 1 | 64242 | VIRGINIA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64242 | 59.3 | 0.1 | 0.05 | 64019 | 2 | 0
64020164063 | 182 | 64020 | BRUNSWCK | 120 | 1 | 64063 | INCLINE | 120 | 1 | 1 | 0 | 0.05 | 2 | 64063 | 58.9 | 0.1 | 0.05 | 64020 | 2 | 0
64042164846 | 183 | 64042 | FALCON | 120 | 1 | 64846 | HALLIBURTN T | 120 | 1 | 1 | 0 | 0.05 | 2 | 64846 | 58.15 | 0.1 | 0.05 | 64042 | 2 | 0
64042164846 | 184 | 64042 | FALCON | 120 | 1 | 64846 | HALLIBURTON | 120 | 1 | 1 | 0 | 0.05 | 2 | 64846 | 0.7 | 1 | 0.08883 | 64042 | 2 | 0
64042164846 | 185 | 64042 | FALCON | 120 | 1 | 64846 | HALLIBURTON | 120 | 1 | 1 | 0 | 0.05 | 2 | 64846 | 0.85 | 10 | 0.08883 | 64042 | 2 | 0
64042164846 | 186 | 64042 | FALCON | 120 | 1 | 64846 | HALLIBURTON | 120 | 1 | 1 | 0 | 0.05 | 2 | 64846 | 0.88 | 20 | 0.08883 | 64042 | 2 | 0
64060164183 | 187 | 64060 | HUMBOLT1 | 120 | 1 | 64183 | JERRITT | 120 | 1 | 1 | 0 | 0.05 | 2 | 64183 | 58.15 | 0.1 | 0.05 | 64060 | 2 | 0
64070164177 | 188 | 64070 | MAGGIE CREEK | 120 | 1 | 64177 | GOLD QUARRY | 120 | 1 | 1 | 0 | 0.05 | 2 | 64177 | 0.7 | 2 | 0.08883 | 64070 | 2 | 0
64070164177 | 189 | 64070 | MAGGIE CREEK | 120 | 1 | 64177 | GOLD QUARRY | 120 | 1 | 1 | 0 | 0.05 | 2 | 64177 | 0.85 | 11 | 0.08883 | 64070 | 2 | 0
64070164177 | 190 | 64070 | MAGGIE CREEK | 120 | 1 | 64177 | GOLD QUARRY | 120 | 1 | 1 | 0 | 0.05 | 2 | 64177 | 0.88 | 21 | 0.08883 | 64070 | 2 | 0
64086164691 | 191 | 64086 | OREANA | 63 | 1 | 64691 | LIMERICK | 63 | 1 | 1 | 0 | 0.05 | 1 | 64555 | 0.92 | 8 | 0.08883 | 64086 | 2 | 0
64086164691 | 192 | 64086 | OREANA | 63 | 1 | 64691 | LIMERICK | 63 | 1 | 1 | 0 | 0.05 | 1 | 64555 | 0.87 | 6 | 0.08883 | 64086 | 2 | 0
64086164691 | 193 | 64086 | OREANA | 63 | 1 | 64691 | LIMERICK | 63 | 1 | 1 | 0 | 0.05 | 1 | 64555 | 0.8 | 4 | 0.08883 | 64086 | 2 | 0
64086164803 | 194 | 64086 | OREANA | 63 | 1 | 64803 | RYEPATCH | 63 | 1 | 1 | 0 | 0.05 | 1 | 64137 | 0.92 | 9 | 0.08883 | 64086 | 2 | 0
64086164803 | 195 | 64086 | OREANA | 63 | 1 | 64803 | RYEPATCH | 63 | 1 | 1 | 0 | 0.05 | 1 | 64137 | 0.87 | 7 | 0.08883 | 64086 | 2 | 0
64086164803 | 196 | 64086 | OREANA | 63 | 1 | 64803 | RYEPATCH | 63 | 1 | 1 | 0 | 0.05 | 1 | 64137 | 0.8 | 5 | 0.08883 | 64086 | 2 | 0
64122164243 | 197 | 64122 | TRUCKEE | 63 | 1 | 64243 | GLENSHIR | 63 | 1 | 1 | 0 | 0.05 | 2 | 64243 | 58.5 | 0.1 | 0.05 | 64122 | 2 | 0
64129164200 | 198 | 64129 | VALMY | 120 | 1 | 64200 | REDHOUSE | 120 | 1 | 1 | 0 | 0.05 | 2 | 64200 | 57.45 | 0.25 | 0.05 | 64129 | 2 | 0
64129164200 | 199 | 64129 | VALMY | 120 | 1 | 64200 | REDHOUSE | 120 | 1 | 1 | 0 | 0.05 | 2 | 64286 | 0.92 | 5.5 | 0.08883 | 64129 | 2 | 0
64129164200 | 200 | 64129 | VALMY | 120 | 1 | 64200 | REDHOUSE | 120 | 1 | 1 | 0 | 0.05 | 2 | 64286 | 0.9 | 3.5 | 0.08883 | 64129 | 2 | 0
64129164200 | 201 | 64129 | VALMY | 120 | 1 | 64200 | REDHOUSE | 120 | 1 | 1 | 0 | 0.05 | 2 | 64286 | 0.85 | 1.5 | 0.08883 | 64129 | 2 | 0
64137164244 | 202 | 64137 | WINN SUB | 63 | 1 | 64244 | SONOMA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64244 | 59.3 | 0.1 | 0.05 | 64137 | 2 | 0
64137164244 | 203 | 64137 | WINN SUB | 63 | 1 | 64244 | SONOMA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64245 | 0.92 | 8 | 0.08883 | 64137 | 2 | 0
64137164244 | 204 | 64137 | WINN SUB | 63 | 1 | 64244 | SONOMA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64245 | 0.87 | 6 | 0.08883 | 64137 | 2 | 0
64137164244 | 205 | 64137 | WINN SUB | 63 | 1 | 64244 | SONOMA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64245 | 0.8 | 4 | 0.08883 | 64137 | 2 | 0
64137164693 | 206 | 64137 | WINN SUB | 63 | 1 | 64693 | GOLCONDA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64693 | 0.92 | 8 | 0.08883 | 64137 | 2 | 0
64137164693 | 207 | 64137 | WINN SUB | 63 | 1 | 64693 | GOLCONDA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64693 | 0.87 | 6 | 0.08883 | 64137 | 2 | 0
64137164693 | 208 | 64137 | WINN SUB | 63 | 1 | 64693 | GOLCONDA | 63 | 1 | 1 | 0 | 0.05 | 2 | 64693 | 0.8 | 4 | 0.08883 | 64137 | 2 | 0
64137164808 | 209 | 64137 | WINN SUB | 63 | 1 | 64808 | WINN GT | 63 | 1 | 1 | 0 | 0.05 | 1 | 64086 | 0.92 | 9 | 0.08883 | 64137 | 2 | 0
64137164808 | 210 | 64137 | WINN SUB | 63 | 1 | 64808 | WINN GT | 63 | 1 | 1 | 0 | 0.05 | 1 | 64086 | 0.87 | 7 | 0.08883 | 64137 | 2 | 0
64137164808 | 211 | 64137 | WINN SUB | 63 | 1 | 64808 | WINN GT | 63 | 1 | 1 | 0 | 0.05 | 1 | 64086 | 0.8 | 5 | 0.08883 | 64137 | 2 | 0
64148164235 | 212 | 64148 | BATLE MT | 63 | 1 | 64235 | SETTY | 63 | 1 | 1 | 0 | 0.05 | 2 | 64235 | 58.9 | 0.1 | 0.05 | 64148 | 2 | 0
64148164422 | 213 | 64148 | BATLE MT | 63 | 1 | 64422 | REESE RV2 | 63 | 1 | 1 | 0 | 0.05 | 2 | 64422 | 58.9 | 0.1 | 0.05 | 64148 | 2 | 0
64174164208 | 214 | 64174 | WINN BPA | 115 | 1 | 64208 | DAVY TWN | 115 | 1 | 1 | 0 | 0.05 | 2 | 64208 | 59.3 | 0.1 | 0.05 | 64174 | 2 | 0
64174164208 | 215 | 64174 | WINN BPA | 115 | 1 | 64208 | DAVY TWN | 115 | 1 | 1 | 0 | 0.05 | 1 | 47160 | 0.92 | 7 | 0.08883 | 64137 | 2 | 0
64174164208 | 216 | 64174 | WINN BPA | 115 | 1 | 64208 | DAVY TWN | 115 | 1 | 1 | 0 | 0.05 | 1 | 47160 | 0.87 | 5 | 0.08883 | 64137 | 2 | 0
64174164208 | 217 | 64174 | WINN BPA | 115 | 1 | 64208 | DAVY TWN | 115 | 1 | 1 | 0 | 0.05 | 1 | 47160 | 0.8 | 3 | 0.08883 | 64137 | 2 | 0
64269164374 | 218 | 64269 | BANNOCK | 120 | 1 | 64374 | PHOENIX T | 120 | 1 | 1 | 0 | 0.05 | 2 | 64374 | 57.45 | 0.25 | 0.05 | 64269 | 2 | 0
64269164374 | 219 | 64269 | BANNOCK | 120 | 1 | 64374 | PHOENIX T | 120 | 1 | 1 | 0 | 0.05 | 2 | 64375 | 0.92 | 6.5 | 0.08883 | 64269 | 2 | 0
64269164374 | 220 | 64269 | BANNOCK | 120 | 1 | 64374 | PHOENIX T | 120 | 1 | 1 | 0 | 0.05 | 2 | 64375 | 0.9 | 4.5 | 0.08883 | 64269 | 2 | 0
64269164374 | 221 | 64269 | BANNOCK | 120 | 1 | 64374 | PHOENIX T | 120 | 1 | 1 | 0 | 0.05 | 2 | 64375 | 0.85 | 2.5 | 0.08883 | 64269 | 2 | 0
64421164484 | 222 | 64421 | IMLAYREG | 63 | 1 | 64484 | LEWIS T | 63 | 1 | 1 | 0 | 0.05 | 1 | 64943 | 0.92 | 7 | 0.08883 | 64062 | 2 | 0
64421164484 | 223 | 64421 | IMLAYREG | 63 | 1 | 64484 | LEWIS T | 63 | 1 | 1 | 0 | 0.05 | 1 | 64943 | 0.87 | 5 | 0.08883 | 64062 | 2 | 0
64421164484 | 224 | 64421 | IMLAYREG | 63 | 1 | 64484 | LEWIS T | 63 | 1 | 1 | 0 | 0.05 | 1 | 64943 | 0.8 | 3 | 0.08883 | 64062 | 2 | 0
64522164524 | 225 | 64522 | BATLE RG | 63 | 1 | 64524 | COPR BSN | 63 | 1 | 1 | 0 | 0.05 | 2 | 64524 | 58.9 | 0.1 | 0.05 | 64522 | 2 | 0
65020165021 | 226 | 65020 | ROWLEY | 138 | 1 | 65021 | MAGCORP | 13.8 | 1 | 1 | 0 | 0 | 2 | 65021 | 59.5 | 0.0667 | 0.0833 | 65021 | 0 | 0
65020165021 | 227 | 65020 | ROWLEY | 138 | 1 | 65021 | MAGCORP | 13.8 | 2 | 1 | 0 | 0 | 2 | 65021 | 59.5 | 0.0667 | 0.0833 | 65021 | 0 | 0
66420166261 | 228 | 66420 | STGEORGE | 138 | 1 | 66261 | CHRCHFRM | 138 | 1 | 1 | 0 | 0 | 2 | 66261 | 59.1 | 0.0667 | 0.0833 | 66261 | 0 | 0
66830166900 | 229 | 66830 | PURG138 | 138 | 1 | 66900 | MAJESTIC | 138 | F | 1 | 0 | 0 | 2 | 66900 | 58.3 | 0.0667 | 0.0833 | 66900 | 0 | 0
70325170245 | 230 | 70325 | PLAZA | 69 | 1 | 70245 | LAGARITA | 69 | 1 | 1 | 0 | 0 | 0 | 70245 | 58.3 | 0.1 | 0.083 | 70325 | 1 | 81
70374170411 | 231 | 70374 | SANLSVLY | 115 | 1 | 70411 | STANLEY | 115 | 1 | 1 | 0 | 0 | 0 | 70374 | 0.93 | 20 | 0.083 | 70374 | 1 | 27
70374170467 | 232 | 70374 | SANLSVLY | 115 | 1 | 70467 | WAVERLY | 115 | 1 | 1 | 0 | 0 | 0 | 70374 | 0.93 | 20 | 0.083 | 70374 | 1 | 27
70376170230 | 233 | 70376 | SANLSVLY | 69 | 1 | 70230 | HOOPERTP | 69 | 1 | 1 | 0 | 0 | 0 | 70092 | 58.3 | 0.1 | 0.083 | 70376 | 1 | 81
70376170230 | 234 | 70376 | SANLSVLY | 69 | 1 | 70230 | HOOPERTP | 69 | 1 | 1 | 0 | 0 | 2 | 70092 | 0.93 | 10 | 0.083 | 70374 | 1 | 27
70453170223 | 235 | 70453 | VILAS | 69 | 1 | 70223 | HLTP_TP | 69 | 1 | 1 | 0 | 0 | 2 | 70222 | 58.9 | 0.1 | 0.083 | 70453 | 1 | 81
70453170223 | 236 | 70453 | VILAS | 69 | 1 | 70223 | HLTP_TP | 69 | 1 | 1 | 0 | 0 | 2 | 70222 | 0.9 | 4 | 0.083 | 70453 | 1 | 27
70453170080 | 237 | 70453 | VILAS | 69 | 1 | 70080 | STONINGT | 69 | 1 | 1 | 0 | 0 | 0 | 70473 | 58.9 | 0.1 | 0.083 | 70453 | 1 | 81
70467170414 | 238 | 70467 | WAVERLY | 115 | 1 | 70414 | STOCKADE | 115 | 1 | 1 | 0 | 0 | 2 | 70373 | 58.3 | 0.1 | 0.05 | 70467 | 1 | 81
70473170203 | 239 | 70473 | WILLOW_CK | 69 | 1 | 70203 | GRANTAP | 69 | 1 | 1 | 0 | 0 | 0 | 70453 | 58.9 | 0.1 | 0.083 | 70473 | 1 | 81
72171172752 | 240 | 72171 | HESPERUS2 | 115 | 1 | 72752 | SUNNYSDE | 115 | 1 | 1 | 0 | 0 | 0 | 79077 | 0.9 | 4 | 0.083 | 72171 | 1 | 27
73035173485 | 241 | 73035 | BURLNGTN | 115 | 1 | 73485 | BURL KC | 115 | 1 | 1 | 0 | 0 | 2 | 73007 | 58.9 | 0.1 | 0.083 | 73035 | 1 | 81
73125172432 | 242 | 73125 | LSCHANCE | 115 | 1 | 72432 | LINDON | 115 | 1 | 1 | 0 | 0 | 0 | 73185 | 58.5 | 0.1 | 0.083 | 73125 | 1 | 81
73127172407 | 243 | 73127 | LYONS | 115 | 1 | 72407 | DOWEFLAT | 115 | 1 | 1 | 0 | 0 | 2 | 73171 | 59.1 | 0.1 | 0.083 | 73127 | 1 | 81
73146173128 | 244 | 73146 | OASISTAP | 115 | 1 | 73128 | MAY | 115 | 1 | 1 | 0 | 0 | 2 | 73128 | 59.3 | 15 | 0.083 | 73146 | 1 | 81
73154173161 | 245 | 73154 | POLE CK | 115 | 1 | 73161 | QUALLS | 115 | 1 | 1 | 0 | 0 | 2 | 73161 | 58.3 | 0.083 | 0.083 | 73154 | 1 | 81
73185173084 | 246 | 73185 | SO FORK | 115 | 1 | 73084 | HELL TAP | 115 | 1 | 1 | 0 | 0 | 0 | 73125 | 58.5 | 0.1 | 0.083 | 73185 | 1 | 81
73275176501 | 247 | 73275 | SUNDHILL | 69 | 1 | 76501 | BLFCH_TP | 69 | 1 | 1 | 0 | 0.067 | 2 | 73275 | 0.975 | 0 | 0.1 | 73275 | 3 | 0
79011172781 | 248 | 79011 | CAHONE | 115 | 1 | 72781 | DOECANYN | 115 | 1 | 1 | 0 | 0 | 0 | 79044 | 58.3 | 0.1 | 0.083 | 79011 | 1 | 81
79044179122 | 249 | 79044 | LOSTCANY | 115 | 1 | 79122 | TOWAOC | 115 | 1 | 1 | 0 | 0 | 0 | 79011 | 58.3 | 0.1 | 0.083 | 79044 | 1 | 81
79077179076 | 250 | 79077 | BAYFIELD | 115 | 1 | 79076 | AM EAST | 115 | 1 | 1 | 0 | 0 | 0 | 72171 | 0.93 | 4 | 0.083 | 79077 | 1 | 27
79189172137 | 251 | 79189 | SUNSH SM | 115 | 1 | 72137 | TELLURID | 115 | 1 | 1 | 0 | 0 | 2 | 72137 | 59.5 | 30 | 0.083 | 79189 | 1 | 81
79266179356 | 252 | 79266 | MEEKER | 345 | 1 | 79356 | MCBRYDE | 345 | 1 | 1 | 0 | 0 | 2 | 79354 | 58.7 | 0.1 | 0.05 | 79266 | 1 | 81
1601041160107 | 253 | 160104 | CLEAR | 138 | 1 | 160107 | CYPRUS | 138 | 1 | 1 | 0 | 0 | 1 | 160107 | 57 | 0.1 | 0.03 | 160104 | 2 | 0
1601091160111 | 254 | 160109 | DMP_CENTRAL | 138 | 1 | 160111 | DMP_NORTH | 138 | 1 | 1 | 0 | 0 | 1 | 160111 | 57.2 | 0.1 | 0.03 | 160109 | 2 | 0
1601121160120 | 255 | 160112 | DREXEL | 138 | 1 | 160120 | IRVINGTON | 138 | 1 | 1 | 0 | 0 | 1 | 160112 | 57.2 | 0.1 | 0.03 | 160120 | 2 | 0
1601131160162 | 256 | 160113 | EAST_LOOP_N | 138 | 1 | 160162 | PATRIOT_TEP | 138 | 1 | 0.041667 | 0 | 0 | 1 | 160113 | 57.2 | 0.1 | 0.03 | 160162 | 2 | 0
1601201A160145 | 257 | 160120 | IRVINGTON | 138 | 1A | 160145 | SONORAN | 138 | 1A | 1 | 0 | 0 | 1 | 160145 | 57.2 | 0.1 | 0.03 | 160120 | 2 | 0
1601202A160145 | 258 | 160120 | IRVINGTON | 138 | 2A | 160145 | SONORAN | 138 | 2A | 1 | 0 | 0 | 1 | 160145 | 57.2 | 0.1 | 0.03 | 160120 | 2 | 0
1601203A160145 | 259 | 160120 | IRVINGTON | 138 | 3A | 160145 | SONORAN | 138 | 3A | 1 | 0 | 0 | 1 | 160145 | 57.2 | 0.1 | 0.03 | 160120 | 2 | 0
1601301160113 | 260 | 160130 | NORTH_EAST_E | 138 | 1 | 160113 | EAST_LOOP_N | 138 | 1 | 1 | 0 | 0 | 1 | 160113 | 57.2 | 0.1 | 0.03 | 160130 | 2 | 0
1601311160144 | 261 | 160131 | NORTH_EAST_W | 138 | 1 | 160144 | SNYDER | 138 | 1 | 1 | 0 | 0 | 1 | 160144 | 57.2 | 0.1 | 0.03 | 160131 | 2 | 0
1601461160101 | 262 | 160146 | SOUTH | 138 | 1 | 160101 | ASARCO | 138 | 1 | 1 | 0 | 0 | 1 | 160101 | 57 | 0.1 | 0.03 | 160146 | 2 | 0
1601511160108 | 263 | 160151 | TUCSON | 138 | 1 | 160108 | DELCERRO | 138 | 1 | 1 | 0 | 0 | 1 | 160108 | 57.2 | 0.1 | 0.03 | 160151 | 2 | 0
1601521160120 | 264 | 160152 | TWENTYSECOND | 138 | 1 | 160120 | IRVINGTON | 138 | 1 | 1 | 0 | 0 | 1 | 160152 | 57.2 | 0.1 | 0.03 | 160120 | 2 | 0
240015118595 | 265 | 240015 | ELDORDO_C | 230 | 1 | 18595 | NSO | 230 | 1 | 1 | 0 | 0 | 0 | 18595 | 57.9 | 1 | 0.0667 | 240015 | 0 | 0
300001130020 | 266 | 300001 | CJ_OL_13 | 500 | 1 | 30020 | OLINDA | 500 | 1 | 1 | 0 | 0 | 1 | 45035 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
3000021300003 | 267 | 300002 | MN_RM_11 | 500 | 1 | 300003 | MN_RM_12 | 500 | 1 | 1 | 0 | 0 | 1 | 40687 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
300003130005 | 268 | 300003 | MN_RM_12 | 500 | 1 | 30005 | ROUND MT | 500 | 1 | 1 | 0 | 0 | 1 | 40687 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
3000041300005 | 269 | 300004 | MN_RM_21 | 500 | 1 | 300005 | MN_RM_22 | 500 | 2 | 1 | 0 | 0 | 1 | 40687 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
3000051300006 | 270 | 300005 | MN_RM_22 | 500 | 1 | 300006 | MN_RM_23 | 500 | 2 | 1 | 0 | 0 | 1 | 40687 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
300006130005 | 271 | 300006 | MN_RM_23 | 500 | 1 | 30005 | ROUND MT | 500 | 2 | 1 | 0 | 0 | 1 | 40687 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
4503511450352 | 272 | 450351 | CJ_OL_11 | 500 | 1 | 450352 | CJ_OL_12 | 500 | 1 | 1 | 0 | 0 | 1 | 45035 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
4503521300001 | 273 | 450352 | CJ_OL_12 | 500 | 1 | 300001 | CJ_OL_13 | 500 | 1 | 1 | 0 | 0 | 1 | 45035 | 57.9 | 1 | 0.083333 | 0 | 0 | 0
6320611632022 | 274 | 632061 | ASSINIBOINE | 69 | 1 | 632022 | HIGHLANDPARK | 69 | 1 | 1 | 0 | 58.5 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
6320611632059 | 275 | 632061 | ASSINIBOINE | 69 | 1 | 632059 | KREMLIN-R | 69 | 1 | 1 | 0 | 58.9 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
6320611632060 | 276 | 632061 | ASSINIBOINE | 69 | 1 | 632060 | HAVRE CITY | 69 | 1 | 1 | 0 | 58.5 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
6320611632150 | 277 | 632061 | ASSINIBOINE | 69 | 1 | 632150 | ROCKYBY-R T | 69 | 1 | 1 | 0 | 58.9 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
6320821632086 | 278 | 632082 | WHATLEY | 69 | 1 | 632086 | WHATLEY-R | 69 | 1 | 4 | 0 | 59.5 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
6321621632132 | 279 | 632162 | VERONA | 69 | 1 | 632132 | BIG SANDY-R | 69 | 1 | 2 | 0 | 58.3 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
6321621632195 | 280 | 632162 | VERONA | 69 | 1 | 632195 | PILOTROCK T | 69 | 1 | 3 | 0 | 58.3 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
6350861632086 | 281 | 635086 | NEW DEAL-R | 69 | 1 | 632086 | WHATLEY-R | 69 | 1 | 5 | 0 | 59.5 | 0.083 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0
640055164189 | 282 | 640055 | BELL157 | 120 | 1 | 64189 | MEIKLE | 120 | 1 | 1 | 0 | 0.05 | 2 | 64183 | 59.3 | 0.1 | 0.05 | 64060 | 2 | 0

## mdf_lhfrt (hidden)
unique_ID | Model | Bus | Name | kv | ID | 2nd Bus | 2nd Name | 2nd kv | 2nd ID | Idk | pslf | st | fref | dftrp1 | dftrp2 | dftrp3 | dftrp4 | dftrp5 | dftrp6 | dftrp7 | dftrp8 | dftrp9 | dftrp10 | dttrp1 | dttrp2 | dttrp3 | dttrp4 | dttrp5 | dttrp6 | dttrp7 | dttrp8 | dttrp9 | dttrp10 | alarm
108331 | lhfrt | 10833 | SBEC_SPV | 0.64 | 1 | : | [5 empty] | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
108351 | lhfrt | 10835 | SBEC_BES | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.05 | 0.15 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 1
105301 | lhfrt | 10530 | RT66_BESS | 0.64 | 1 | 10710 | CIBOLA | 115 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107121 | lhfrt | 10712 | RT66_G1 | 34.5 | 1 | 10710 | CIBOLA | 115 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109761 | lhfrt | 10976 | SANDIA_BESS | 0.6 | 1 | : | [5 empty] | #9 | 60 | 1 | 1.25 | 1.5 | 1.8 | -0.5 | -1 | -1.5 | -2 | -2.19 | -2.2 | 48.51 | 20.97 | 10.72 | 0.0001 | 1792.05 | 242.49 | 32.81 | 4.44 | 2.08 | 0.0001 | 1
107471 | lhfrt | 10747 | TAG_PV1 | 0.64 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | 0 | 0 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0
107431 | lhfrt | 10743 | TAG_BESS1 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
107441 | lhfrt | 10744 | TAG_BESS2 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
107791 | lhfrt | 10779 | TAG_PV2 | 0.64 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | 0 | 0 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0
107511 | lhfrt | 10751 | TAG_BESS3 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
107501 | lhfrt | 10750 | TAG_BESS4 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
1042301 | lhfrt | 10423 | SJSOL_PV1 | 0.64 | 1 | 10420 | SJ_SOLAR | 345 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1042502 | lhfrt | 10425 | SJSOL_BESS1 | 0.9 | 2 | 10420 | SJ_SOLAR | 345 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1071603 | lhfrt | 10716 | SJSOL_PV2 | 0.64 | 3 | 10420 | SJ_SOLAR | 345 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1071804 | lhfrt | 10718 | SJSOL_BESS2 | 0.9 | 4 | 10420 | SJ_SOLAR | 345 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108361 | lhfrt | 10836 | ATRISCO_PV1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108372 | lhfrt | 10837 | ATRISCO_B1 | 0.63 | 2 | : | [5 empty] | #9 | 60 | 10 | 1.7 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.05 | 31 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
108383 | lhfrt | 10838 | ATRISCO_PV2 | 0.63 | 3 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108394 | lhfrt | 10839 | ATRISCO_B2 | 0.63 | 4 | : | [5 empty] | #9 | 60 | 10 | 1.7 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.05 | 31 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
107541 | lhfrt | 10754 | SKYRCH_PVCL | 34.5 | 1 | 10755 | SUNRANCH | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107531 | lhfrt | 10753 | SKYRCH_BSCL1 | 34.5 | 1 | 10755 | SUNRANCH | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107591 | lhfrt | 10759 | SKYRCH_BSCL2 | 34.5 | 1 | 10755 | SUNRANCH | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107561 | lhfrt | 10756 | SKYRCH_BS | 0.645 | 1 | 10755 | SUNRANCH | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108951 | lhfrt | 10895 | CC1 | 0.69 | 1 | 10895 | CC1 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108941 | lhfrt | 10894 | CC1 2.3 | 0.69 | 1 | 10894 | CC1 2.3 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108891 | lhfrt | 10889 | CC2 | 0.69 | 1 | 10889 | CC1 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108921 | lhfrt | 10892 | CC2 2.3 | 0.69 | 1 | 10892 | CC1 2.3 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109201 | lhfrt | 10920 | DM | 0.69 | 1 | 10920 | DM | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108591 | lhfrt | 10859 | DM 2.3 | 0.69 | 1 | 10859 | DM 2.3 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108561 | lhfrt | 10856 | RC2 | 0.69 | 1 | 10856 | RC2 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108611 | lhfrt | 10861 | RC1 | 0.69 | 1 | 10861 | RC1 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108841 | lhfrt | 10884 | TC1 | 0.69 | 1 | 10884 | TC1 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108601 | lhfrt | 10860 | TC1 2.3 | 0.69 | 1 | 10860 | TC1 2.3 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109671 | lhfrt | 10967 | TC2 | 0.69 | 1 | 10967 | TC1 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108981 | lhfrt | 10898 | TC2 2.3 | 0.69 | 1 | 10898 | TC1 2.3 | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107671 | lhfrt | 10767 | NOENC_PV | 0.63 | 1 | 10767 | NOENC_PV | 0.63 | 1 | 1 | : | #1 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106351 | lhfrt | 10635 | ARROY_PV1 | 0.63 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.5 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
106361 | lhfrt | 10636 | ARROY_BS1 | 0.48 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.01 | 30.01 | 0.16 | 180.01 | 30.01 | 7.51 | 0.76 | 0.5 | 0 | 0 | 0
106401 | lhfrt | 10640 | ARROY_PV2 | 0.63 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.5 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
106411 | lhfrt | 10641 | ARROY_BS2 | 0.48 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.01 | 30.01 | 0.16 | 180.01 | 30.01 | 7.51 | 0.76 | 0.5 | 0 | 0 | 0
108731 | lhfrt | 10873 | LAJOY_GE1_WG | 0.69 | 1 | 10873 | LAJOY_GE1_WG | 0.69 | 1 | 1 | : | #9 | 60 | -3 | -1.2 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 200 | 1 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108741 | lhfrt | 10874 | LAJOY_SE1_WG | 0.69 | 1 | 10874 | LAJOY_SE1_WG | 0.69 | 1 | 1 | : | #9 | 60 | -3 | -1.2 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 200 | 1 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108781 | lhfrt | 10878 | LAJOY_GE2_WG | 0.69 | 1 | 10878 | LAJOY_GE2_WG | 0.69 | 1 | 1 | : | #9 | 60 | -3 | -1.2 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 200 | 1 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108791 | lhfrt | 10879 | LAJOY_SE2_WG | 0.69 | 1 | 10879 | LAJOY_SE2_WG | 0.69 | 1 | 1 | : | #9 | 60 | -3 | -1.2 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 200 | 1 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121541 | lhfrt | 12154 | CIM_GEN | 0.3 | 1 | : | [5 empty] | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
120941 | lhfrt | 12094 | PYRMDG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120942 | lhfrt | 12094 | PYRMDG1 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120951 | lhfrt | 12095 | PYRMDG2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120952 | lhfrt | 12095 | PYRMDG2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101891 | lhfrt | 10189 | LALUZ | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102461 | lhfrt | 10246 | RIOBRAVO | 18 | 1 | : | [5 empty] | #9 | 60 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102611 | lhfrt | 10261 | REEVE_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102621 | lhfrt | 10262 | REEVE_G2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102631 | lhfrt | 10263 | REEVE_G3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103941 | lhfrt | 10394 | LEF_G1 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103951 | lhfrt | 10395 | LEF_G2 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103961 | lhfrt | 10396 | LEF_S1 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104851 | lhfrt | 10485 | AFTONS | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104861 | lhfrt | 10486 | AFTONG | 18 | 1 | : | [5 empty] | #9 | 60 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104911 | lhfrt | 10491 | LRDSBGG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104921 | lhfrt | 10492 | LRDSBGG2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107241 | lhfrt | 10724 | ENCINO_SOLG | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | 3 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 60 | 0.1 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107341 | lhfrt | 10734 | BRITTON_SOLG | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | 3 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 60 | 0.1 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109031 | lhfrt | 10903 | VEF | 18 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109091 | lhfrt | 10909 | REDMESA4 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
109331 | lhfrt | 10933 | HLWR_4 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109721 | lhfrt | 10972 | EL_CABO_1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
109751 | lhfrt | 10975 | EL_CABO_2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
10549SC | lhfrt | 10549 | BLACKWTR-SC | 17.5 | SC | : | [5 empty] | #9 | 60 | -1.6 | -3 | 1.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.5 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109971 | lhfrt | 10997 | NMCASA_WTG | 0.69 | 1 | 10996 | NMCASA_GSUHS | 345 | 1 | 1 | : | #9 | 60 | 5 | 3 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 0.2625 | 63 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
136111 | lhfrt | 13611 | BEJN1_TURB | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136121 | lhfrt | 13612 | BEJN2_TURB | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136101 | lhfrt | 13610 | BEKW_TURB | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136181 | lhfrt | 13618 | GRADYNM1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136191 | lhfrt | 13619 | GRADYNM2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105661 | lhfrt | 10566 | JEC SPV2 | 0.55 | 1 | 10563 | JEC | 345 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 999 | 999 | 999 | 1
105521 | lhfrt | 10552 | JEC_SPV1 | 0.55 | 1 | 10563 | JEC | 345 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 999 | 999 | 999 | 1
105641 | lhfrt | 10564 | JEC_BES | 0.69 | 1 | 10563 | JEC | 345 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 999 | 999 | 999 | 1
106331 | lhfrt | 10633 | ARROY_C1A | 34.5 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 0 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0.15 | 0.75 | 7.5 | 30 | 180 | 0.15 | 30 | 180 | 0 | 0
106361 | lhfrt | 10636 | ARROY_BS1 | 0.48 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 0 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0.15 | 0.75 | 7.5 | 30 | 180 | 0.15 | 30 | 180 | 0 | 0
106361 | lhfrt | 10636 | ARROY_BS1 | 0.48 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 0 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0.15 | 0.75 | 7.5 | 30 | 180 | 0.15 | 30 | 180 | 0 | 0
106381 | lhfrt | 10638 | ARROY_C2A | 34.5 | 1 | 10631 | ARROY_STA | 345 | 1 | 1 | : | #9 | 0 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0.15 | 0.75 | 7.5 | 30 | 180 | 0.15 | 30 | 180 | 0 | 0
109011 | lhfrt | 10901 | ARAGONNE_LV1 | 0.69 | 1 | 10116 | GUADLUPE | 345 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0.008334 | 0.008334 | 1
109951 | lhfrt | 10995 | ARAGONNE_LV2 | 0.69 | 1 | 10116 | GUADLUPE | 345 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0.008334 | 0.008334 | 1
109121 | lhfrt | 10912 | AR_EXP_LV1 | 0.69 | 1 | 10116 | GUADLUPE | 345 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0.008334 | 0.008334 | 1
109161 | lhfrt | 10916 | AR_EXP_LV2 | 0.69 | 1 | 10116 | GUADLUPE | 345 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0.008334 | 0.008334 | 1
12080PV | lhfrt | 12080 | TAOS | 69 | PV | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | 1.7 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 180.1 | 30.1 | 0.5 | 0.5 | 0.5 | 180.1 | 30.1 | 7.6 | 0.84 | 0.1 | 0
120941 | lhfrt | 12094 | PYRMDG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120942 | lhfrt | 12094 | PYRMDG1 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120951 | lhfrt | 12095 | PYRMDG2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120952 | lhfrt | 12095 | PYRMDG2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 180 | 7.5 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11248PV | lhfrt | 11248 | HECATE | 0.69 | PV | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
11335PV | lhfrt | 11335 | BV_PV1 | 0.6 | PV | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
11334PV | lhfrt | 11334 | BV_PV2 | 0.6 | PV | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
11319BT | lhfrt | 11319 | BV_BATT | 13.8 | BT | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 99999 | 99999 | 0
11287PV | lhfrt | 11287 | MS_G1 | 0.69 | PV | 11286 | MACHOSPRNGHV | 345 | : |  |  | #99 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.04 | 30 | 180 | 0.04 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
11288PV | lhfrt | 11288 | MS_G2 | 0.55 | PV | 11286 | MACHOSPRNGHV | 345 | : |  |  | #99 | 60 | 3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111121 | lhfrt | 11112 | NEWMANG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 1.3 | -1.2 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111131 | lhfrt | 11113 | NEWMANG2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 1.3 | -1.2 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112271 | lhfrt | 11227 | MPS1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112281 | lhfrt | 11228 | MPS2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112321 | lhfrt | 11232 | MPS3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112331 | lhfrt | 11233 | MPS4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111331 | lhfrt | 11133 | RIOGD_G6 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 1.3 | -1.2 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111341 | lhfrt | 11134 | RIOGD_G7 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 1.7 | 1.3 | -1.2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 1 | 30 | 180 | 180 | 10 | 1 | 0 | 0 | 0 | 0 | 0
111351 | lhfrt | 11135 | RIOGD_G8 | 17.5 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.7 | -0.7 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 180 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112261 | lhfrt | 11226 | RIOGD_G9 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2.4 | 1.2 | -1.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 180 | 180 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111141 | lhfrt | 11114 | NEWMANG3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.2 | -1.2 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 240 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111151 | lhfrt | 11115 | NEWMN4G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.7 | -0.7 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111161 | lhfrt | 11116 | NEWMN4G2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.7 | -0.7 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111171 | lhfrt | 11117 | NEWMN4S1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.7 | -0.7 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110511 | lhfrt | 11051 | COPPER_G | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.2 | -1.2 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 240 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112081 | lhfrt | 11208 | NEWMAN_5GT3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.2 | -1.2 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 240 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112091 | lhfrt | 11209 | NEWMAN_5GT4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.2 | -1.2 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 240 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112611 | lhfrt | 11261 | NEWMAN_5ST2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.2 | -1.2 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 240 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1482141 | lhfrt | 148214 | Q256_SPV | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 0.5 | 181 | 31 | 7.6 | 0.76 | 0.5 | 0 | 0 | 0
1482161 | lhfrt | 148216 | Q256_BES | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 0.5 | 181 | 31 | 7.6 | 0.76 | 0.5 | 0 | 0 | 0
1482201 | lhfrt | 148220 | Q264_SPV | 0.6 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.5 | 180 | 30 | 0.2 | 0 | 0 | 0
1482221 | lhfrt | 148222 | Q264_BES | 0.385 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.5 | 180 | 30 | 0.2 | 0 | 0 | 0
1482271 | lhfrt | 148227 | Q295_PV | 0.645 | 1 | 148223 | Q295 | 230 | : |  |  | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1482281 | lhfrt | 148228 | Q295_BES | 0.9 | 1 | 148223 | Q295 | 230 | : |  |  | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1482491 | lhfrt | 148249 | Q311_WIND | 0.69 | 1 | 148245 | Q311 | 345 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1482501 | lhfrt | 148250 | Q311_BES | 0.434 | 1 | 148245 | Q311 | 345 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
14756FT | lhfrt | 14756 | WNDFUT6 | 18 | FT | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
1481401 | lhfrt | 148140 | Q227SPV1 | 0.63 | 1 | 148135 | Q227 | 500 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481421 | lhfrt | 148142 | Q227BES1 | 0.69 | 1 | 148135 | Q227 | 500 | 1 | 1 | : | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481441 | lhfrt | 148144 | Q227DCB1 | 0.91 | 1 | 148135 | Q227 | 500 | 1 | 1 | : | #9 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481492 | lhfrt | 148149 | Q227DCB2 | 0.91 | 2 | 148135 | Q227 | 500 | 1 | 1 | : | #9 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481542 | lhfrt | 148154 | Q227BES2 | 0.69 | 2 | 148135 | Q227 | 500 | 1 | 1 | : | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1480231 | lhfrt | 148023 | Q248BES1 | 0.66 | 1 | 148018 | Q248 | 500 | 1 | 1 | : | #1 | 60 | -0.7 | -2 | -3 | -6 | 0 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0 | 6550 | 90 | 5 | 1 | 1 | 1
1481582 | lhfrt | 148158 | Q248BES2 | 0.66 | 2 | 148018 | Q248 | 500 | 1 | 1 | : | #1 | 60 | -0.7 | -2 | -3 | -6 | 0 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0 | 6550 | 90 | 5 | 1 | 1 | 1
1481631 | lhfrt | 148163 | Q248_SPV | 0.63 | 1 | 148018 | Q248 | 500 | 1 | 1 | : | #1 | 60 | -0.7 | -2 | -3 | -6 | 0 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0 | 6550 | 90 | 5 | 1 | 1 | 1
1480101 | lhfrt | 148010 | Q276_SPV | 0.63 | 1 | 148005 | Q276 | 500 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1480421 | lhfrt | 148042 | Q389_SPV1 | 0.63 | 1 | 148035 | Q389 | 500 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481692 | lhfrt | 148169 | Q389_SPV2 | 0.63 | 2 | 148035 | Q389 | 500 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1480401 | lhfrt | 148040 | Q389_BES1 | 0.48 | 1 | 148035 | Q389 | 500 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481672 | lhfrt | 148167 | Q389_BES2 | 0.48 | 2 | 148035 | Q389 | 500 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481711 | lhfrt | 148171 | Q274SPV1 | 0.8 | 1 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | 1.5 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481782 | lhfrt | 148178 | Q274SPV2 | 0.8 | 2 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | 1.5 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481853 | lhfrt | 148185 | Q274SPV3 | 0.8 | 3 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | 1.5 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481924 | lhfrt | 148192 | Q274SPV4 | 0.8 | 4 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | 1.5 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481995 | lhfrt | 148199 | Q274SPV5 | 0.8 | 5 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | 1.5 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1482066 | lhfrt | 148206 | Q274SPV6 | 0.8 | 6 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | 1.5 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481731 | lhfrt | 148173 | Q274BES1 | 0.69 | 1 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | -3 | -1.5 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 0.16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481802 | lhfrt | 148180 | Q274BES2 | 0.69 | 2 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | -3 | -1.5 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 0.16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481873 | lhfrt | 148187 | Q274BES3 | 0.69 | 3 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | -3 | -1.5 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 0.16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481944 | lhfrt | 148194 | Q274BES4 | 0.69 | 4 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | -3 | -1.5 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 0.16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1482015 | lhfrt | 148201 | Q274BES5 | 0.69 | 5 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | -3 | -1.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 0.16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1482086 | lhfrt | 148208 | Q274BES6 | 0.69 | 6 | 927400 | Q274 | 500 | : |  |  | #9 | 60 | -3 | -1.5 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 0.16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1481151 | lhfrt | 148115 | Q255 PV1 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481161 | lhfrt | 148116 | Q255BES1 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481171 | lhfrt | 148117 | Q255 PV2 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481181 | lhfrt | 148118 | Q255BES2 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481191 | lhfrt | 148119 | Q255 PV3 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481201 | lhfrt | 148120 | Q255BES3 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481211 | lhfrt | 148121 | Q255 PV4 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481221 | lhfrt | 148122 | Q255BES4 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481231 | lhfrt | 148123 | Q255 PV5 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481241 | lhfrt | 148124 | Q255BES5 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481251 | lhfrt | 148125 | Q255 PV6 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481261 | lhfrt | 148126 | Q255BES6 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481271 | lhfrt | 148127 | Q255 PV7 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481281 | lhfrt | 148128 | Q255BES7 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481291 | lhfrt | 148129 | Q255 PV8 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481301 | lhfrt | 148130 | Q255BES8 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481311 | lhfrt | 148131 | Q255 PV9 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481321 | lhfrt | 148132 | Q255BES9 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481331 | lhfrt | 148133 | Q255PV10 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1481341 | lhfrt | 148134 | Q255BS10 | 0.55 | 1 | 14003 | NAVAJO | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 1
1480831 | lhfrt | 148083 | Q357 BES | 0.385 | 1 | 84453 | FREEDOM | 69 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
1480781 | lhfrt | 148078 | Q354 PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1480791 | lhfrt | 148079 | Q354 BES | 0.9 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1480691 | lhfrt | 148069 | Q363 BES | 0.385 | 1 | 84297 | SCTWSH | 69 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
1480641 | lhfrt | 148064 | Q269 PV | 0.385 | 1 | 14012 | DELANEY | 500 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
1480651 | lhfrt | 148065 | Q269 BES | 0.48 | 1 | 14012 | DELANEY | 500 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
1480591 | lhfrt | 148059 | Q268 BES | 0.64 | 1 | 148057 | Q268 | 69 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
148621 | lhfrt | 14862 | Q270 PV | 0.6 | 1 | 14000 | CHOLLA | 500 | 1 | 1 | : | #9 | 60 | 1.8 | 1.5 | 1 | 0.5 | -2.2 | -1.8 | -1.25 | -0.5 | 0 | 0 | 0.1001 | 50.1 | 125.1 | 600.1 | 0.1001 | 10.1 | 100.1 | 1800.1 | 0 | 0 | 0
148631 | lhfrt | 14863 | Q270 BES | 0.645 | 1 | 14000 | CHOLLA | 500 | 1 | 1 | : | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480551 | lhfrt | 148055 | Q274 PV | 0.55 | 1 | 158046 | RABTCNYN | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.01 | 30.01 | 0.16 | 180.01 | 30.01 | 7.51 | 0.76 | 0.16 | 0 | 0 | 0
1480391 | lhfrt | 148039 | Q389 PV | 0.6 | 1 | 14012 | DELANEY | 500 | 1 | 1 | : | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
1480441 | lhfrt | 148044 | Q389 PV2 | 0.6 | 1 | 14012 | DELANEY | 500 | 1 | 1 | : | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
1480451 | lhfrt | 148045 | Q389BES2 | 0.48 | 1 | 14012 | DELANEY | 500 | 1 | 1 | : | #9 | 60 | -5 | -3.5 | -1.5 | 1.2 | 2 | 5 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 300 | 300 | 0.16 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
1480281 | lhfrt | 148028 | Q230 PV | 0.66 | 1 | 14000 | CHOLLA | 500 | 1 | 1 | : | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480291 | lhfrt | 148029 | Q230 BES | 0.66 | 1 | 14000 | CHOLLA | 500 | 1 | 1 | : | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480331 | lhfrt | 148033 | Q271 PV | 0.66 | 1 | 14000 | CHOLLA | 500 | 1 | 1 | : | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480341 | lhfrt | 148034 | Q271 BES | 0.66 | 1 | 14000 | CHOLLA | 500 | 1 | 1 | : | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480161 | lhfrt | 148016 | Q288 PV | 0.6 | 1 | 14238 | PANDA 12 | 230 | 1 | 1 | : | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480172 | lhfrt | 148017 | Q288 BES | 0.6 | 2 | 14238 | PANDA 12 | 230 | 1 | 1 | : | #1 | 60 | -0.6 | -1.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480031 | lhfrt | 148003 | Q314_BES1 | 0.55 | 1 | 148000 | Q314 | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | -3 | -2.2 | -1.6 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 1
1480042 | lhfrt | 148004 | Q314_BES2 | 0.55 | 2 | 148000 | Q314 | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | -3 | -2.2 | -1.6 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 1
1480501 | lhfrt | 148050 | Q196WND1 | 0.69 | 1 | 148047 | Q196 | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480511 | lhfrt | 148051 | Q196WND2 | 0.69 | 1 | 148047 | Q196 | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480731 | lhfrt | 148073 | Q358 BES | 0.385 | 1 | 84375 | COLTER S | 69 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148641 | lhfrt | 14864 | CHINOBES | 0.69 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 1
148601 | lhfrt | 14860 | Q225 PV | 34.5 | 1 | : | [5 empty] | #99 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
148611 | lhfrt | 14861 | Q225 BES | 34.5 | 1 | : | [5 empty] | #99 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
149391 | lhfrt | 14939 | IRNWD PV | 0.385 | 1 | 84941 | IRONWDC2 | 69 | 1 | 1 | : | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
149401 | lhfrt | 14940 | IRNWDBES | 0.385 | 1 | 84941 | IRONWDC2 | 69 | 1 | 1 | : | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
857701 | lhfrt | 85770 | LUKFDSLR | 0.36 | 1 | 85324 | LUKFLD11 | 12.5 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148561 | lhfrt | 14856 | Q315 BES | 0.6 | 1 | 84939 | Q315 | 69 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.15 | 180 | 30 | 0.15 | 0 | 0 | 1
148541 | lhfrt | 14854 | Q239 PV | 0.55 | 1 | 14428 | Q239 | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 1
148551 | lhfrt | 14855 | Q239 BES | 0.48 | 1 | 14428 | Q239 | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.75 | 0.3 | 0 | 0 | 1
148471 | lhfrt | 14847 | Q273 WND | 0.69 | 1 | 14114 | CHEVELON | 345 | : |  |  | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1482591 | lhfrt | 148259 | CHEV_W1A | 0.72 | 1 | : | [5 empty] | #9 | 60 | 4.2 | -4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1482601 | lhfrt | 148260 | CHEV_W1B | 0.65 | 1 | : | [5 empty] | #9 | 60 | 4.2 | -4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1482611 | lhfrt | 148261 | CHEV_W1C | 0.696 | 1 | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1482631 | lhfrt | 148263 | CHEV_W2 | 0.72 | 1 | 148266 | OHACO_2 | 34.5 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148481 | lhfrt | 14848 | Q291BES1 | 0.63 | 1 | 14426 | Q291 | 230 | : |  |  | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
148492 | lhfrt | 14849 | Q291BES2 | 0.63 | 2 | 14426 | Q291 | 230 | : |  |  | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1482391 | lhfrt | 148239 | Q278_PV1 | 0.69 | 1 | 148234 | Q278 | 230 | : |  |  | #1 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
1482442 | lhfrt | 148244 | Q278_PV2 | 0.69 | 2 | 148234 | Q278 | 230 | : |  |  | #1 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
148311 | lhfrt | 14831 | Q236 PV | 0.63 | 1 | 84938 | Q236 272 | 69 | 1 | 1 | : | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.033 | 350 | 650 | 5000 | 0.033 | 650 | 5000 | 0 | 0 | 0 | 0
148321 | lhfrt | 14832 | Q272 BES | 0.48 | 1 | 84938 | Q236 272 | 69 | 1 | 1 | : | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.5 | -1 | 0 | 0 | 0 | 0 | 0.016 | 2 | 540 | 0.016 | 35 | 540 | 0 | 0 | 0 | 0 | 0
857721 | lhfrt | 85772 | DSTAR PV | 0.36 | 1 | 85404 | GILLESPI | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
857761 | lhfrt | 85776 | CTNCT PV | 0.2 | 1 | 85407 | COTNCT 3 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
857771 | lhfrt | 85777 | PLOMA PV | 0.315 | 1 | 85440 | COTNCT11 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
857781 | lhfrt | 85778 | HYDR1 PV | 0.27 | 1 | 85996 | CNTYLN 3 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
857821 | lhfrt | 85782 | HYDR2 PV | 0.355 | 1 | 85995 | CNTYLN11 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
857731 | lhfrt | 85773 | GILB1 PV | 0.69 | 1 | 85409 | GILABD11 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
857741 | lhfrt | 85774 | GILB2 PV | 0.69 | 1 | 85410 | GILABD19 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148371 | lhfrt | 14837 | Q300 BES | 0.434 | 1 | 85407 | COTNCT 3 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148381 | lhfrt | 14838 | Q301 BES | 0.434 | 1 | 85404 | GILLESPI | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148391 | lhfrt | 14839 | Q302 BES | 0.434 | 1 | 85996 | CNTYLN 3 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148401 | lhfrt | 14840 | Q303 BES | 0.434 | 1 | 85995 | CNTYLN11 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148411 | lhfrt | 14841 | Q305 BES | 0.434 | 1 | 85440 | COTNCT11 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148421 | lhfrt | 14842 | Q306 BES | 0.434 | 1 | 85409 | GILABD11 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148431 | lhfrt | 14843 | Q307 BES | 0.434 | 1 | 85410 | GILABD19 | 12.47 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
148441 | lhfrt | 14844 | SPI1BES1 | 0.53 | 1 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
148452 | lhfrt | 14845 | SPI1BES2 | 0.53 | 2 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
148461 | lhfrt | 14846 | SPI2 BES | 0.53 | 1 | 14356 | SAG.EAST | 115 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
14701FT | lhfrt | 14701 | PV FUT1 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14702FT | lhfrt | 14702 | BESFUT1 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14703FT | lhfrt | 14703 | PV FUT2 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14704FT | lhfrt | 14704 | BESFUT2 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14705FT | lhfrt | 14705 | PV FUT3 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14706FT | lhfrt | 14706 | BESFUT3 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14707FT | lhfrt | 14707 | PV FUT4 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14708FT | lhfrt | 14708 | BESFUT4 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14709FT | lhfrt | 14709 | PV FUT5 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14710FT | lhfrt | 14710 | BESFUT5 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14711FT | lhfrt | 14711 | PV FUT6 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14712FT | lhfrt | 14712 | BESFUT6 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14713FT | lhfrt | 14713 | PV FUT7 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14714FT | lhfrt | 14714 | BESFUT7 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14715FT | lhfrt | 14715 | PV FUT8 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14716FT | lhfrt | 14716 | BESFUT8 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14717FT | lhfrt | 14717 | PV FUT9 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14718FT | lhfrt | 14718 | BESFUT9 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14719FT | lhfrt | 14719 | PV FUT10 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14720FT | lhfrt | 14720 | BESFUT10 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14721FT | lhfrt | 14721 | PV FUT11 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14722FT | lhfrt | 14722 | BESFUT11 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14723FT | lhfrt | 14723 | PV FUT12 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14724FT | lhfrt | 14724 | BESFUT12 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14725FT | lhfrt | 14725 | PV FUT13 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14726FT | lhfrt | 14726 | BESFUT13 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14727FT | lhfrt | 14727 | PV FUT14 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14728FT | lhfrt | 14728 | BESFUT14 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14729FT | lhfrt | 14729 | PV FUT15 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14730FT | lhfrt | 14730 | BESFUT15 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14731FT | lhfrt | 14731 | PV FUT16 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14732FT | lhfrt | 14732 | BESFUT16 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14733FT | lhfrt | 14733 | PV FUT17 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14734FT | lhfrt | 14734 | BESFUT17 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14735FT | lhfrt | 14735 | PV FUT18 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14736FT | lhfrt | 14736 | BESFUT18 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14737FT | lhfrt | 14737 | PV FUT19 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14738FT | lhfrt | 14738 | BESFUT19 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14739FT | lhfrt | 14739 | PV FUT20 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14740FT | lhfrt | 14740 | BESFUT20 | 34.5 | FT | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14751FT | lhfrt | 14751 | WNDFUT1 | 18 | FT | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
14752FT | lhfrt | 14752 | WNDFUT2 | 18 | FT | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
14753FT | lhfrt | 14753 | WNDFUT3 | 18 | FT | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
14754FT | lhfrt | 14754 | WNDFUT4 | 18 | FT | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
14755FT | lhfrt | 14755 | WNDFUT5 | 18 | FT | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
856831 | lhfrt | 85683 | Q292BES1 | 0.63 | 1 | 14045 | Q292 STA | 230 | : |  |  | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
856842 | lhfrt | 85684 | Q292BES2 | 0.63 | 2 | 14045 | Q292 STA | 230 | : |  |  | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1482771 | lhfrt | 148277 | Q292BES1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
1482781 | lhfrt | 148278 | Q292BS2A | 0.735 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
1482791 | lhfrt | 148279 | Q292BS2B | 0.59 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
856741 | lhfrt | 85674 | Q229_G1 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 6 | 2.4 | -3.6 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2 | 2 | 0.1 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
856751 | lhfrt | 85675 | Q229_G2 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 6 | 2.4 | -3.6 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2 | 2 | 0.1 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
149721 | lhfrt | 14972 | AGAVE PV | 0.63 | 1 | 14435 | AGAVE | 500 | 1 | 1 | : | #9 | 60 | -3.2 | -3 | -2 | -1.7 | -0.7 | 1 | 2 | 2.2 | 0 | 0 | 0.6 | 0.5 | 700 | 600 | 600 | 700 | 0.1 | 0.6 | 0 | 0 | 0
149731 | lhfrt | 14973 | AGAVEBES | 0.63 | 1 | 14435 | AGAVE | 500 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
857881 | lhfrt | 85788 | REDRCK | 0.42 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.25 | 0.2 | 1
857841 | lhfrt | 85784 | DSRTSND1 | 0.42 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | -4 | 0 | 0 | 0 | 0 | 200 | 180 | 30 | 7.5 | 0.08 | 0 | 0 | 0 | 0 | 0 | 1
857851 | lhfrt | 85785 | DSRTSND2 | 0.8 | 1 | : | [5 empty] | #9 | 60 | -0.5 | -2.2 | 0.5 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1800 | 2000 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1
149001 | lhfrt | 14900 | CHOLLA | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.6 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149021 | lhfrt | 14902 | CHOLLA3 | 22 | 1 | : | [5 empty] | #9 | 60 | -2 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14914H | lhfrt | 14914 | FCNGN4CC | 22 | H | : | [5 empty] | #9 | 60 | -2 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14914L | lhfrt | 14914 | FCNGN4CC | 22 | L | : | [5 empty] | #9 | 60 | -2 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14915H | lhfrt | 14915 | FCNGN5CC | 22 | H | : | [5 empty] | #9 | 60 | -2 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14915L | lhfrt | 14915 | FCNGN5CC | 22 | L | : | [5 empty] | #9 | 60 | -2 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149211 | lhfrt | 14921 | OCOTGT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149221 | lhfrt | 14922 | OCOTGT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149311 | lhfrt | 14931 | PALOVRD1 | 24 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149321 | lhfrt | 14932 | PALOVRD2 | 24 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149331 | lhfrt | 14933 | PALOVRD3 | 24 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149741 | lhfrt | 14974 | RED-CT1 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149751 | lhfrt | 14975 | RED-CT2 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149761 | lhfrt | 14976 | RED-CT3 | 18 | 1 | : | [5 empty] | #9 | 60 | -2 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149771 | lhfrt | 14977 | RED-CT4 | 18 | 1 | : | [5 empty] | #9 | 60 | -2 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149821 | lhfrt | 14982 | RED-ST1 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149831 | lhfrt | 14983 | RED-ST2 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149441 | lhfrt | 14944 | SAG. CT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149431 | lhfrt | 14943 | SAG. CT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.75 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149451 | lhfrt | 14945 | SAG. CT3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149541 | lhfrt | 14954 | WPHX GT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149571 | lhfrt | 14957 | WPHX GT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149511 | lhfrt | 14951 | WPHX CC1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149521 | lhfrt | 14952 | WPHX CC2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149531 | lhfrt | 14953 | WPHX CC3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -3 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.167 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149661 | lhfrt | 14966 | WPCC5CT1 | 15 | 1 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.117 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149671 | lhfrt | 14967 | WPCC5CT2 | 15 | 1 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.115 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149681 | lhfrt | 14968 | WPCC5ST1 | 16.5 | 1 | : | [5 empty] | #9 | 60 | -3.2 | -2.2 | 1.6 | 1.71 | 2.71 | 0 | 0 | 0 | 0 | 0 | 0.13 | 7.5 | 30 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
149611 | lhfrt | 14961 | YUCCACT1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -7.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149621 | lhfrt | 14962 | YUCCACT2 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -7.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149631 | lhfrt | 14963 | YUCCACT3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149641 | lhfrt | 14964 | YUCCACT4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149721 | lhfrt | 14972 | AGAVE PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | -3.2 | -3 | -2 | -1.7 | -0.7 | 1 | 2 | 2.2 | 0 | 0 | 0.6 | 0.5 | 700 | 600 | 600 | 700 | 0.1 | 0.6 | 0 | 0 | 0
857881 | lhfrt | 85788 | REDRCK | 0.42 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.25 | 0.2 | 0
857841 | lhfrt | 85784 | DSRTSND1 | 0.42 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | -4 | 0 | 0 | 0 | 0 | 200 | 180 | 30 | 7.5 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0
857851 | lhfrt | 85785 | DSRTSND2 | 0.8 | 1 | : | [5 empty] | #9 | 60 | -0.5 | -2.2 | 0.5 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1800 | 2000 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148291 | lhfrt | 14829 | Q289 BES | 0.63 | 1 | 14829 | Q289 BES | 0.63 | : |  |  | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 0
148511 | lhfrt | 14851 | Q227BES1 | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 1
148532 | lhfrt | 14853 | Q227BES2 | 34.5 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 1
149461 | lhfrt | 14946 | SOL GEN1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 6 | 1.8 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
149472 | lhfrt | 14947 | SOL GEN2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 6 | 1.8 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1565281 | lhfrt | 156528 | LITHIUM | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3.1 | 5 | 6 | -3.1 | -4.1 | -5 | 0 | 0 | 0 | 0 | 30 | 1 | 0.2 | 30 | 1 | 0.2 | 0 | 0 | 0 | 0 | 0
1563330 | lhfrt | 156333 | GRANJA_ES1 | 0.69 | E1 | : | [5 empty] | #9 | 60 | 2 | 1.7 | 1.6 | -3 | -2.7 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0.6 | 61 | 0 | 1 | 61 | 0 | 0 | 0 | 0 | 1
15633500 | lhfrt | 156335 | GRANJA_ES2 | 0.69 | E2 | : | [5 empty] | #9 | 60 | 2 | 1.7 | 1.6 | -3 | -2.7 | -1.6 | 0 | 0 | 0 | 0 | 0.01 | 0.6 | 61 | 0 | 1 | 61 | 0 | 0 | 0 | 0 | 1
156330P1 | lhfrt | 156330 | GRANJA_PV1 | 0.66 | P1 | : | [5 empty] | #9 | 60 | 5 | -2 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
156334P2 | lhfrt | 156334 | GRANJA_PV2 | 0.66 | P2 | : | [5 empty] | #9 | 60 | 5 | -2 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
151545S1 | lhfrt | 151545 | Q27T41_ESLO | 0.69 | S1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
151495S2 | lhfrt | 151495 | Q27T42_ESLO | 0.69 | S2 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
151620S1 | lhfrt | 151620 | Q27T1_BESLO | 0.69 | S1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
151622P1 | lhfrt | 151622 | Q27T41_PVLO | 0.63 | P1 | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
151623P2 | lhfrt | 151623 | Q27T42_PVLO | 0.63 | P2 | : | [5 empty] | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
151621P1 | lhfrt | 151621 | Q27T1_PV_LO | 0.63 | P1 | : | [5 empty] | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
1554351 | lhfrt | 155435 | GCLEL_PVS | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1554371 | lhfrt | 155437 | GCLCL_PVS | 0.63 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
1548281 | lhfrt | 154828 | GCLWL1_PVS | 0.63 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
1554492 | lhfrt | 155449 | GCLWL2_PVS | 0.63 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
1563481 | lhfrt | 156348 | BLACKJAK | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
1563581 | lhfrt | 156358 | Q60_PV | 0.6 | 1 | 156354 | Q60_HV | 230 | : |  |  | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
1563590 | lhfrt | 156359 | Q60_ES | 0.63 | E1 | 156354 | Q60_HV | 230 | : |  |  | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
156381P1 | lhfrt | 156381 | HVQ27_PV1 | 34.5 | P1 | : | [5 empty] | #9 | 60 | 3 | -13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156379S1 | lhfrt | 156379 | HVQ27_ES1 | 34.5 | S1 | : | [5 empty] | #9 | 60 | 3 | -13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156382P2 | lhfrt | 156382 | HVQ27_PV2 | 34.5 | P2 | : | [5 empty] | #9 | 60 | 3 | -13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156380S2 | lhfrt | 156380 | HVQ27_ES2 | 34.5 | S2 | : | [5 empty] | #9 | 60 | 3 | -13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1550211 | lhfrt | 155021 | CRE_PVC1 | 34.5 | 1 | 155011 | CREOSOTE | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1550641 | lhfrt | 155064 | CRE_BSC1 | 34.5 | 1 | 155011 | CREOSOTE | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1571972 | lhfrt | 157197 | CRE_PVC2 | 34.5 | 2 | 155011 | CREOSOTE | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1571982 | lhfrt | 157198 | CRE_BSC2 | 34.5 | 2 | 155011 | CREOSOTE | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1571993 | lhfrt | 157199 | CRE_PVC3 | 34.5 | 3 | 155011 | CREOSOTE | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1572153 | lhfrt | 157215 | CRE_BSC3 | 34.5 | 3 | 155011 | CREOSOTE | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
150030ST | lhfrt | 150030 | CHUKAR3S | 0.69 | ST | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 1
150035ST | lhfrt | 150035 | CHUKAR4S | 0.69 | ST | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 1
150029PV | lhfrt | 150029 | CHUKAR3G | 0.63 | PV | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 1
150034PV | lhfrt | 150034 | CHUKAR4G | 0.63 | PV | : | [5 empty] | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 1
155085ES | lhfrt | 155085 | HAO_Q44_BS | 0.48 | ES | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1553141 | lhfrt | 155314 | MES4A_PV1 | 0.63 | 1 | 154975 | MES45A_LV | 34.5 | : |  |  | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 1
155313ES | lhfrt | 155313 | MES4A_ES1 | 0.48 | ES | 154975 | MES45A_LV | 34.5 | : |  |  | #9 | 60 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.14 | 31 | 181 | 181 | 31 | 7.5 | 0.75 | 0.2 | 0 | 0 | 1
155010ES | lhfrt | 155010 | MES5A_ES2 | 0.48 | ES | 154975 | MES45A_LV | 34.5 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1549531 | lhfrt | 154953 | MES5A_PV2 | 0.63 | 1 | 154975 | MES45A_LV | 34.5 | : |  |  | #9 | 60 | 4 | 3 | 2 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0.16 | 350 | 650 | 0.16 | 650 | 0.0083 | 0.0083 | 0.0083 | 0.0083 | 0.0083 | 0
1548731 | lhfrt | 154873 | FLND_PV | 0.565 | 1 | : | [5 empty] | #9 | 60 | -2 | -3.5 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 300 | 1 | 0.1 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 1
1548751 | lhfrt | 154875 | FLND_E1 | 0.56 | 1 | : | [5 empty] | #1 | 60 | 0.7 | 1.7 | 1.8 | -0.7 | -1.7 | -2.3 | -2.8 | -3.1 | 0 | 0 | 181 | 31 | 0.0001 | 181 | 31 | 8 | 0.8 | 0.0001 | 0 | 0 | 1
1548772 | lhfrt | 154877 | FLND_E2 | 0.565 | 2 | : | [5 empty] | #9 | 60 | 0.7 | 1.7 | 1.8 | -0.7 | -1.7 | -2.3 | -2.8 | -3.1 | 0 | 0 | 181 | 31 | 0 | 181 | 31 | 8 | 0.8 | 0 | 0 | 0 | 1
1547261 | lhfrt | 154726 | Q55PVCOL | 34.5 | 1 | 154722 | Q55-HV | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1547271 | lhfrt | 154727 | Q55-BSCOL | 34.5 | 1 | 154722 | Q55-HV | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1500131 | lhfrt | 150013 | HALO1 | 0.62 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
151841 | lhfrt | 15184 | AVSOLAR2_48 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 2 | 1.2 | -1.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 300 | 300 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159011 | lhfrt | 15901 | AGUAFR 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159021 | lhfrt | 15902 | AGUAFR 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159031 | lhfrt | 15903 | AGUAFR 3 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159041 | lhfrt | 15904 | AGUAFR 4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159051 | lhfrt | 15905 | AGUAFR 5 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159061 | lhfrt | 15906 | AGUAFR 6 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159711 | lhfrt | 15971 | CORONAD1 | 22 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -1.6 | -2.2 | -2.7 | -3.1 | 0 | 0 | 0 | 0 | 0 | 300.1 | 60.1 | 8.5 | 1.3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
159721 | lhfrt | 15972 | CORONAD2 | 22 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -1.6 | -2.2 | -2.7 | -3.1 | 0 | 0 | 0 | 0 | 0 | 300.1 | 60.1 | 8.5 | 1.3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
151401 | lhfrt | 15140 | DBG-CT1 | 18 | 1 | : | [5 empty] | #9 | 60 | 3.01 | 2.11 | -2.5 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 10 | 10 | 0.1167 | 0 | 0 | 0 | 0 | 0 | 0 | 1
151411 | lhfrt | 15141 | DBG-CT2 | 18 | 1 | : | [5 empty] | #9 | 60 | 3.01 | 2.11 | -2.5 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 10 | 10 | 0.1167 | 0 | 0 | 0 | 0 | 0 | 0 | 1
151421 | lhfrt | 15142 | DBG-ST1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -2.22 | -2.72 | -3.62 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.75 | 0.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159311 | lhfrt | 15931 | HRSMS123 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159312 | lhfrt | 15931 | HRSMS123 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159313 | lhfrt | 15931 | HRSMS123 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159341 | lhfrt | 15934 | HRSMS4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159141 | lhfrt | 15914 | KYRENE 4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -2.9 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159151 | lhfrt | 15915 | KYRENE 5 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159161 | lhfrt | 15916 | KYRENE 6 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159181 | lhfrt | 15918 | KYREN 7S | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -1 | -1.9 | -2.9 | -3.9 | 0 | 0 | 0 | 0 | 0 | 30 | 360 | 30 | 0.8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
159191 | lhfrt | 15919 | KYREN 7A | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -2.9 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
151641 | lhfrt | 15164 | MES-CT1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
151651 | lhfrt | 15165 | MES-CT2 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
151661 | lhfrt | 15166 | MES-ST3 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.6 | -2.6 | -3.1 | -3.6 | 0 | 0 | 0 | 0 | 0 | 3 | 31 | 30 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 1
159411 | lhfrt | 15941 | MRMFLT12 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159412 | lhfrt | 15941 | MRMFLT12 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159511 | lhfrt | 15951 | RSVLTGEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159211 | lhfrt | 15921 | SANTAN 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159221 | lhfrt | 15922 | SANTAN 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159231 | lhfrt | 15923 | SANTAN 3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159241 | lhfrt | 15924 | SANTAN 4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159271 | lhfrt | 15927 | SANTN 5A | 18 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3.1 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159281 | lhfrt | 15928 | SANTN 5B | 18 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3.1 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159261 | lhfrt | 15926 | SANTN 5S | 18 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3.1 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159291 | lhfrt | 15929 | SANTN 6A | 18 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3.1 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159301 | lhfrt | 15930 | SANTN 6S | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3.1 | -3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159611 | lhfrt | 15961 | STEWMTN | 11 | 1 | : | [5 empty] | #9 | 60 | 2.8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1590461 | lhfrt | 159046 | ELEVENMILEPV | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1590471 | lhfrt | 159047 | ELEVENMILEBS | 0.48 | 1 | : | [5 empty] | #9 | 60 | -3 | -0.5 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 2 | 2 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599711 | lhfrt | 159971 | GIL-CT1A | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -1.6 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599711 | lhfrt | 159971 | GIL-CT1A | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599721 | lhfrt | 159972 | GIL-CT1B | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599731 | lhfrt | 159973 | GIL-CT2A | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599741 | lhfrt | 159974 | GIL-CT2B | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599751 | lhfrt | 159975 | GIL-CT3A | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599761 | lhfrt | 159976 | GIL-CT3B | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599771 | lhfrt | 159977 | GIL-CT4A | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599781 | lhfrt | 159978 | GIL-CT4B | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599791 | lhfrt | 159979 | GIL-ST1C | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599801 | lhfrt | 159980 | GIL-ST2C | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599811 | lhfrt | 159981 | GIL-ST3C | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1599821 | lhfrt | 159982 | GIL-ST4C | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -1 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
159013S1 | lhfrt | 159013 | MES1_1_85 | 0.42 | S1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | -1.7 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.1 | 0.75 | 0 | 0 | 1
159014S1 | lhfrt | 159014 | MES2_1_55 | 0.42 | S1 | 159000 | MESSOLAR | 230 | : |  |  | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 1
159015S1 | lhfrt | 159015 | MES3_1_84 | 0.42 | S1 | 159000 | MESSOLAR | 230 | : |  |  | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 1
1609021 | lhfrt | 160902 | DMPCCT #1 | 13.8 | 1 | : | #9 | 60 | 1.8 | -1.5 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609181 | lhfrt | 160918 | SPR_GEN1 | 19 | 1 | : | [5 empty] | #9 | 60 | 2 | -1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 7.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609191 | lhfrt | 160919 | SPR_GEN2 | 19 | 1 | : | [5 empty] | #9 | 60 | 2 | -1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 7.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609201 | lhfrt | 160920 | SPR_GEN3 | 21 | 1 | : | [5 empty] | #9 | 60 | 2.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609211 | lhfrt | 160921 | SPR_GEN4 | 21 | 1 | : | [5 empty] | #9 | 60 | 2.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609251 | lhfrt | 160925 | SUNDT_GEN3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
1609261 | lhfrt | 160926 | SUNDT_GEN4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
1609221 | lhfrt | 160922 | SUNDT_CT | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
1609222 | lhfrt | 160922 | SUNDT_CT | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
1609281 | lhfrt | 160928 | SUNDT_RICE1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609282 | lhfrt | 160928 | SUNDT_RICE1 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609283 | lhfrt | 160928 | SUNDT_RICE1 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609284 | lhfrt | 160928 | SUNDT_RICE1 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609285 | lhfrt | 160928 | SUNDT_RICE1 | 13.8 | 5 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609291 | lhfrt | 160929 | SUNDT_RICE2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609292 | lhfrt | 160929 | SUNDT_RICE2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609293 | lhfrt | 160929 | SUNDT_RICE2 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609294 | lhfrt | 160929 | SUNDT_RICE2 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609295 | lhfrt | 160929 | SUNDT_RICE2 | 13.8 | 5 | : | [5 empty] | #9 | 60 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609341 | lhfrt | 160934 | OSO_G11 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.5 | 60.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609351 | lhfrt | 160935 | OSO_G12 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.5 | 60.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609361 | lhfrt | 160936 | OSO_G21 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.5 | 60.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1815101 | lhfrt | 181510 | DRYLK E1 BS | 0.645 | 1 | 181507 | DRYLK E1 HV | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1815021 | lhfrt | 181502 | DRYLK E2 PVG | 34.5 | 1 | 181500 | DRYLAKE EAST | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1815041 | lhfrt | 181504 | DRYLK E2 BSG | 0.645 | 1 | 181500 | DRYLAKE EAST | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1806031 | lhfrt | 180603 | RG BESS GEN | 0.66 | 1 | : | [5 empty] | #9 | 60 | 5 | 3 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 60 | 60 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187531 | lhfrt | 18753 | GEM-G1 | 0.66 | 1 | 18750 | GEMINI | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -4 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 1.5 | 0.75 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
187561 | lhfrt | 18756 | GEM-G2 | 0.66 | 1 | 18750 | GEMINI | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -4 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 1.5 | 0.75 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
187591 | lhfrt | 18759 | GEM-G3 | 0.66 | 1 | 18750 | GEMINI | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -4 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 1.5 | 0.75 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
187621 | lhfrt | 18762 | GEM-G4 | 0.66 | 1 | 18750 | GEMINI | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -4 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 1.5 | 0.75 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
1809451 | lhfrt | 180945 | CHCKWLLA G1 | 0.69 | 1 | : | [5 empty] | #1 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
1809502 | lhfrt | 180950 | CHCKWLLA G2 | 0.69 | 2 | : | [5 empty] | #1 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
1812431 | lhfrt | 181243 | BOULDER3PV G | 0.38 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.3 | 0.008334 | 0.008334 | 0.008334 | 0
1810331 | lhfrt | 181033 | DRYLAKE-B1 | 34.5 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 0
1810362 | lhfrt | 181036 | DRYLAKE-B2 | 34.5 | 2 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 0
187811 | lhfrt | 18781 | EGLESHDW-G1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187821 | lhfrt | 18782 | EGLESHDW-G2 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187841 | lhfrt | 18784 | STRGE_1_GEN | 0.55 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187831 | lhfrt | 18783 | STRGE_2_GEN | 0.55 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180653PV | lhfrt | 180653 | ACS_GEN | 0.645 | PV | 18019 | H ALLEN | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0.008334 | 0.008334 | 0
1858041 | lhfrt | 185804 | DRYLK GEN | 0.66 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
1810402 | lhfrt | 181040 | BOULDER2PV-G | 0.38 | 2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 0 | 0 | 0 | 0.17 | 0.75 | 7.5 | 30 | 180 | 180 | 0.17 | 0 | 0 | 0 | 0
18566PV | lhfrt | 18566 | CMS5-G1 | 0.36 | PV | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 30 | 180 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0
18571PV | lhfrt | 18571 | CMS5-G2 | 0.36 | PV | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 30 | 180 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0
1810021 | lhfrt | 181002 | PLAYA1-G | 0.55 | 1 | : | [5 empty] | #9 | 60 | 3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1810132 | lhfrt | 181013 | PLAYA2-G | 0.55 | 2 | : | [5 empty] | #9 | 60 | 3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18265GT | lhfrt | 18265 | LVCOGEN | 13.1 | GT | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 7.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182611 | lhfrt | 18261 | HA CT1 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -2.7 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182621 | lhfrt | 18262 | HA CT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.2 | -2.7 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.75 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1810061 | lhfrt | 181006 | BOULDER1PV-G | 0.385 | 1 | 181008 | BOULDER1PV-C | 34.5 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -4 | -4 | 0.7 | 2 | 3 | 4 | 4 | 1000 | 200 | 40 | 5 | 5 | 1000 | 200 | 40 | 2 | 2 | 0
182555 | lhfrt | 18255 | CLARK 5 | 13.8 | 5 | : | [5 empty] | #8 | 60 | -3 | -2.2 | -1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 8 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182566 | lhfrt | 18256 | CLARK 6 | 13.8 | 6 | : | [5 empty] | #8 | 60 | -3 | -2.2 | -1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 8 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182577 | lhfrt | 18257 | CLARK 7 | 13.8 | 7 | : | [5 empty] | #8 | 60 | -3 | -2.2 | -1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 8 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182588 | lhfrt | 18258 | CLARK 8 | 13.8 | 8 | : | [5 empty] | #8 | 60 | -3 | -2.2 | -1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 8 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182599 | lhfrt | 18259 | CLARK 9 | 13.8 | 9 | : | [5 empty] | #8 | 60 | -3 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1826010 | lhfrt | 18260 | CLARK10 | 13.8 | 10 | : | [5 empty] | #8 | 60 | -3 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18265ST | lhfrt | 18265 | LVCOGEN | 13.1 | ST | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18276B | lhfrt | 18276 | NCA2A | 13.8 | B | : | [5 empty] | #8 | 60 | -1.6 | -2.2 | 3 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0
18276C | lhfrt | 18276 | NCA2A | 13.8 | C | : | [5 empty] | #8 | 60 | -1.6 | -2.2 | 3 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0
18277A | lhfrt | 18277 | NCA2B | 13.8 | A | : | [5 empty] | #8 | 60 | -1.6 | -2.2 | 3 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0
18277ST | lhfrt | 18277 | NCA2B | 13.8 | ST | : | [5 empty] | #8 | 60 | -1.6 | -2.2 | 3 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0
182821 | lhfrt | 18282 | SAGUAR 1 | 14 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182832 | lhfrt | 18283 | SAGUAR 2 | 14 | 2 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182843 | lhfrt | 18284 | SAGUAR 3 | 14 | 3 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183151 | lhfrt | 18315 | APEX-PV-G | 0.48 | 1 | : | [5 empty] | #8 | 60 | -3 | -1.6 | 1.6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.254 | 5.2 | 5.16 | 1.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184011 | lhfrt | 18401 | SLHWKG1 | 17 | 1 | : | [5 empty] | #9 | 60 | -3.6 | -3.2 | -2.7 | -2.2 | -1.6 | -0.6 | 1.5 | 1.6 | 1.7 | 3.01 | 0 | 0.12 | 0.75 | 7.5 | 30 | 180 | 600 | 30 | 1 | 0.1 | 0
184022 | lhfrt | 18402 | SLHWKG2 | 17 | 2 | : | [5 empty] | #9 | 60 | -3.6 | -3.2 | -2.7 | -2.2 | -1.6 | -0.6 | 1.5 | 1.6 | 1.7 | 3.01 | 0 | 0.12 | 0.75 | 7.5 | 30 | 180 | 600 | 30 | 1 | 0.1 | 0
184071 | lhfrt | 18407 | HIGGINS3 | 21 | 1 | : | [5 empty] | #9 | 60 | -3.2 | -2.71 | 1.61 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0.75 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184081 | lhfrt | 18408 | HIGGINS2 | 18 | 1 | : | [5 empty] | #9 | 60 | -3.2 | -2.5 | 2.11 | 3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 10 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184091 | lhfrt | 18409 | HIGGINS1 | 18 | 1 | : | [5 empty] | #9 | 60 | -3.2 | -2.5 | 2.11 | 3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 10 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184261 | lhfrt | 18426 | HA CC1 | 18 | 1 | : | [5 empty] | #8 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184271 | lhfrt | 18427 | HA CC2 | 18 | 1 | : | [5 empty] | #8 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184281 | lhfrt | 18428 | HA CC3 | 18 | 1 | : | [5 empty] | #8 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184311 | lhfrt | 18431 | LENZIE 1 | 18 | 1 | : | [5 empty] | #8 | 60 | -4 | -2.6 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184321 | lhfrt | 18432 | LENZIE 2 | 18 | 1 | : | [5 empty] | #8 | 60 | -4 | -2.6 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184331 | lhfrt | 18433 | LENZIE 3 | 18 | 1 | : | [5 empty] | #8 | 60 | -4 | -2.6 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184341 | lhfrt | 18434 | LENZIE 4 | 18 | 1 | : | [5 empty] | #8 | 60 | -4 | -2.6 | -2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 33 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184351 | lhfrt | 18435 | LENZIE 5 | 18 | 1 | : | [5 empty] | #8 | 60 | -4 | -2.6 | -2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 33 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184361 | lhfrt | 18436 | LENZIE 6 | 18 | 1 | : | [5 empty] | #8 | 60 | -4 | -2.6 | -2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 33 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184941 | lhfrt | 18494 | MTV_G1 | 0 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184952 | lhfrt | 18495 | MTV_G2 | 0 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185961 | lhfrt | 18596 | NSO | 13.8 | 1 | : | [5 empty] | #8 | 60 | 1.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880411 | lhfrt | 18804 | CLARKPB1-1 | 13.8 | 11 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880413 | lhfrt | 18804 | CLARKPB1-1 | 13.8 | 13 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880512 | lhfrt | 18805 | CLARKPB1-2 | 13.8 | 12 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880514 | lhfrt | 18805 | CLARKPB1-2 | 13.8 | 14 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880615 | lhfrt | 18806 | CLARKPB2-1 | 13.8 | 15 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880617 | lhfrt | 18806 | CLARKPB2-1 | 13.8 | 17 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880716 | lhfrt | 18807 | CLARKPB2-2 | 13.8 | 16 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880718 | lhfrt | 18807 | CLARKPB2-2 | 13.8 | 18 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880819 | lhfrt | 18808 | CLARKPB3-1 | 13.8 | 19 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880821 | lhfrt | 18808 | CLARKPB3-1 | 13.8 | 21 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880920 | lhfrt | 18809 | CLARKPB3-2 | 13.8 | 20 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1880922 | lhfrt | 18809 | CLARKPB3-2 | 13.8 | 22 | : | [5 empty] | #8 | 60 | -3.6 | -3 | 2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188752 | lhfrt | 18875 | SILV_ST_G2 | 0.4 | 2 | : | [5 empty] | #8 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188741 | lhfrt | 18874 | SILV_ST_G1 | 0.4 | 1 | : | [5 empty] | #8 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890211 | lhfrt | 189021 | DESERT VIEW | 230 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890161 | lhfrt | 189016 | INNOVATION | 230 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182873 | lhfrt | 18287 | SUNRISE3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | 1.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
182884 | lhfrt | 18288 | SUNRISE4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -3 | 1.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
182895 | lhfrt | 18289 | SUNRISE5 | 13.8 | 5 | : | [5 empty] | #9 | 60 | -3 | 1.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
188841 | lhfrt | 18884 | SPECTRUM GEN | 0 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.6 | 1.61 | 1.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 30 | 30 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182701 | lhfrt | 18270 | NCA1A | 14 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 30 | 7.5 | 0.03 | 0 | 0 | 0 | 0 | 0
18270ST | lhfrt | 18270 | NCA1A | 14 | ST | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.01 | 30 | 180 | 30 | 7.5 | 0.01 | 0 | 0 | 0 | 0 | 0
182712 | lhfrt | 18271 | NCA1B | 14 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 30 | 7.5 | 0.03 | 0 | 0 | 0 | 0 | 0
182713 | lhfrt | 18271 | NCA1B | 14 | 3 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 30 | 7.5 | 0.03 | 0 | 0 | 0 | 0 | 0
18700B | lhfrt | 18700 | LVCOGEN2-B | 13.8 | B | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 7.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184033 | lhfrt | 18403 | SLHWKG3 | 18 | 3 | : | [5 empty] | #9 | 60 | -3.6 | -3.2 | -2.7 | -2.2 | -1.6 | -0.6 | 1.5 | 1.6 | 1.7 | 3.01 | 0 | 0.12 | 0.75 | 7.5 | 30 | 180 | 600 | 30 | 1 | 0.1 | 0
18702A | lhfrt | 18702 | LVCOGEN2-A | 13.8 | A | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 7.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18702ST | lhfrt | 18702 | LVCOGEN2-A | 13.8 | ST | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18699B | lhfrt | 18699 | LVCOGEN3-B | 13.8 | B | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 7.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18703A | lhfrt | 18703 | LVCOGEN3-A | 13.8 | A | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 7.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18703ST | lhfrt | 18703 | LVCOGEN3-A | 13.8 | ST | : | [5 empty] | #8 | 60 | -3 | -2.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198901 | lhfrt | 19890 | TNS-PV | 0.66 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | 0.7 | 2 | 3 | 4 | 0 | 0 | 6550 | 90 | 10 | 0.25 | 6550 | 90 | 5 | 0.25 | 0 | 0 | 0
198911 | lhfrt | 19891 | TNS-ES | 0.66 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | 0.7 | 2 | 3 | 4 | 0 | 0 | 6550 | 90 | 10 | 0.25 | 6550 | 90 | 5 | 0.25 | 0 | 0 | 0
199811 | lhfrt | 19981 | WTHHLS1_WT1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199851 | lhfrt | 19985 | WTHHLS2_WT1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199862 | lhfrt | 19986 | WTHHLS2_WT2 | 0.69 | 2 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206551 | lhfrt | 20655 | PPF-01-PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206571 | lhfrt | 20657 | PPF-01-BESS | 0.6 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
206598 | lhfrt | 20659 | PPF-08-PV | 0.63 | 8 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2066515 | lhfrt | 20665 | PPF-15-PV | 0.63 | 15 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206672 | lhfrt | 20667 | PPF-02-BESS | 0.6 | 2 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
2066922 | lhfrt | 20669 | PPF-22-PV | 0.63 | 22 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2067529 | lhfrt | 20675 | PPF-29-PV | 0.63 | 29 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206773 | lhfrt | 20677 | PPF-03-BESS | 0.6 | 3 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
2067936 | lhfrt | 20679 | PPF-36-PV | 0.63 | 36 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200501 | lhfrt | 20050 | SMA-6.0 | 6 | 1 | : | [5 empty] | #9 | 60 | -9 | -4.998 | -3 | 3 | 4.98 | 0 | 0 | 0 | 0 | 0 | 0.2625 | 1.05 | 63 | 63 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
200065 | lhfrt | 20006 | PJZ-U5 | 15 | 5 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200076 | lhfrt | 20007 | PJZ-U6 | 15 | 6 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200147 | lhfrt | 20014 | PJZ-U7 | 18 | 7 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200088 | lhfrt | 20008 | PJZ-U8 | 21 | 8 | : | [5 empty] | #9 | 60 | -1.8 | -3.6 | -5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200099 | lhfrt | 20009 | PJZ-U9 | 21 | 9 | : | [5 empty] | #9 | 60 | -1.8 | -3.6 | -5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200121 | lhfrt | 20012 | TTI-U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
200132 | lhfrt | 20013 | TTI-U2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
200101 | lhfrt | 20010 | CCBC-U1 | 16.5 | 1 | : | [5 empty] | #9 | 60 | -3.1 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200112 | lhfrt | 20011 | CCBC-U2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200991 | lhfrt | 20099 | CIP-U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
201561 | lhfrt | 20156 | MXI-U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202312 | lhfrt | 20231 | MXI-U2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202323 | lhfrt | 20232 | MXI-U3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201415 | lhfrt | 20141 | CPU-U5 | 13.8 | 5 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201051 | lhfrt | 20105 | CPD-U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201062 | lhfrt | 20106 | CPD-U2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201092 | lhfrt | 20109 | CPT-U2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201431 | lhfrt | 20143 | CPC-U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201442 | lhfrt | 20144 | CPC-U2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201453 | lhfrt | 20145 | CPC-U3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201464 | lhfrt | 20146 | CPC-U4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201081 | lhfrt | 20108 | CPT-U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201882 | lhfrt | 20188 | LRP-U2 | 16 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201903 | lhfrt | 20190 | LRP-U3 | 16 | 3 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201894 | lhfrt | 20189 | LRP-U4 | 21 | 4 | : | [5 empty] | #9 | 60 | -1.2 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204161 | lhfrt | 20416 | JOV-U1 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.2 | -2.2 | -2.7 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 7.5 | 0.75 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204172 | lhfrt | 20417 | JOV-U2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3.1 | -3.6 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205121 | lhfrt | 20512 | MOE-34.5 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210401 | lhfrt | 21040 | BESS_GEN | 0.2 | 1 | : | [5 empty] | #9 | 60 | 6 | 3 | 2.5 | 1.7 | -2.5 | -3.5 | -6 | -9 | 0 | 0 | 0.25 | 10 | 10 | 30 | 10 | 10 | 1 | 0.25 | 99999 | 99999 | 0
216811 | lhfrt | 21681 | HELS_KTCHN-G | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211151 | lhfrt | 21115 | VIKING PV-G | 0.63 | 1 | 21120 | VIKING | 230 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211162 | lhfrt | 21116 | VIKING BAT-G | 0.48 | 2 | 21120 | VIKING | 230 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213501 | lhfrt | 21350 | HOLT_BESS_BS | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 99999 | 99999 | 0
210831 | lhfrt | 21083 | OCOTILLO-W_B | 0.95 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217411 | lhfrt | 21741 | IPP142A_PV | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217421 | lhfrt | 21742 | IPP142A_BS | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217531 | lhfrt | 21753 | IPP143_PV | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217541 | lhfrt | 21754 | IPP143_BS | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217591 | lhfrt | 21759 | IPP140_PV | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217601 | lhfrt | 21760 | IPP140_BS | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216661 | lhfrt | 21666 | HEBER 1 | 13.8 | 1 | : | [5 empty] | #8 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
216662 | lhfrt | 21666 | HEBER 1 | 13.8 | 2 | : | [5 empty] | #8 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
2101211 | lhfrt | 21012 | HEBER1 | 13.8 | 11 | : | [5 empty] | #8 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
216511 | lhfrt | 21651 | SIG13.8 | 13.8 | 1 | : | [5 empty] | #8 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
216512 | lhfrt | 21651 | SIG13.8 | 13.8 | 2 | : | [5 empty] | #8 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
213861 | lhfrt | 21386 | SEVILLE3_G | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217071 | lhfrt | 21707 | VEGA_2_PV-G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217081 | lhfrt | 21708 | VEGA_2_BAT-G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217261 | lhfrt | 21726 | VEGA_3_PV-G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217271 | lhfrt | 21727 | VEGA_3_BAT-G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217331 | lhfrt | 21733 | VEGA_4_PV-G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217341 | lhfrt | 21734 | VEGA_4_BAT-G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219621 | lhfrt | 21962 | NBSOLAR-BAT_G | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.7 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 10 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219651 | lhfrt | 21965 | NBSOLAR-PV_G | 0.66 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.7 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 10 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211081 | lhfrt | 21108 | VEGA-PV_G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 0
211121 | lhfrt | 21112 | VEGA-BESS_G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0
214581 | lhfrt | 21458 | CLGRN_G | 0.38 | 1 | 21459 | CLGRN_B1 | 92 | : |  |  | #9 | 60 | -5 | -3 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 60 | 600 | 60 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0
218741 | lhfrt | 21874 | CSF_GEN | 0.41 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.001 | 30 | 180 | 0.001 | 1 | 15 | 30 | 180 | 0 | 0 | 0
218761 | lhfrt | 21876 | V2_GEN | 0.38 | 1 | : | [5 empty] | #9 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210411 | lhfrt | 21041 | WISTER_G | 0.48 | 1 | 21035 | WISTER | 92 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.08 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
212051 | lhfrt | 21205 | ALHAMBRA | 0.36 | 1 | : | [5 empty] | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
212061 | lhfrt | 21206 | ARKANSAS | 0.36 | 1 | : | [5 empty] | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
212141 | lhfrt | 21214 | SONORA | 0.36 | 1 | : | [5 empty] | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
218781 | lhfrt | 21878 | MDWY3_G | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210261 | lhfrt | 21026 | SOL-GEN | 0.42 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
215121 | lhfrt | 21512 | IVSC-2a | 0.69 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.16 | 30 | 180 | 0.16 | 1 | 15 | 30 | 180 | 0 | 0 | 0
215021 | lhfrt | 21502 | IVSC-1_G | 0.208 | 1 | : | [5 empty] | #9 | 60 | 2 | -2.3 | -2.8 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 10 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210481 | lhfrt | 21048 | HEBERPV_G | 0.38 | 1 | : | [5 empty] | #99 | 60 | -3.5 | -1 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 300 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219931 | lhfrt | 21993 | MDWY2_G | 0.42 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -3 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 180 | 0.01 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210161 | lhfrt | 21016 | MDWY4_G | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.8 | -3 | -1.8 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 185 | 3 | 90 | 185 | 0 | 0 | 0 | 0 | 0
210401 | lhfrt | 21040 | BESS_GEN | 0.2 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 99999 | 99999 | 0
213752 | lhfrt | 21375 | SEVILLE2_G | 0.36 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.7 | 1.7 | -4 | -4 | -3 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0
213831 | lhfrt | 21383 | SEVILLE1_G | 0.36 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.7 | 1.7 | -4 | -4 | -3 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0
210181 | lhfrt | 21018 | CTZNS_G | 0.418 | 1 | : | [5 empty] | #9 | 60 | 2 | 1 | -1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 200 | 300 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210081 | lhfrt | 21008 | SDSU_GEN | 0.42 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219891 | lhfrt | 21989 | MDWY1_G | 0.42 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210321 | lhfrt | 21032 | OCOTILLO-W_G | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216471 | lhfrt | 21647 | ELSTM 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216491 | lhfrt | 21649 | ELSTM 3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0.016 | 0 | 30 | 180 | 0 | 0 | 0 | 0
210201 | lhfrt | 21020 | REPU3-1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0.016 | 0 | 30 | 180 | 0 | 0 | 0 | 0
210211 | lhfrt | 21021 | REPU3-2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0.016 | 0 | 30 | 180 | 0 | 0 | 0 | 0
216481 | lhfrt | 21648 | ELSTM4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216591 | lhfrt | 21659 | DROP2 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216592 | lhfrt | 21659 | DROP2 | 6.9 | 2 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216551 | lhfrt | 21655 | DROP3 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216552 | lhfrt | 21655 | DROP3 | 6.9 | 2 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216561 | lhfrt | 21656 | DROP4 1 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.75 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216571 | lhfrt | 21657 | DROP4 2 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
216601 | lhfrt | 21660 | DROP5 | 4.16 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210001 | lhfrt | 21000 | GPNI01 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.05 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210501 | lhfrt | 21050 | GPNI02 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.05 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213681 | lhfrt | 21368 | PILOTKNB | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
213682 | lhfrt | 21368 | PILOTKNB | 13.8 | 2 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 1.6 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.76 | 0.08 | 0.08 | 30 | 0 | 0 | 0 | 0 | 0
210711 | lhfrt | 21071 | YUCCAGEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238711 | lhfrt | 23871 | Q1662_ES | 0.66 | 1 | 23869 | Q1662_HV | 69 | 1 | 1 | : | #1 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234751 | lhfrt | 23475 | GR1194_GEN | 0.385 | 1 | 23470 | GR1194_HV | 69 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2225610 | lhfrt | 22256 | ESCNDIDO | 69 | 10 | : | [5 empty] | #9 | 60 | -3 | -1.5 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2225611 | lhfrt | 22256 | ESCNDIDO | 69 | 11 | : | [5 empty] | #9 | 60 | -3 | -1.5 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2225612 | lhfrt | 22256 | ESCNDIDO | 69 | 12 | : | [5 empty] | #9 | 60 | -3 | -1.5 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234211 | lhfrt | 23421 | IV GEN4 G1 | 0.69 | 1 | 23428 | WCS | 230 | : |  |  | #9 | 60 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 30 | 180 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0
234251 | lhfrt | 23425 | Q1531 G2 | 0.69 | 1 | 23579 | Q1531_BDS_EXP | 230 | : |  |  | #9 | 60 | 2 | 1.2 | -1.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 300 | 300 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235841 | lhfrt | 23584 | Q1531 G3 | 0.69 | 1 | 23579 | Q1531_BDS_EXP | 230 | : |  |  | #9 | 60 | 2 | 1.2 | -1.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 300 | 300 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235441 | lhfrt | 23544 | AV GEN1_BESS | 0.64 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
235191 | lhfrt | 23519 | Q1169_BESS2 | 0.64 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
231551 | lhfrt | 23155 | DU GEN1 G1 | 0.36 | 1 | 22356 | IMPRLVLY | 230 | : |  |  | #9 | 60 | 1.7 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231561 | lhfrt | 23156 | DU GEN1 G2 | 0.36 | 1 | 22356 | IMPRLVLY | 230 | : |  |  | #9 | 60 | 1.7 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232981 | lhfrt | 23298 | DW GEN1 G1 | 0.31 | 1 | 23293 | DW GEN1 230 | 230 | : |  |  | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232991 | lhfrt | 23299 | DW GEN1 G2 | 0.31 | 1 | 23293 | DW GEN1 230 | 230 | : |  |  | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234011 | lhfrt | 23401 | DW GEN3 G1 | 0.33 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
234022 | lhfrt | 23402 | DW GEN3 G2 | 0.33 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
232871 | lhfrt | 23287 | DW GEN5 G1 | 0.42 | 1 | : | [5 empty] | #9 | 60 | 3 | 2 | 1 | -1 | -2 | -3 | 0 | 0 | 0 | 0 | 0.1 | 5 | 180 | 180 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0
229971 | lhfrt | 22997 | INTBCT | 16 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3.5 | -20 | 1.6 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 2.4 | 1 | 30 | 0 | 0 | 0 | 0 | 0
229961 | lhfrt | 22996 | INTBST | 18 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3.5 | -20 | 1.6 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 2.4 | 1 | 30 | 0 | 0 | 0 | 0 | 0
229771 | lhfrt | 22977 | AGUACAL1 | 0.324 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229782 | lhfrt | 22978 | AGUACAL2 | 0.324 | 2 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234121 | lhfrt | 23412 | MRGT GEN1 | 0.6 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0.75 | 30 | 180 | 0.3 | 30 | 180 | 0 | 0 | 0 | 0 | 0
226051 | lhfrt | 22605 | OTAYMGT1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226061 | lhfrt | 22606 | OTAYMGT2 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226071 | lhfrt | 22607 | OTAYMST1 | 16 | 1 | : | [5 empty] | #9 | 60 | 1.81 | -3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231621 | lhfrt | 23162 | PIO PICO 1A | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
231631 | lhfrt | 23163 | PIO PICO 1B | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
231641 | lhfrt | 23164 | PIO PICO 1C | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
235601 | lhfrt | 23560 | Q1047_BESS | 0.55 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234161 | lhfrt | 23416 | Q1166_ES_G1 | 0.6 | 1 | 23434 | Q1166_HV_1 | 230 | : |  |  | #9 | 60 | 0.5 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
234381 | lhfrt | 23438 | Q1166_ES_G2 | 0.6 | 1 | 23434 | Q1166_HV_1 | 230 | : |  |  | #9 | 60 | 0.5 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
232311 | lhfrt | 23231 | Q1432_PV | 0.385 | 1 | : | [5 empty] | #1 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
232531 | lhfrt | 23253 | Q1432_ES | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229691 | lhfrt | 22969 | Q1532_GEN | 34.5 | 1 | : | [5 empty] | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
2384112 | lhfrt | 23841 | Q1657_ES | 0.6 | 12 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2387112 | lhfrt | 23871 | Q1662_ES | 34.5 | 12 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 1 | 1 | 6550 | 90 | 5 | 1 | 1 | 0
239291 | lhfrt | 23929 | Q1669_ES | 0.6 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2393312 | lhfrt | 23933 | Q1670_ES | 0.6 | 12 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
239591 | lhfrt | 23959 | Q1673_ES | 0.48 | 1 | : | [5 empty] | #9 | 60 | -2 | -3.5 | -5 | 0 | 0 | 2 | 3.5 | 5 | 0 | 0 | 300 | 1 | 0.2 | 0 | 0 | 300 | 1 | 0.2 | 0 | 0 | 0
230421 | lhfrt | 23042 | Q1806_GEN | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
237101 | lhfrt | 23710 | OM GEN4_ES1 | 0.507 | 1 | 23707 | OM GEN4_HV | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
239611 | lhfrt | 23961 | OM GEN4_ES2 | 0.63 | 1 | 23707 | OM GEN4_HV | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
231001 | lhfrt | 23100 | ECO GEN1 | 0.65 | 1 | : | [5 empty] | #0 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231082 | lhfrt | 23108 | ECO_GEN1G2_6 | 0.65 | 2 | : | [5 empty] | #0 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231083 | lhfrt | 23108 | ECO_GEN1G2_6 | 0.65 | 3 | : | [5 empty] | #0 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236271 | lhfrt | 23627 | VC GEN1_GEN1 | 34.5 | 1 | 23629 | VC GEN1_HV | 69 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
236281 | lhfrt | 23628 | VC GEN1_GEN2 | 34.5 | 1 | 23629 | VC GEN1_HV | 69 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
229911 | lhfrt | 22991 | Q1675_GEN | 34.5 | 1 | 23629 | VC GEN1_HV | 69 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
235971 | lhfrt | 23597 | DW GEN8_BESS | 0.69 | 1 | 23592 | DW GEN8_HV | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
228981 | lhfrt | 22898 | Q106A_G1 | 0.55 | 1 | 23288 | BOULEVRD | 138 | : |  |  | #9 | 60 | 6 | 2.4 | -3.6 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2 | 2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233521 | lhfrt | 23352 | ECO GEN2 | 0.55 | 1 | 22932 | ECO | 138 | : |  |  | #9 | 60 | 1.7 | 0.6 | -4 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 180 | 5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234401 | lhfrt | 23440 | DW GEN2 G1 | 0.36 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234421 | lhfrt | 23442 | DW GEN4 G1 | 0.6 | 1 | : | [5 empty] | #9 | 60 | 3 | 2 | 1 | -3 | -2 | -1 | 0 | 0 | 0 | 0 | 0.1 | 5 | 180 | 0.1 | 60 | 180 | 0 | 0 | 0 | 0 | 0
234431 | lhfrt | 23443 | DW GEN4 G2 | 0.6 | 1 | : | [5 empty] | #9 | 60 | 3 | 2 | 1 | -3 | -2 | -1 | 0 | 0 | 0 | 0 | 0.1 | 5 | 180 | 0.1 | 60 | 180 | 0 | 0 | 0 | 0 | 0
234411 | lhfrt | 23441 | DW GEN6 | 0.6 | 1 | : | [5 empty] | #9 | 60 | 0.5 | 2 | -1.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.16 | 300 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233091 | lhfrt | 23309 | IV GEN3 G1 | 0.315 | 1 | 23306 | IV GEN3 | 230 | : |  |  | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233011 | lhfrt | 23301 | IV GEN3 G2 | 0.315 | 1 | 23306 | IV GEN3 | 230 | : |  |  | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227171 | lhfrt | 22717 | SANLUSRY A1 | 17.5 | 1 | : | [5 empty] | #9 | 60 | -3 | -4.2 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.5 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227151 | lhfrt | 22715 | SANLUSRY B1 | 17.5 | 1 | : | [5 empty] | #9 | 60 | -3 | -4.2 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.5 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237011 | lhfrt | 23701 | SONGS SC A1 | 17.5 | 1 | : | [5 empty] | #9 | 60 | -3 | -4.2 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.5 | 10 | 0.5 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
222621 | lhfrt | 22262 | PEN_CT1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0.1 | 30 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0
222631 | lhfrt | 22263 | PEN_CT2 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0.1 | 30 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0
222651 | lhfrt | 22265 | PEN_ST | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0.1 | 30 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0 | 0
220821 | lhfrt | 22082 | BR GEN1 | 0.36 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226281 | lhfrt | 22628 | PA GEN1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -3 | 1.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226291 | lhfrt | 22629 | PA GEN2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -3 | 1.4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221491 | lhfrt | 22149 | CALPK_BD | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221531 | lhfrt | 22153 | CALPK_ES | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233141 | lhfrt | 23314 | OCO GEN G1 | 0.69 | 1 | 23311 | OCOTILLO 1 | 500 | 1 | 1 | : | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0
233181 | lhfrt | 23318 | OCO GEN G2 | 0.69 | 1 | 23311 | OCOTILLO 1 | 500 | 1 | 1 | : | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0
229451 | lhfrt | 22945 | BUE GEN 1_G2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 180 | 30 | 0.04 | 180 | 7.5 | 0.04 | 0 | 0 | 0 | 0 | 0
229491 | lhfrt | 22949 | BUE GEN 1_G4 | 0.69 | 1 | 22881 | BUE GEN 1 | 138 | : |  |  | #9 | 60 | -3 | -2.2 | -0.06 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0.03 | 7.5 | 180 | 0.03 | 30 | 180 | 0 | 0 | 0 | 0 | 0
230071VW | lhfrt | 230071 | GR1201_GEN1 | 0.72 | VW | : | [5 empty] | #9 | 60 | 1.06 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230076VW | lhfrt | 230076 | GR1201_GEN2 | 0.72 | VW | : | [5 empty] | #9 | 60 | 1.06 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230093VW | lhfrt | 230093 | GR1202_G1 | 0.72 | VW | 230091 | GR1202_MV1 | 34.5 | : |  |  | #9 | 60 | 4.2 | 3.6 | -4.8 | -4.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0.2 | 10 | 0.2 | 0.4 | 30 | 0 | 0 | 0 | 0 | 0 | 0
230095VW | lhfrt | 230095 | GR1202_G2 | 0.72 | VW | 230091 | GR1202_MV1 | 34.5 | : |  |  | #9 | 60 | 4.2 | 3.6 | -4.8 | -4.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0.2 | 10 | 0.2 | 0.4 | 30 | 0 | 0 | 0 | 0 | 0 | 0
230100VW | lhfrt | 230100 | GR1202_G3 | 0.72 | VW | 230098 | GR1202_MV2 | 34.5 | : |  |  | #9 | 60 | 4.2 | 3.6 | -4.8 | -4.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0.2 | 10 | 0.2 | 0.4 | 30 | 0 | 0 | 0 | 0 | 0 | 0
230102VW | lhfrt | 230102 | GR1202_G4 | 0.72 | VW | 230098 | GR1202_MV2 | 34.5 | : |  |  | #9 | 60 | 4.2 | 3.6 | -4.8 | -4.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0.2 | 10 | 0.2 | 0.4 | 30 | 0 | 0 | 0 | 0 | 0 | 0
230116VW | lhfrt | 230116 | GR1203_G | 0.72 | VW | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230108VW | lhfrt | 230108 | GR1204_G | 0.65 | VW | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.2 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
230123VS | lhfrt | 230123 | GR1205_G | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230126VS | lhfrt | 230126 | GR1206_G | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230130VS | lhfrt | 230130 | GR1207_G1 | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230131VS | lhfrt | 230131 | GR1207_G2 | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230134VS | lhfrt | 230134 | GR1208_G | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2301380000 | lhfrt | 230138 | GR1209_G | 0.64 | E4 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2301410000 | lhfrt | 230141 | GR1210_G | 0.48 | E4 | : | [5 empty] | #9 | 60 | 5 | -15 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230144En | lhfrt | 230144 | GR1211_G | 0.48 | En | : | [5 empty] | #9 | 60 | 5 | -15 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2301470000 | lhfrt | 230147 | GR1212_G | 0.48 | E4 | : | [5 empty] | #9 | 60 | 5 | -15 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230157VS | lhfrt | 230157 | GR1214_G1 | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230158VS | lhfrt | 230158 | GR1214_G2 | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230159VS | lhfrt | 230159 | GR1214_G2 | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230163VS | lhfrt | 230163 | GR1208_G1 | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230164VS | lhfrt | 230164 | GR1208_G2 | 0.48 | VS | : | [5 empty] | #11 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230167VE | lhfrt | 230167 | GR1216_G | 0.48 | VE | : | [5 empty] | #9 | 60 | 5 | -15 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230171En | lhfrt | 230171 | GR1217_G1 | 0.48 | En | : | [5 empty] | #9 | 60 | 5 | -15 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230172En | lhfrt | 230172 | GR1217_G2 | 0.48 | En | : | [5 empty] | #9 | 60 | 5 | -15 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230175VE | lhfrt | 230175 | GR1218_G | 0.48 | VE | : | [5 empty] | #9 | 60 | 5 | -15 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221501 | lhfrt | 22150 | EC GEN1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.2 | -3 | -1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 180 | 1 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201871 | lhfrt | 20187 | IV GEN2-U1 | 16 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220741 | lhfrt | 22074 | LRKSPBD1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220751 | lhfrt | 22075 | LRKSPBD2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221531 | lhfrt | 22153 | CALPK ES | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.2 | 1.8 | -1.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2220813 | lhfrt | 22208 | EL CAJON | 69 | 13 | : | [5 empty] | #9 | 60 | -3 | -1.5 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222571 | lhfrt | 22257 | ES GEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223331 | lhfrt | 22333 | GOALLINE GEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223332 | lhfrt | 22333 | GOALLINE GEN | 13.8 | 2 | : | [5 empty] | #9 | 60 | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224501 | lhfrt | 22450 | MIGUEL A | 17.5 | 1 | : | [5 empty] | #9 | 60 | -4.2 | -3 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224511 | lhfrt | 22451 | MIGUEL B | 17.5 | 1 | : | [5 empty] | #9 | 60 | -4.2 | -3 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 10 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224861 | lhfrt | 22486 | MEF MR1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224871 | lhfrt | 22487 | MEF MR2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226171 | lhfrt | 22617 | OY GEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226251 | lhfrt | 22625 | LkHodG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
226261 | lhfrt | 22626 | LkHodG2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
229421 | lhfrt | 22942 | BUE GEN 1 G1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 180 | 30 | 0.04 | 180 | 7.5 | 0.04 | 0 | 0 | 0 | 0 | 0
229451 | lhfrt | 22945 | BUE GEN 1 G2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 180 | 30 | 0.04 | 180 | 7.5 | 0.04 | 0 | 0 | 0 | 0 | 0
229471 | lhfrt | 22947 | BUE GEN 1 G3 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 180 | 30 | 0.04 | 180 | 7.5 | 0.04 | 0 | 0 | 0 | 0 | 0
229811 | lhfrt | 22981 | IV GEN1 STG | 21 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0
229821 | lhfrt | 22982 | IV GEN1 CTG2 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0
229831 | lhfrt | 22983 | IV GEN1 CTG3 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0
232161 | lhfrt | 23216 | ME GEN 1_BS2 | 0.645 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.6 | -0.6 | 0.6 | 1.6 | 2 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
233141 | lhfrt | 23314 | OCO GEN G1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0
233181 | lhfrt | 23318 | OCO GEN G2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -1.6 | -0.5 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0
233201 | lhfrt | 23320 | EC GEN2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234631 | lhfrt | 23463 | DW GEN3 | 0.33 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0
234632 | lhfrt | 23463 | DW GEN3 | 0.33 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0
235411 | lhfrt | 23541 | ME GEN 1_BS1 | 0.645 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.6 | -0.6 | 0.6 | 1.6 | 2 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
236011 | lhfrt | 23601 | TALEGA | 17.5 | 1 | : | [5 empty] | #9 | 60 | -3 | -4.2 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.5 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236042 | lhfrt | 23604 | TALEGA B1 | 17.5 | 2 | : | [5 empty] | #9 | 60 | -3 | -4.2 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.5 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237011 | lhfrt | 23701 | SONGS SC A1 | 17.5 | 1 | : | [5 empty] | #9 | 60 | -3 | -4.2 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.5 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229151 | lhfrt | 22915 | KUMEYAAY | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236271 | lhfrt | 23627 | Q1191_ES | 0.6 | 1 | : | [5 empty] | #9 | 60 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
236281 | lhfrt | 23628 | Q1191_PV | 0.6 | 1 | : | [5 empty] | #9 | 60 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
235851 | lhfrt | 23585 | Q838_GEN | 0.63 | 1 | : | [5 empty] | #9 | 60 | -1.5 | -3 | 0.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 299.2 | 0.01 | 299.2 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2403361 | lhfrt | 240336 | DAWN_BESS | 0.63 | 1 | 29881 | DAWN | 66 | : |  |  | #9 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
2403381 | lhfrt | 240338 | TWILIGHTL_BS | 0.63 | 1 | 29885 | TWILIGHT | 66 | : |  |  | #9 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
296811 | lhfrt | 29681 | NortRsmdG2 | 0.9 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2405591 | lhfrt | 240559 | SILVERSI | 34.5 | 1 | 240558 | SILVERSK | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2404511 | lhfrt | 240451 | WH_STN_5 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2404521 | lhfrt | 240452 | WH_STN_7 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2405941 | lhfrt | 240594 | TOT1005_G_ES | 0.645 | 1 | 240587 | TOT1005_HV | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2404821 | lhfrt | 240482 | MORDOR2_G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.2 | 31 | 181 | 181 | 31 | 7.5 | 0.3 | 0 | 0 | 0
2403671 | lhfrt | 240367 | MORDOR1_G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.2 | 31 | 181 | 181 | 31 | 7.5 | 0.3 | 0 | 0 | 0
248881 | lhfrt | 24888 | SUNRAY2_G | 0.385 | 1 | 24750 | SEGS2 | 115 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 181.82 | 30.82 | 7.79 | 0.79 | 178.22 | 29.22 | 0 | 0 | 0 | 0 | 0
2403871 | lhfrt | 240387 | TOT773_PV1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2403891 | lhfrt | 240389 | TOT773_BS1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2403921 | lhfrt | 240392 | TOT773_PV2 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2403941 | lhfrt | 240394 | TOT773_BS2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2403971 | lhfrt | 240397 | TOT773_PV3 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2403991 | lhfrt | 240399 | TOT773_BS3 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2403611 | lhfrt | 240361 | DAGGET1BESS | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2407031 | lhfrt | 240703 | TOT833_PV | 0.63 | 1 | 240698 | TOT833_S | 230 | : |  |  | #99 | 60 | -0.7 | -2 | -3 | -5 | 0.7 | 2 | 3 | 4 | 0 | 0 | 6550 | 90 | 10 | 0.2 | 6550 | 90 | 5 | 0.2 | 0 | 0 | 0
2407041 | lhfrt | 240704 | TOT833_BS | 0.66 | 1 | 240698 | TOT833_S | 230 | : |  |  | #9 | 60 | -3.5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2404611 | lhfrt | 240461 | WDT1580_PV | 0.55 | 1 | 240465 | WDT1580_H | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | -3 | -2.2 | -1.6 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 0
2404631 | lhfrt | 240463 | WDT1580_ES | 0.6 | 1 | 240465 | WDT1580_H | 66 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | -3 | -2.2 | -1.6 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 0
2404061 | lhfrt | 240406 | WDT1639-ES | 0.69 | 1 | : | [5 empty] | #1 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.16 | 30 | 180 | 0.05 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2405421 | lhfrt | 240542 | WDT1644_PV | 0.55 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.2 | 180 | 180 | 0
2405411 | lhfrt | 240541 | WDT1644_ST | 0.55 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.2 | 180 | 180 | 0
2404091 | lhfrt | 240409 | WDT1650_G | 0.48 | 1 | : | [5 empty] | #1 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.16 | 30 | 180 | 0.05 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2403431 | lhfrt | 240343 | WDT1659_G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 6 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3.4 | 0 | 0 | 0.16 | 0.16 | 31 | 181 | 181 | 31 | 7.5 | 0.16 | 0 | 0 | 0
2406951 | lhfrt | 240695 | WDT1701_G | 0.69 | 1 | 240696 | WDT1701_L | 34.5 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.2 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
240425BS | lhfrt | 240425 | WDT1710_G | 66 | BS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.25 | 0.25 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
2404261 | lhfrt | 240426 | WDT1725_G | 0.385 | 1 | 240429 | WDT1725_H | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2404361 | lhfrt | 240436 | WDT1816-G | 34.5 | 1 | 240434 | WDT1816-H | 66 | : |  |  | #99 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
297201 | lhfrt | 29720 | GARLND_G1 | 0.418 | 1 | 29713 | GARLAND | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.3 | 30 | 180 | 0.3 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
297211 | lhfrt | 29721 | GARLND_G2 | 0.418 | 1 | 29713 | GARLAND | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.3 | 30 | 180 | 0.3 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
298901 | lhfrt | 29890 | GARLND_ST1 | 0.53 | 1 | 29713 | GARLAND | 230 | : |  |  | #9 | 60 | 4 | 3 | 2 | 0.7 | -5 | -3 | -2 | -0.7 | 0 | 0 | 0.2 | 5 | 90 | 6550 | 0.2 | 10 | 90 | 6550 | 0 | 0 | 0
298912 | lhfrt | 29891 | GARLND_ST2 | 0.53 | 2 | 29713 | GARLAND | 230 | : |  |  | #9 | 60 | 4 | 3 | 2 | 0.7 | -5 | -3 | -2 | -0.7 | 0 | 0 | 0.2 | 5 | 90 | 6550 | 0.2 | 10 | 90 | 6550 | 0 | 0 | 0
240711 | lhfrt | 24071 | INLAND | 12.47 | 1 | : | [5 empty] | #9 | 60 | 2.4 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240712 | lhfrt | 24071 | INLAND | 12.47 | 2 | : | [5 empty] | #9 | 60 | 2.4 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29016C1 | lhfrt | 29016 | CHEVGEN 34 | 13.8 | C1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29009D1 | lhfrt | 29009 | CHEVGEN 5 | 13.8 | D1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29016C2 | lhfrt | 29016 | CHEVGEN 34 | 13.8 | C2 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29009D2 | lhfrt | 29009 | CHEVGEN 5 | 13.8 | D2 | : | [5 empty] | #9 | 60 | -3 | -0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.165 | 2 | 0.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252261 | lhfrt | 25226 | ARBWIND_G1 | 0.48 | 1 | : | [5 empty] | #9 | 60 | -0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252251 | lhfrt | 25225 | ARBWIND_G2 | 0.69 | 1 | 25225 | ARBWIND_G2 | 0.69 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400671 | lhfrt | 240067 | COACHELLA_2 | 0.65 | 1 | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257261 | lhfrt | 25726 | VALLECITO | 0.5 | 1 | 25725 | VALLECITO | 16 | 1 | 1 | : | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25434VE | lhfrt | 25434 | RP_JOHANNA_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25380VE | lhfrt | 25380 | RP_LAGUBELL_G_1 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25383VE | lhfrt | 25383 | RP_LAGUBELL_G_2 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25377VE | lhfrt | 25377 | RP_MESA_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25356VE | lhfrt | 25356 | RP_MIRALOMA_G_1 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25359VE | lhfrt | 25359 | RP_MIRALOMA_G_2 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25347VE | lhfrt | 25347 | RP_WALNUT_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25440VE | lhfrt | 25440 | RP_MP_G_1 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25443VE | lhfrt | 25443 | RP_MP_G_2 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25316VE | lhfrt | 25316 | RP_DEVE_BESS_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25449VE | lhfrt | 25449 | RP_VINC_G_1 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25452VE | lhfrt | 25452 | RP_VINC_G_2 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25455VE | lhfrt | 25455 | RP_VINC_G_3 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25446VE | lhfrt | 25446 | RP_ELNIDO_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25437VE | lhfrt | 25437 | RP_ANTELOPE_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25480VE | lhfrt | 25480 | RP_WH_G_1 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25483VE | lhfrt | 25483 | RP_WH_G_2 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25487VE | lhfrt | 25487 | RP_MOHAVE_G_1 | 0.39 | VE | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 0.1 | 181 | 31 | 7.6 | 0.76 | 0.1 | 0 | 0 | 0
25491VE | lhfrt | 25491 | RP_MOHAVE_G_2 | 0.39 | VE | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 0.1 | 181 | 31 | 7.6 | 0.76 | 0.1 | 0 | 0 | 0
25477VE | lhfrt | 25477 | RP_WW_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240239VE | lhfrt | 240239 | RP_KRAMER_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240236VE | lhfrt | 240236 | RP_CALCITE_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240242VE | lhfrt | 240242 | RP_COLWTR_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240279VE | lhfrt | 240279 | RP_ROADWAY_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240221VE | lhfrt | 240221 | RP_WHRLWD_LDES_G_1 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240224VE | lhfrt | 240224 | RP_WHRLWD_LDES_G_2 | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240282VE | lhfrt | 240282 | RP_MANDALY_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25540VE | lhfrt | 25540 | RP_ELDORDO_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25505VE | lhfrt | 25505 | RP_COLRVR_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
240615VE | lhfrt | 240615 | RP_RB_3G | 0.39 | VE | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 0.1 | 181 | 31 | 7.6 | 0.76 | 0.1 | 0 | 0 | 0
25502VE | lhfrt | 25502 | RP_CENTER_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25543VE | lhfrt | 25543 | RP_HINSON_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25468VE | lhfrt | 25468 | RP_LITEHIPE_g | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25546VE | lhfrt | 25546 | RP_KRAMER_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25471VE | lhfrt | 25471 | RP_PISGAH_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25474VE | lhfrt | 25474 | RP_VICTOR_G | 0.66 | VE | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.2 | 30 | 180 | 0.2 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
25310VS | lhfrt | 25310 | RP_DEVE_PV1_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25313VS | lhfrt | 25313 | RP_DEVE_PV2_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25348VS | lhfrt | 25348 | RP_ANT_PV_G_1 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25351VS | lhfrt | 25351 | RP_ANT_PV_G_2 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25384VS | lhfrt | 25384 | RP_WW_PV_G_1 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25387VS | lhfrt | 25387 | RP_WW_PV_G_2 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25363VS | lhfrt | 25363 | RP_VIN_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25366VS | lhfrt | 25366 | RP_VIN_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25369VS | lhfrt | 25369 | RP_VIN_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25372VS | lhfrt | 25372 | RP_VIN_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25360VS | lhfrt | 25360 | RP_VESTAL_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25390VS | lhfrt | 25390 | RP_WH_PV_G_1 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25393VS | lhfrt | 25393 | RP_WH_PV_G_2 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25396VS | lhfrt | 25396 | RP_WH_PV_G_3 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25459VS | lhfrt | 25459 | RP_WH_1G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25462VS | lhfrt | 25462 | RP_WH_2G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25465VS | lhfrt | 25465 | RP_WH_3G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240269VS | lhfrt | 240269 | RP_COLWTR_PV_G_1 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240272VS | lhfrt | 240272 | RP_COLWTR_PV_G_2 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240618VS | lhfrt | 240618 | RP_ROADW_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240230VS | lhfrt | 240230 | RP_CALCITE_PV_G_1 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240233VS | lhfrt | 240233 | RP_CALCITE_PV_G_2 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240245VS | lhfrt | 240245 | RP_KRAMER_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240631VS | lhfrt | 240631 | RP_MOHV_1G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240634VS | lhfrt | 240634 | RP_MOHV_2G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240637VS | lhfrt | 240637 | RP_MOHV_3G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240275VS | lhfrt | 240275 | RP_KRAMR_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25556VS | lhfrt | 25556 | RP_CR_1G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25559VS | lhfrt | 25559 | RP_CR_2G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25562VS | lhfrt | 25562 | RP_CR_3G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25575VS | lhfrt | 25575 | RP_RDBLF_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240608VS | lhfrt | 240608 | RP_RB_1G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240611VS | lhfrt | 240611 | RP_RB_2G | 0.39 | VS | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25549VS | lhfrt | 25549 | RP_LTHIPE_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240676VS | lhfrt | 240676 | RP_KRAMR_PV_G2 | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25572VS | lhfrt | 25572 | RP_PSGH_PV_G | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240227VS | lhfrt | 240227 | RP_VCTR_PV_PV | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
25552VS | lhfrt | 25552 | RP_VCTR_PV_DG | 0.38 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
240248VW | lhfrt | 240248 | RP-DEVERS-WND_1 | 0.69 | VW | 240246 | RP_DEVERS_WIND_1 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
240251VW | lhfrt | 240251 | RP_DEVERS_WND_2 | 0.69 | VW | 240249 | RP_DEVERS_WIND_2 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
240254VW | lhfrt | 240254 | RP_DEVERS_WND_3 | 0.69 | VW | 240252 | RP_DEVERS_WIND_3 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
240257VW | lhfrt | 240257 | RP_DEVERS_WND_4 | 0.69 | VW | 240255 | RP_DEVERS_WIND_4 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25494VW | lhfrt | 25494 | RP_CALCITE_WIND_1 | 0.69 | VW | 25492 | RP_CALCITE_WIND_1 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25497VW | lhfrt | 25497 | RP_CALCITE_WIND_2 | 0.69 | VW | 25495 | RP_CALCITE_WIND_2 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
240260VW | lhfrt | 240260 | RP_COLWTR_WND_G_1 | 0.69 | VW | 240258 | RP_COLWTR_WND_H_1 | 115 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
240263VW | lhfrt | 240263 | RP_COLWTR_WND_G_2 | 0.69 | VW | 240261 | RP_COLWTR_WND_H_2 | 115 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
240266VW | lhfrt | 240266 | RP_COLWTR_WND_G_3 | 0.69 | VW | 240264 | RP_COLWTR_WND_H_3 | 115 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25322VW | lhfrt | 25322 | RP_ANTELOPE_WIND_1 | 0.69 | VW | 25320 | RP_ANTELOPE_WIND_1 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25325VW | lhfrt | 25325 | RP_ANTELOPE_WIND_2 | 0.69 | VW | 25323 | RP_ANTELOPE_WIND_2 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25332VW | lhfrt | 25332 | RP_WW_WIND_1 | 0.69 | VW | 25330 | RP_WW_WIND_1 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25335VW | lhfrt | 25335 | RP_WW_WIND_2 | 0.69 | VW | 25333 | RP_WW_WIND_2 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25338VW | lhfrt | 25338 | RP_WW_WIND_3 | 0.69 | VW | 25336 | RP_WW_WIND_3 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25341VW | lhfrt | 25341 | RP_WH_WIND_1 | 0.69 | VW | 25339 | RP_WH_WIND_1 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
25344VW | lhfrt | 25344 | RP_WH_WIND_2 | 0.69 | VW | 25342 | RP_WH_WIND_2 | 230 | : |  |  | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.15 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0.008334 | 0.008334 | 0
251061 | lhfrt | 25106 | CMS1_G | 0.301 | 1 | 25103 | CMS1_HS | 230 | : |  |  | #9 | 60 | 1.2 | -1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251131 | lhfrt | 25113 | CMS2_G | 0.324 | 1 | 25108 | CM2 HS | 230 | : |  |  | #9 | 60 | 1.7 | -3 | 0.6 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.16 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251191 | lhfrt | 25119 | CMS4_G | 0.385 | 1 | 25116 | CMS4 HS | 230 | : |  |  | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25099G1 | lhfrt | 25099 | DSEC CT1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | 3.01 | 1.81 | -2.5 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 10 | 10 | 0.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25102G2 | lhfrt | 25102 | DSEC CT2 | 13.8 | G2 | : | [5 empty] | #9 | 60 | 3.01 | 1.81 | -2.5 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 10 | 10 | 0.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25101ST | lhfrt | 25101 | DSEC ST | 16 | ST | : | [5 empty] | #9 | 60 | 3.01 | 1.81 | -2.5 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 10 | 10 | 0.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2410131 | lhfrt | 241013 | TOT907_G | 0.6 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
2404451 | lhfrt | 240445 | TOT927_G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
291771 | lhfrt | 29177 | TOT777AVEP_B | 0.95 | 1 | 29676 | RATTLSNK | 230 | : |  |  | #9 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
297631 | lhfrt | 29763 | TOT726_G | 34.5 | 1 | 29357 | TOT726_TMBLE | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
297641 | lhfrt | 29764 | TOT778_G | 34.5 | 1 | 29357 | TOT726_TMBLE | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
293601 | lhfrt | 29360 | TOT793C_BESS | 34.5 | 1 | 29670 | DSTFLWER | 230 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293631 | lhfrt | 29363 | TOT793WS3_BE | 34.5 | 1 | 29670 | DSTFLWER | 230 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293541 | lhfrt | 29354 | TOT793C_PV | 0.63 | 1 | 29670 | DSTFLWER | 230 | : |  |  | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293621 | lhfrt | 29362 | TOT793WS3_PV | 0.63 | 1 | 29670 | DSTFLWER | 230 | : |  |  | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29709EQ | lhfrt | 29709 | SGS_AVG1 | 0.385 | EQ | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | 0.7 | -0.7 | -2 | -3 | -4 | 0 | 0 | 2 | 40 | 200 | 1000 | 1000 | 200 | 40 | 5 | 0 | 0 | 0
29710EQ | lhfrt | 29710 | SGS_AVG2 | 0.385 | EQ | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | 0.7 | -0.7 | -2 | -3 | -4 | 0 | 0 | 2 | 40 | 200 | 1000 | 1000 | 200 | 40 | 5 | 0 | 0 | 0
2402141 | lhfrt | 240214 | MENIFEE_G1 | 0.66 | 1 | 240205 | ROMOLA | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2402152 | lhfrt | 240215 | MENIFEE_G2 | 0.66 | 2 | 240205 | ROMOLA | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2402163 | lhfrt | 240216 | MENIFEE_G3 | 0.66 | 3 | 240205 | ROMOLA | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2402174 | lhfrt | 240217 | MENIFEE_G4 | 0.66 | 4 | 240205 | ROMOLA | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2402185 | lhfrt | 240218 | MENIFEE_G5 | 0.66 | 5 | 240205 | ROMOLA | 500 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400921 | lhfrt | 240092 | TOT959_G | 0.69 | 1 | 240089 | TOT959_H | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.08 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
2402881 | lhfrt | 240288 | WDT1558_G | 0.55 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 1.6 | 0.6 | -3 | -1.6 | -2.7 | -2.2 | -1.6 | 1.7 | 0 | 180 | 30 | 180 | 0.75 | 30 | 7.5 | 30 | 180 | 0.16 | 0 | 0
2401691 | lhfrt | 240169 | WDT1648_G | 0.38 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0.008334 | 0.008334 | 0
2403151 | lhfrt | 240315 | WDT1652_G | 0.6 | 1 | 240313 | WDT1652_H | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2403191 | lhfrt | 240319 | WDT1702_G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2403351 | lhfrt | 240335 | WDT1641_G | 0.6 | 1 | 240333 | WDT1641_H | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2402011 | lhfrt | 240201 | SOLCAT_G_PV1 | 0.63 | 1 | 29140 | VICTORY_PASS | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2402042 | lhfrt | 240204 | SOLCAT_I_ES | 34.5 | 2 | 29140 | VICTORY_PASS | 230 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2402033 | lhfrt | 240203 | SOLCAT_G_PV2 | 0.63 | 3 | 29140 | VICTORY_PASS | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2401951 | lhfrt | 240195 | SLOTH_G_PV | 0.63 | 1 | 29140 | VICTORY_PASS | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2401962 | lhfrt | 240196 | SLOTH_I_ES | 34.5 | 2 | 29140 | VICTORY_PASS | 230 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291461 | lhfrt | 29146 | VIC_PS_PV | 0.63 | 1 | 29140 | VICTORY_PASS | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
291472 | lhfrt | 29147 | VIC_PS_ES | 34.5 | 2 | 29140 | VICTORY_PASS | 230 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255241 | lhfrt | 25524 | ALMITOS B2_G | 0.75 | 1 | 25529 | ALMITOS_ES | 230 | : |  |  | #9 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 600 | 600 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248991 | lhfrt | 24899 | WDT1510G | 0.69 | 1 | 24345 | SIMPSON | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.66 | -3 | -2.7 | -2.2 | -1.6 | -0.66 | 0 | 0 | 0.5 | 30 | 180 | 0.5 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2404181 | lhfrt | 240418 | WDT1532_G | 0.48 | 1 | 240416 | SALLY | 66 | : |  |  | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.2 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
240346EQ | lhfrt | 240346 | WDT1635_G | 0.6 | EQ | 240346 | WDT1635_G | 0.6 | : |  |  | #9 | 60 | 5 | 3 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240349EQ | lhfrt | 240349 | WDT1636_G | 0.6 | EQ | 240349 | WDT1636_G | 0.6 | : |  |  | #9 | 60 | 5 | 3 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.16 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2404331 | lhfrt | 240433 | WDT1649_G | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2403541 | lhfrt | 240354 | WDT1669_G | 0.6 | 1 | 240352 | WDT1669_H | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2404691 | lhfrt | 240469 | WDT1711_G | 0.385 | 1 | 240466 | WDT1711_H | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2404731 | lhfrt | 240473 | WDT1719_G | 0.385 | 1 | 240470 | WDT1719_H | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2404741 | lhfrt | 240474 | WDT1583 | 12.47 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1667 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
2400861 | lhfrt | 240086 | TOT806_PV | 0.52 | 1 | 29665 | TEDDY | 230 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 180 | 30 | 0.2 | 180 | 30 | 7.5 | 0.75 | 0.2 | 0 | 0 | 0
2400882 | lhfrt | 240088 | TOT806_BESS | 0.48 | 2 | 29665 | TEDDY | 230 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.2 | 180 | 30 | 0.16 | 0 | 0 | 0
2400191 | lhfrt | 240019 | RAMPA_G | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299311 | lhfrt | 29931 | TOT892_G1_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299331 | lhfrt | 29933 | TOT892_G1_ST | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.2 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
299371 | lhfrt | 29937 | TOT892_G2_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299391 | lhfrt | 29939 | TOT892_G2_ST | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.2 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
299431 | lhfrt | 29943 | TOT892_G3_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299451 | lhfrt | 29945 | TOT892_G3_ST | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.2 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
259591 | lhfrt | 25959 | TOT896_G1PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259611 | lhfrt | 25961 | TOT896_G1ST | 0.69 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259651 | lhfrt | 25965 | TOT896_G2PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259671 | lhfrt | 25967 | TOT896_G2ST | 0.69 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298271 | lhfrt | 29827 | WDT1454_EQ_G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.2 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
250691 | lhfrt | 25069 | WDT1490_PV | 0.36 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.16 | 30 | 180 | 0.16 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
298361 | lhfrt | 29836 | WDT1384_G | 0.63 | 1 | 24152 | VESTAL | 66 | : |  |  | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290861 | lhfrt | 29086 | CALGREN_PIX | 12.47 | 1 | : | [5 empty] | #9 | 60 | 6 | 3 | 3 | -6 | -3 | -3 | 0 | 0 | 0 | 0 | 2 | 2 | 5 | 2 | 2 | 5 | 0 | 0 | 0 | 0 | 0
290862 | lhfrt | 29086 | CALGREN_PIX | 12.47 | 2 | : | [5 empty] | #9 | 60 | 6 | 3 | 3 | -6 | -3 | -3 | 0 | 0 | 0 | 0 | 2 | 2 | 5 | 2 | 2 | 5 | 0 | 0 | 0 | 0 | 0
257351 | lhfrt | 25735 | ARLNGTN_G1B1 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257411 | lhfrt | 25741 | ARLNGTN_G1B2 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257401 | lhfrt | 25740 | ARLNGTN_G2B1 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257341 | lhfrt | 25734 | ARLNGTN_G1PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257391 | lhfrt | 25739 | ARLNGTN_G2PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257421 | lhfrt | 25742 | ARLNGTN_G2B2 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241481 | lhfrt | 24148 | TENNGEN1 | 12.47 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241491 | lhfrt | 24149 | TENNGEN2 | 12.47 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24026D1 | lhfrt | 24026 | CIMGENCT | 12.47 | D1 | : | [5 empty] | #9 | 60 | 1.9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24026D2 | lhfrt | 24026 | CIMGENST | 12.47 | D2 | : | [5 empty] | #9 | 60 | 1.9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290333 | lhfrt | 29033 | SUN_PVPAD3 | 13.8 | 3 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290344 | lhfrt | 29034 | SUN_PVPAD4 | 13.8 | 4 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290355 | lhfrt | 29035 | SUN_PVPAD5 | 13.8 | 5 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247541 | lhfrt | 24754 | SUN_MV3 | 13.8 | 1 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247551 | lhfrt | 24755 | SUN_MV4 | 13.8 | 1 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247561 | lhfrt | 24756 | SUN_MV5 | 13.8 | 1 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292386 | lhfrt | 29238 | SUN_PVPAD6 | 13.8 | 6 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292397 | lhfrt | 29239 | SUN_PVPAD7 | 13.8 | 7 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247571 | lhfrt | 24757 | SUN_MV6 | 13.8 | 1 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247581 | lhfrt | 24758 | SUN_MV7 | 13.8 | 1 | 24753 | SUNGEN | 115 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252311 | lhfrt | 25231 | MARVEL_ES1 | 34.5 | 1 | 25227 | MARVEL | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252351 | lhfrt | 25235 | MARVEL_ES2 | 34.5 | 1 | 25227 | MARVEL | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252391 | lhfrt | 25239 | MARVEL_ES3 | 34.5 | 1 | 25227 | MARVEL | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400561 | lhfrt | 240056 | LCKHRT1_PV1 | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400571 | lhfrt | 240057 | LCKHRT1_PV2 | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400541 | lhfrt | 240054 | LCKHRT1_BMS | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400551 | lhfrt | 240055 | LCKHRT1_IFS | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400581 | lhfrt | 240058 | LCKHRT2_PV | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400591 | lhfrt | 240059 | LCKHRT2_BMS | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400601 | lhfrt | 240060 | LCKHRT2_IFS | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400661 | lhfrt | 240066 | TOT989_PV | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400651 | lhfrt | 240065 | TOT989_BMS | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
2400641 | lhfrt | 240064 | TOT989_IFS | 34.5 | 1 | 240050 | LOCKHART_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
257661 | lhfrt | 25766 | DS3PVA | 34.5 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 6550 | 90 | 0.2 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
257671 | lhfrt | 25767 | DS3BTA | 34.5 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 6550 | 90 | 0.2 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
257701 | lhfrt | 25770 | DS3PVCD | 34.5 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 6550 | 90 | 0.2 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
257711 | lhfrt | 25771 | DS3BTCD | 34.5 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 6550 | 90 | 0.2 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
257721 | lhfrt | 25772 | DS3PVE | 34.5 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 6550 | 90 | 0.2 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
257731 | lhfrt | 25773 | DS3BTE | 34.5 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 6550 | 90 | 0.2 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
257681 | lhfrt | 25768 | DS3PVB | 34.5 | 1 | : | [5 empty] | #1 | 60 | -2 | -3.5 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 300 | 6 | 0.1 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
257691 | lhfrt | 25769 | DS3BTB | 34.5 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 6550 | 90 | 0.2 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
2400761 | lhfrt | 240076 | DS2_PPA6_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.16 | 0.16 | 6550 | 90 | 5 | 0.16 | 0.16 | 0
2400771 | lhfrt | 240077 | DS2_PPA7_ES | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.16 | 0.16 | 6550 | 90 | 5 | 0.16 | 0.16 | 0
2400781 | lhfrt | 240078 | DS2_PPA7_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.16 | 0.16 | 6550 | 90 | 5 | 0.16 | 0.16 | 0
2400791 | lhfrt | 240079 | DS2_PPA8_ES | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.16 | 0.16 | 6550 | 90 | 5 | 0.16 | 0.16 | 0
2400801 | lhfrt | 240080 | DS2_PPA6_ES | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.16 | 0.16 | 6550 | 90 | 5 | 0.16 | 0.16 | 0
2400811 | lhfrt | 240081 | DS2_PPA8_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.16 | 0.16 | 6550 | 90 | 5 | 0.16 | 0.16 | 0
2400251 | lhfrt | 240025 | OBERON_PV1G | 0.63 | 1 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400322 | lhfrt | 240032 | OBERON_PV2G | 0.63 | 2 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400395 | lhfrt | 240039 | OBERON_PV3G | 0.63 | 5 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400466 | lhfrt | 240046 | OBERON_PV4G | 0.63 | 6 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400273 | lhfrt | 240027 | OBERON_ES1G | 0.48 | 3 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400344 | lhfrt | 240034 | OBERON_ES2G | 0.48 | 4 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400417 | lhfrt | 240041 | OBERON_ES3G | 0.48 | 7 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400488 | lhfrt | 240048 | OBERON_ES4G | 0.48 | 8 | 240020 | OBERON | 500 | : |  |  | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0.2 | 34.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292671 | lhfrt | 29267 | BLDMSA_1 | 0.91 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292682 | lhfrt | 29268 | BLDMSA_2 | 0.91 | 2 | : | [5 empty] | #1 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 600 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292693 | lhfrt | 29269 | BLDMSA_3 | 0.69 | 3 | : | [5 empty] | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25729EQ | lhfrt | 25729 | JOHANNA_PRP | 66 | EQ | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400111 | lhfrt | 240011 | ANODE_G1 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400142 | lhfrt | 240014 | ANODE_G2 | 34.5 | 2 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400021 | lhfrt | 240002 | CATHODE1_G | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2400042 | lhfrt | 240004 | CATHODE2_G | 34.5 | 2 | : | [5 empty] | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297541 | lhfrt | 29754 | TOT727_G2 | 0.645 | 1 | 29746 | GASKEL_WEST | 230 | 1 | 1 | : | #9 | 60 | 2.5 | 1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 30 | 10 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298011 | lhfrt | 29801 | TOT727_G3 | 0.645 | 1 | 29746 | GASKEL_WEST | 230 | 1 | 1 | : | #9 | 60 | 2.5 | 1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 30 | 10 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298051 | lhfrt | 29805 | TOT727_G4 | 0.645 | 1 | 29746 | GASKEL_WEST | 230 | 1 | 1 | : | #9 | 60 | 2.5 | 1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 30 | 10 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298071 | lhfrt | 29807 | TOT727_G5 | 0.645 | 1 | 29746 | GASKEL_WEST | 230 | 1 | 1 | : | #9 | 60 | 2.5 | 1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 30 | 10 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298121 | lhfrt | 29812 | TOT727G1B | 0.6 | 1 | 29746 | GASKEL_WEST | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
298091 | lhfrt | 29809 | TOT727G2B | 0.6 | 1 | 29746 | GASKEL_WEST | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
298101 | lhfrt | 29810 | TOT727G3B | 0.6 | 1 | 29746 | GASKEL_WEST | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
298453 | lhfrt | 29845 | SGS_AVBESS3 | 0.48 | 3 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.2 | 180 | 30 | 0.16 | 0 | 0 | 0
298474 | lhfrt | 29847 | SGS_AVBESS45 | 0.48 | 4 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.2 | 180 | 30 | 0.16 | 0 | 0 | 0
297921 | lhfrt | 29792 | ANTLP2_P6A_G | 0.69 | 1 | 29698 | BIG SKY | 230 | : |  |  | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
297671 | lhfrt | 29767 | ANT2_LAB_G | 0.69 | 1 | 29698 | BIG SKY | 230 | : |  |  | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297821 | lhfrt | 29782 | ANTLP2_P10G1 | 0.63 | 1 | 29559 | POLARIS | 230 | : |  |  | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
295652 | lhfrt | 29565 | ANTLP2_P10G2 | 0.69 | 2 | 29559 | POLARIS | 230 | : |  |  | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
295632 | lhfrt | 29563 | ANTLP2_P9_G2 | 0.69 | 2 | 29559 | POLARIS | 230 | : |  |  | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
295611 | lhfrt | 29561 | ANTLP2_P9_G1 | 0.63 | 1 | 29559 | POLARIS | 230 | : |  |  | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
295662 | lhfrt | 29566 | ANTLP2_P1BG2 | 0.69 | 2 | 29795 | NORTH BIGSKY | 230 | : |  |  | #9 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.16 | 21 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
1890641 | lhfrt | 189064 | SunSh_Val_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.7 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1890601 | lhfrt | 189060 | SunSh_Val_ES | 0.52 | 1 | 189068 | T2 | 138 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
291361 | lhfrt | 29136 | TOT872_PV | 0.63 | 1 | 29125 | FILIPPI | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
291372 | lhfrt | 29137 | TOT872_ES | 0.69 | 2 | 29125 | FILIPPI | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
291291 | lhfrt | 29129 | TOT749_PV | 0.63 | 1 | 29125 | FILIPPI | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
291302 | lhfrt | 29130 | TOT749_ES | 0.69 | 2 | 29125 | FILIPPI | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
292941 | lhfrt | 29294 | SBPH1_ST | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
292951 | lhfrt | 29295 | SBPH2_ST | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
292991 | lhfrt | 29299 | SBPH6_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
293971 | lhfrt | 29397 | SBPH6_BMS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
298531 | lhfrt | 29853 | SBPH6_IFS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
293001 | lhfrt | 29300 | SBPH7_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
298491 | lhfrt | 29849 | SBPH7_BMS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
298541 | lhfrt | 29854 | SBPH7_IFS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
293011 | lhfrt | 29301 | SBPH8_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
298501 | lhfrt | 29850 | SBPH8_BMS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
298551 | lhfrt | 29855 | SBPH8_IFS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
292961 | lhfrt | 29296 | EDPH3_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
293941 | lhfrt | 29394 | EDPH3_BMS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
298511 | lhfrt | 29851 | EDPH3_IFS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
292971 | lhfrt | 29297 | EDPH4_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
293951 | lhfrt | 29395 | EDPH4_BMS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
298521 | lhfrt | 29852 | EDPH4_IFS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
292981 | lhfrt | 29298 | EDPH5_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
293961 | lhfrt | 29396 | EDPH5_BMS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
251351 | lhfrt | 25135 | BLYTHMS_PV1G | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.7 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
251401 | lhfrt | 25140 | BLYTHMS_PV2G | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.7 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
290791 | lhfrt | 29079 | BLYTHMS_ES1G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.7 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
290811 | lhfrt | 29081 | BLYTHMS_ES2G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.7 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
248781 | lhfrt | 24878 | CSA DIAB 4 | 12.47 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
256001 | lhfrt | 25600 | PBLOSM_GEN | 0.385 | 1 | 25597 | PBLOSM_TAP | 230 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
297751 | lhfrt | 29775 | ANT2_EXP1B_G | 0.66 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0.16 | 350 | 650 | 0.16 | 650 | 0 | 0 | 0 | 0 | 0 | 0
297741 | lhfrt | 29774 | ANT2_EXP3A_G | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295691 | lhfrt | 29569 | ANT2_EXP3B_G | 0.66 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0.16 | 350 | 650 | 650 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0
256631 | lhfrt | 25663 | SNTANSG1 | 0.55 | 1 | 25661 | SNTANSTP | 66 | : |  |  | #9 | 60 | 1.75 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 1.01 | 30.11 | 180.11 | 180.11 | 30.11 | 7.51 | 0.85 | 0.21 | 99999 | 99999 | 0
2402892 | lhfrt | 240289 | SNTANSG2 | 0.48 | 2 | 25661 | SNTANSTP | 66 | : |  |  | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.11 | 0.21 | 31 | 181 | 181 | 31 | 7.5 | 0.21 | 0 | 0 | 0
2402921 | lhfrt | 240292 | SNTANSG3 | 0.48 | 1 | 240290 | SNTANST2 | 13.8 | : |  |  | #9 | 60 | 3 | 1.2 | -1.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 300 | 300 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2402954 | lhfrt | 240295 | SNTANSG4 | 0.48 | 4 | 25661 | SNTANSTP | 66 | : |  |  | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.11 | 0.21 | 31 | 181 | 181 | 31 | 7.5 | 0.21 | 0 | 0 | 0
240299EQ | lhfrt | 240299 | PW2_WD1_G | 0.65 | EQ | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240302EQ | lhfrt | 240302 | PW2_WD2_G | 0.65 | EQ | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298241 | lhfrt | 29824 | SATICOY_BESS | 0.505 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0 | 0 | 0 | 0
293711 | lhfrt | 29371 | TOT753_PV | 0.38 | 1 | 29371 | TOT753_PV | 0.38 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 180 | 30 | 0.2 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
293721 | lhfrt | 29372 | TOT753_BESS | 0.48 | 1 | 29372 | TOT753_BESS | 0.48 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0.16 | 0 | 0 | 0
293791 | lhfrt | 29379 | TOT754_PV | 0.385 | 1 | 29379 | TOT754_PV | 0.385 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 180 | 30 | 0.2 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
293801 | lhfrt | 29380 | TOT754_BESS | 0.48 | 1 | 29380 | TOT754_BESS | 0.48 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0.2 | 0 | 0 | 0
259451 | lhfrt | 25945 | TOT904_PV1 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259471 | lhfrt | 25947 | TOT904_ES1 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259521 | lhfrt | 25952 | TOT904_PV2 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259541 | lhfrt | 25954 | TOT904_ES2 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
292811 | lhfrt | 29281 | CRMSN_PV1G | 0.63 | 1 | 29270 | CRIMSON | 230 | : |  |  | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 5000 | 0.2 | 650 | 5000 | 0 | 0 | 0 | 0
292831 | lhfrt | 29283 | CRMSN_PV2G | 0.63 | 1 | 29270 | CRIMSON | 230 | : |  |  | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 5000 | 0.2 | 650 | 5000 | 0.008334 | 0 | 0 | 0
290871 | lhfrt | 29087 | CRMSN_ESG1 | 0.66 | 1 | 29270 | CRIMSON | 230 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290882 | lhfrt | 29088 | CRMSN_ESG2 | 0.66 | 2 | 29270 | CRIMSON | 230 | : |  |  | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291701 | lhfrt | 29170 | RABTBRSH_1PV | 0.63 | 1 | 29676 | RATTLSNK | 230 | : |  |  | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0
293661 | lhfrt | 29366 | RABTBRSH_2PV | 0.63 | 1 | 29676 | RATTLSNK | 230 | : |  |  | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0
291681 | lhfrt | 29168 | RABTBRSH_1B1 | 0.434 | 1 | 29676 | RATTLSNK | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.08 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.08 | 0 | 0 | 0
293651 | lhfrt | 29365 | RABTBRSH_2B | 0.434 | 1 | 29676 | RATTLSNK | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.08 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.08 | 0 | 0 | 0
293671 | lhfrt | 29367 | RABTBRSH_1B2 | 0.434 | 1 | 29676 | RATTLSNK | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.08 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.08 | 0 | 0 | 0
257771 | lhfrt | 25777 | TOT811BG | 0.48 | 1 | 25769 | TOT811H | 230 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 1 | 180 | 30 | 7.5 | 0.75 | 1 | 0 | 0 | 0
293451 | lhfrt | 29345 | TOT833_B1 | 0.55 | 1 | 29337 | TOT833_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.01 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.01 | 0 | 0 | 0
293461 | lhfrt | 29346 | TOT833_B2 | 0.55 | 1 | 29337 | TOT833_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.01 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.01 | 0 | 0 | 0
293431 | lhfrt | 29343 | TOT833_PV1 | 0.55 | 1 | 29337 | TOT833_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.01 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.01 | 0 | 0 | 0
293441 | lhfrt | 29344 | TOT833_PV2 | 0.55 | 1 | 29337 | TOT833_S | 230 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.01 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.01 | 0 | 0 | 0
25518G1 | lhfrt | 25518 | TOT6401G | 0.38 | G1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.008334 | 180 | 30 | 7.5 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
25519G2 | lhfrt | 25519 | TOT6402G | 0.38 | G2 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.008334 | 180 | 30 | 7.5 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
259041 | lhfrt | 25904 | TOT909_PV1 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259061 | lhfrt | 25906 | TOT909_ST1 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259101 | lhfrt | 25910 | TOT909_PV2 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259121 | lhfrt | 25912 | TOT909_ST2 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259161 | lhfrt | 25916 | TOT909_PV3 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259181 | lhfrt | 25918 | TOT909_ST3 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259221 | lhfrt | 25922 | TOT909_PV4 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259241 | lhfrt | 25924 | TOT909_ST4 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259281 | lhfrt | 25928 | TOT909_PV5 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
259301 | lhfrt | 25930 | TOT909_ST5 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 181 | 31 | 1 | 181 | 31 | 7.6 | 0.76 | 1 | 0 | 0 | 0
299581 | lhfrt | 29958 | TOT876_P1_G | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
299591 | lhfrt | 29959 | TOT876_P3_G | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
299601 | lhfrt | 29960 | TOT876_P4_PV | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
2401781 | lhfrt | 240178 | TOT876_4_BMS | 0.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
2401791 | lhfrt | 240179 | TOT876_4_IMS | 0.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
299611 | lhfrt | 29961 | TOT876_P5_G | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
299621 | lhfrt | 29962 | TOT876_P6_G | 34.5 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
299261 | lhfrt | 29926 | SEPV_PE_G | 0.8 | 1 | 29923 | SPARKLE | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 9999 | 7.5 | 30 | 180 | 9999 | 0 | 0 | 0 | 0
293841 | lhfrt | 29384 | MVTOT823_P1 | 34.5 | 1 | 29382 | BIG_BEAU | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.15 | 0.15 | 6550 | 90 | 5 | 0.25 | 0.25 | 0
293851 | lhfrt | 29385 | TOT823_P2 | 34.5 | 1 | 29382 | BIG_BEAU | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.5 | 0.5 | 6550 | 90 | 5 | 0.25 | 0.25 | 0
293881 | lhfrt | 29388 | TOT455_P4 | 34.5 | 1 | 29382 | BIG_BEAU | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.15 | 0.15 | 6550 | 90 | 5 | 0.25 | 0.25 | 0
249981 | lhfrt | 24998 | COSO_ES_G1 | 0.69 | 1 | 24998 | COSO_ES_G1 | 0.69 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
257781 | lhfrt | 25778 | BLACK_CRK B1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257791 | lhfrt | 25779 | BLACK_CRK B2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249821 | lhfrt | 24982 | DRACKER_G1 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 1 | 2 | -1.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0.1 | 200 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249852 | lhfrt | 24985 | DRACKER_G2 | 0.55 | 2 | : | [5 empty] | #9 | 60 | 1 | 2 | -1.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0.1 | 200 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251571 | lhfrt | 25157 | DRACKER_B1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251602 | lhfrt | 25160 | DRACKER_B2 | 0.645 | 2 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251613 | lhfrt | 25161 | DRACKER_B3 | 0.69 | 3 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251433 | lhfrt | 25143 | DRACKER_G3 | 0.615 | 3 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251444 | lhfrt | 25144 | DRACKER_G4 | 0.615 | 4 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251631 | lhfrt | 25163 | DRACKER_B41 | 0.645 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242761 | lhfrt | 24276 | SKYRIVER_G1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241721 | lhfrt | 24172 | SKYRIVER_G2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1891201 | lhfrt | 189120 | Q1341_PV | 0.66 | 1 | 189115 | Q1341_HV2 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1891211 | lhfrt | 189121 | Q1341_ES | 0.69 | 1 | 189115 | Q1341_HV2 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252451 | lhfrt | 25245 | ALMASOL_G1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | 0.7 | -0.7 | -2 | -2.3 | 0 | 0 | 0 | 0.01 | 5 | 200 | 6550 | 6550 | 200 | 10 | 0 | 0 | 0 | 0
252501 | lhfrt | 25250 | ALMASOL_G4 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | 0.7 | -0.7 | -2 | -2.3 | 0 | 0 | 0 | 0.01 | 5 | 200 | 6550 | 6550 | 200 | 10 | 0 | 0 | 0 | 0
252621 | lhfrt | 25262 | ALMASOL_G7PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.15 | 60 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252621 | lhfrt | 25262 | ALMASOL_G7PV | 0.63 | 1 | 25260 | ALMASOL_MV7 | 34.5 | : |  |  | #9 | 60 | 4 | 3.8 | 3.6 | -4.5 | -4.3 | -4.1 | 0 | 0 | 0 | 0 | 1.1 | 30 | 180 | 1.1 | 30 | 180 | 0 | 0 | 0 | 0 | 0
252551 | lhfrt | 25255 | ALMASOL_G6PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.15 | 60 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252551 | lhfrt | 25255 | ALMASOL_G6PV | 0.63 | 1 | 25253 | ALMASOL_MV6 | 34.5 | : |  |  | #9 | 60 | 4 | 3.8 | 3.6 | -4.5 | -4.3 | -4.1 | 0 | 0 | 0 | 0 | 1.1 | 30 | 180 | 1.1 | 30 | 180 | 0 | 0 | 0 | 0 | 0
252572 | lhfrt | 25257 | ALMASOL_G6ES | 0.69 | 2 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.15 | 60 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252572 | lhfrt | 25257 | ALMASOL_G6ES | 0.69 | 2 | 25253 | ALMASOL_MV6 | 34.5 | : |  |  | #9 | 60 | 4 | 3.8 | 3.6 | -4.5 | -4.3 | -4.1 | 0 | 0 | 0 | 0 | 1.1 | 30 | 180 | 1.1 | 30 | 180 | 0 | 0 | 0 | 0 | 0
255951 | lhfrt | 25595 | HDSRT_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.02 | 30 | 180 | 180 | 30 | 10 | 1 | 0.02 | 0 | 0 | 0
255961 | lhfrt | 25596 | HDSRT_BESS | 0.69 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.02 | 30 | 180 | 180 | 30 | 10 | 1 | 0.02 | 0 | 0 | 0
252811 | lhfrt | 25281 | ATHOS_PV1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0.16 | 350 | 650 | 650 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0
252841 | lhfrt | 25284 | ATHOS_PV2 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0.16 | 350 | 650 | 650 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0
252871 | lhfrt | 25287 | ATHOS_PV3 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0.16 | 350 | 650 | 650 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0
252901 | lhfrt | 25290 | ATHOS_PV4 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 4 | 3 | 2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0.16 | 350 | 650 | 650 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0
292011 | lhfrt | 29201 | WALCRKG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292021 | lhfrt | 29202 | WALCRKG2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292031 | lhfrt | 29203 | WALCRKG3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292041 | lhfrt | 29204 | WALCRKG4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292051 | lhfrt | 29205 | WALCRKG5 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247081 | lhfrt | 24708 | BORAX I | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.81 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290641 | lhfrt | 29064 | MOUNTWND_1G | 0.6 | 1 | 29060 | MOUNTWND | 115 | : |  |  | #9 | 60 | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290661 | lhfrt | 29066 | MOUNTWND_2G | 0.6 | 1 | 29060 | MOUNTWND | 115 | : |  |  | #9 | 60 | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290691 | lhfrt | 29069 | MOUNTWND_3G | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291803 | lhfrt | 29180 | INDIGO G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -1.95 | 1.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291904 | lhfrt | 29190 | INDIGO G4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -1.95 | 1.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291915 | lhfrt | 29191 | INDIGO G5 | 13.8 | 5 | : | [5 empty] | #9 | 60 | -1.95 | 1.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292871 | lhfrt | 29287 | SB_BESS_G1 | 34.5 | 1 | 24250 | WESTWIND | 230 | 1 | 1 | : | #9 | 60 | -2 | -3.5 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 300 | 6 | 0.1 | 180 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0
299651 | lhfrt | 29965 | TOT818_BESS_P2 | 34.5 | 1 | 24250 | WESTWIND | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.25 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
299661 | lhfrt | 29966 | TOT818_BESS_P3 | 34.5 | 1 | 24250 | WESTWIND | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.25 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0
2410011 | lhfrt | 241001 | WHITEWTR_G | 0.575 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 1.6 | -2.7 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 31 | 1 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29051G1 | lhfrt | 29051 | PSTRIAG1 | 18 | G1 | : | [5 empty] | #9 | 60 | -3.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29052G2 | lhfrt | 29052 | PSTRIAG2 | 18 | G2 | : | [5 empty] | #9 | 60 | -3.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29053S1 | lhfrt | 29053 | PSTRIAS1 | 18 | S1 | : | [5 empty] | #9 | 60 | -3.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29054G3 | lhfrt | 29054 | PSTRIAG3 | 18 | G3 | : | [5 empty] | #9 | 60 | -3.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29055S2 | lhfrt | 29055 | PSTRIAS2 | 13.8 | S2 | : | [5 empty] | #9 | 60 | -3.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2936322 | lhfrt | 29363 | TOT793_PV2 | 34.5 | 22 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
2936412 | lhfrt | 29364 | TOT793_BESS2 | 34.5 | 12 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
293911 | lhfrt | 29391 | TOT848_PV | 0.38 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
293921 | lhfrt | 29392 | TOT848_ST | 0.38 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
293471 | lhfrt | 29347 | WDT1517_G1 | 0.36 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
256751 | lhfrt | 25675 | WH_STN_8 | 0.69 | 1 | : | [5 empty] | #99 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.36 | 21 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256771 | lhfrt | 25677 | WH_STN_9 | 0.69 | 1 | : | [5 empty] | #99 | 60 | 3 | 4 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.36 | 21 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250321 | lhfrt | 25032 | DSTHVST_G1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250361 | lhfrt | 25036 | DSTHVST_G2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250171 | lhfrt | 25017 | DSTHVST_BESS | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296371 | lhfrt | 29637 | Catalina_G1 | 0.32 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296351 | lhfrt | 29635 | Catalina_G2 | 0.32 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296401 | lhfrt | 29640 | Catalina2_G | 0.36 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.15 | 30 | 180 | 0.15 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
299045 | lhfrt | 29904 | ELSEG5GT | 16.5 | 5 | : | [5 empty] | #9 | 60 | -3.61 | -3.01 | 1.81 | 3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299036 | lhfrt | 29903 | ELSEG6ST | 13.8 | 6 | : | [5 empty] | #9 | 60 | -2.7 | 2.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299027 | lhfrt | 29902 | ELSEG7GT | 16.5 | 7 | : | [5 empty] | #9 | 60 | -3.61 | -3.01 | 1.81 | 3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299018 | lhfrt | 29901 | ELSEG8ST | 13.8 | 8 | : | [5 empty] | #9 | 60 | -2.6 | 2.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290491 | lhfrt | 29049 | BLAST_G | 0.6 | 1 | 24839 | BLAST | 115 | : |  |  | #9 | 60 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0
294379 | lhfrt | 29437 | ALTA_IX | 1 | 9 | 29438 | CPC_EAST_6A | 230 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295917 | lhfrt | 29591 | Alta_VII_G | 1 | 7 | 29574 | SUB 6D | 230 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1891801 | lhfrt | 189180 | GAMEBIRD | 230 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1891811 | lhfrt | 189181 | Crazy Eyes-G | 230 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1891791 | lhfrt | 189179 | DESERT VIEW | 230 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1891781 | lhfrt | 189178 | INNOVATION | 230 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29800EQ | lhfrt | 29800 | VALENTINE_G | 0.645 | EQ | : | [5 empty] | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24119D1 | lhfrt | 24119 | PROCGEN | 12.48 | D1 | : | [5 empty] | #9 | 60 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294151 | lhfrt | 29415 | ALTA_I | 0.69 | 1 | 29415 | ALTA_I | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
294348 | lhfrt | 29434 | ALTA_VIII | 1 | 8 | : | [5 empty] | #8 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295961 | lhfrt | 29596 | Alta_X_G | 6 | 1 | 29596 | Alta_X_G | 6 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
297011 | lhfrt | 29701 | BSKY_G_ESWA | 0.42 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 2 | -3.5 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297011 | lhfrt | 29701 | BSKY_G_ESWA | 0.42 | 1 | 29699 | BSKY_T1 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297241 | lhfrt | 29724 | BSKY_G_ABSR | 0.38 | 1 | : | [5 empty] | #9 | 60 | 6 | 3 | -3 | -4 | -10 | 0 | 0 | 0 | 0 | 0 | 0.1 | 100 | 600 | 100 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
297241 | lhfrt | 29724 | BSKY_G_ABSR | 0.38 | 1 | 29704 | BSKY_T2 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297271 | lhfrt | 29727 | BSKY_G_SMR | 0.44 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 2 | -3.5 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297271 | lhfrt | 29727 | BSKY_G_SMR | 0.44 | 1 | 29725 | BSKY_T3 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297301 | lhfrt | 29730 | BSKY_G_SOLV | 0.44 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 2 | -3.5 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297301 | lhfrt | 29730 | BSKY_G_SOLV | 0.44 | 1 | 29728 | BSKY_T4 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297331 | lhfrt | 29733 | BSKY_G_DSR12 | 0.44 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 2 | -3.5 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297331 | lhfrt | 29733 | BSKY_G_DSR12 | 0.44 | 1 | 29731 | BSKY_T5 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297361 | lhfrt | 29736 | BSKY_G_BA | 0.645 | 1 | : | [5 empty] | #9 | 60 | 3 | 0.7 | -0.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297361 | lhfrt | 29736 | BSKY_G_BA | 0.645 | 1 | 29734 | BSKY_T6 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297391 | lhfrt | 29739 | BSKY_G_BB | 0.645 | 1 | : | [5 empty] | #9 | 60 | 3 | 0.7 | -0.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297391 | lhfrt | 29739 | BSKY_G_BB | 0.645 | 1 | 29737 | BSKY_T7 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297421 | lhfrt | 29742 | BSKY_G_BC | 0.645 | 1 | : | [5 empty] | #9 | 60 | 3 | 0.7 | -0.7 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297421 | lhfrt | 29742 | BSKY_G_BC | 0.645 | 1 | 29740 | BSKY_T8 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297451 | lhfrt | 29745 | BSKY_G_DSR3 | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297451 | lhfrt | 29745 | BSKY_G_DSR3 | 0.6 | 1 | 29743 | BSKY_T9 | 34.5 | : |  |  | #9 | 60 | 0.6 | 1.7 | -0.6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 30 | 185 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297731 | lhfrt | 29773 | ANT2_EXP2_G | 0.63 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | 0.6 | 1.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 185 | 9 | 185 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
25196EQ | lhfrt | 25196 | WINHB_SLRA_G | 0.6 | EQ | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24263EQ | lhfrt | 24263 | WINDSTAR1_GS | 0.69 | EQ | 24263 | WINDSTAR1_GS | 0.69 | EQ | : |  | #9 | 60 | -0.1 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180.04 | 30.04 | 7.54 | 0.79 | 0.06 | 180.04 | 7.54 | 0.06 | 0 | 0 | 0
24268EQ | lhfrt | 24268 | WINDSTAR2_GS | 0.69 | EQ | 24268 | WINDSTAR2_GS | 0.69 | EQ | : |  | #9 | 60 | -0.1 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180.04 | 30.04 | 7.54 | 0.79 | 0.06 | 180.04 | 7.54 | 0.06 | 0 | 0 | 0
242961 | lhfrt | 24296 | DWIII_BES1_G | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | 3 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 60 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242951 | lhfrt | 24295 | DWI_BES2_G | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | 3 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 60 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242521 | lhfrt | 24252 | DWI_BES3_G | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | 3 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 60 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296731 | lhfrt | 29673 | WILSP2_G1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
29751EQ | lhfrt | 29751 | GASKEL_WG1 | 0.645 | EQ | : | [5 empty] | #9 | 60 | 2.5 | 1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 30 | 10 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29752EQ | lhfrt | 29752 | GASKEL_WG2 | 0.645 | EQ | : | [5 empty] | #9 | 60 | 2.5 | 1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 30 | 10 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24248EQ | lhfrt | 24248 | EASTWND_G | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.25 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
24288EQ | lhfrt | 24288 | MONOLITH1_G1 | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0 | 0 | 0
24289EQ | lhfrt | 24289 | MONOLITH1_G2 | 0.69 | EQ | 24285 | MONOLITH_HS | 66 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
24292EQ | lhfrt | 24292 | MONOLITH2_G | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.25 | 0 | 0 | 0
242801 | lhfrt | 24280 | WINDWALL_1_G | 0.65 | 1 | : | [5 empty] | #9 | 60 | -3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242841 | lhfrt | 24284 | WINDWALL_2_G | 0.65 | 1 | : | [5 empty] | #9 | 60 | -3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250751 | lhfrt | 25075 | SOLARISG | 0.208 | 1 | 25072 | SOLARISH1 | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -0.6 | 0 | 0 | 0 | 0.1 | 30.0325 | 180.03 | 0.1 | 0.78534 | 7.5 | 180 | 0 | 0 | 0 | 0
250952 | lhfrt | 25095 | SOLARISG2 | 0.208 | 2 | 25072 | SOLARISH1 | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -0.6 | 0 | 0 | 0 | 0.1 | 30.0325 | 180.03 | 0.1 | 0.78534 | 7.5 | 180 | 0 | 0 | 0 | 0
295551 | lhfrt | 29555 | PACIFIC_WTG | 0.575 | 1 | : | [5 empty] | #9 | 60 | 0.5 | -0.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.3 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250491 | lhfrt | 25049 | DUCOR1 | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250521 | lhfrt | 25052 | DUCOR2 | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250551 | lhfrt | 25055 | DUCOR3 | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250581 | lhfrt | 25058 | DUCOR4 | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29687EQ | lhfrt | 29687 | ROY_AG | 0.55 | EQ | : | [5 empty] | #9 | 60 | 3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29690EQ | lhfrt | 29690 | ROY_BG | 0.55 | EQ | : | [5 empty] | #9 | 60 | 3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29536EQ | lhfrt | 29536 | SS1T2_G1 | 0.342 | EQ | : | [5 empty] | #9 | 60 | -4 | -3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29537EQ | lhfrt | 29537 | SS1T2_G2 | 0.342 | EQ | : | [5 empty] | #9 | 60 | -4 | -3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29543EQ | lhfrt | 29543 | SS1T1_G1 | 0.342 | EQ | : | [5 empty] | #9 | 60 | -4 | -3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29544EQ | lhfrt | 29544 | SS1T1_G2 | 0.342 | EQ | : | [5 empty] | #9 | 60 | -4 | -3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29447EQ | lhfrt | 29447 | KNGSS2G1 | 0.342 | EQ | : | [5 empty] | #9 | 60 | -4 | -3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29448EQ | lhfrt | 29448 | KNGSS2G2 | 0.342 | EQ | : | [5 empty] | #9 | 60 | -4 | -3 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29454EQ | lhfrt | 29454 | FRESS2G1 | 0.69 | EQ | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.05 | 0 | 0.008334 | 0
29455EQ | lhfrt | 29455 | FRESS2G2 | 0.69 | EQ | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.05 | 0 | 0.008334 | 0
296791 | lhfrt | 29679 | NortRsmdG1 | 0.6 | 1 | : | [5 empty] | #9 | 60 | 3 | -13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29888EQ | lhfrt | 29888 | TWILGHTGEN | 0.36 | EQ | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29884EQ | lhfrt | 29884 | DAWNGEN | 0.36 | EQ | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250091 | lhfrt | 25009 | DSRTSTAG | 0.55 | 1 | : | [5 empty] | #9 | 60 | -3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.151 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250082 | lhfrt | 25008 | DSRTSTBG | 0.55 | 2 | : | [5 empty] | #9 | 60 | -3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.151 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296591 | lhfrt | 29659 | CAMELOT_G | 0.418 | 1 | 29655 | KALAMA | 66 | : |  |  | #9 | 60 | 3 | 2 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 650 | 0.16 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296621 | lhfrt | 29662 | COLUMBIA2_G | 0.418 | 1 | 29655 | KALAMA | 66 | : |  |  | #9 | 60 | 3 | 2 | -5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 650 | 0.16 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298781 | lhfrt | 29878 | ACACIA_G | 0.342 | 1 | 29875 | BERRENDO | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1 | 30.1 | 180.1 | 0.1 | 0.84 | 7.6 | 30.1 | 180.1 | 0 | 0 | 0
290231 | lhfrt | 29023 | TIFFWIND_G | 0.6 | 1 | : | [5 empty] | #9 | 60 | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249741 | lhfrt | 24974 | BLACK_CRK G1 | 0.34 | 1 | : | [5 empty] | #9 | 60 | 3.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250442 | lhfrt | 25044 | BLACK_CRK G2 | 0.34 | 2 | : | [5 empty] | #9 | 60 | 3.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250383 | lhfrt | 25038 | BLACK_CRK G3 | 0.34 | 3 | : | [5 empty] | #9 | 60 | 3.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250414 | lhfrt | 25041 | BLACK_CRK G4 | 0.34 | 4 | : | [5 empty] | #9 | 60 | 3.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2401651 | lhfrt | 240165 | COACHELLA_1 | 0.65 | 1 | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290751 | lhfrt | 29075 | COACHELLA_1G | 0.65 | 1 | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294741 | lhfrt | 29474 | NSR_WND1 | 0.69 | 1 | 29468 | MANDIBLE | 230 | : |  |  | #9 | 60 | 2.5 | 1.6 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 31 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298961 | lhfrt | 29896 | APPINV | 0.48 | 1 | 29893 | GLOW | 66 | : |  |  | #9 | 60 | -3 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299001 | lhfrt | 29900 | ALPINE_G | 0.324 | 1 | : | [5 empty] | #9 | 60 | 3 | 1.7 | -4 | -3 | -3 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
241161 | lhfrt | 24116 | WELLGEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249691 | lhfrt | 24969 | DSRTSL_PV1_1 | 0.315 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249702 | lhfrt | 24970 | DSRTSL_PV1_2 | 0.315 | 2 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249673 | lhfrt | 24967 | DSRTSL_PV2_3 | 0.315 | 3 | : | [5 empty] | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249684 | lhfrt | 24968 | DSRTSL_PV2_4 | 0.315 | 4 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291611 | lhfrt | 29161 | DSRTSL_BS1_G | 0.66 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291621 | lhfrt | 29162 | DSRTSL_BS2_G | 0.66 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246521 | lhfrt | 24652 | COLOSEM1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246501 | lhfrt | 24650 | COLOSEM2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246541 | lhfrt | 24654 | COLOSEM3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29604G1 | lhfrt | 29604 | AVSR_A_G1 | 0.324 | G1 | 29600 | SOLAR RN | 230 | : |  |  | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
29606G2 | lhfrt | 29606 | AVSR_A_G2 | 0.315 | G2 | 29600 | SOLAR RN | 230 | : |  |  | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29608G3 | lhfrt | 29608 | AVSR_B_G3 | 0.324 | G3 | 29600 | SOLAR RN | 230 | : |  |  | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
29610G4 | lhfrt | 29610 | AVSR_B_G4 | 0.315 | G4 | 29600 | SOLAR RN | 230 | : |  |  | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248401 | lhfrt | 24840 | SPRINGS12 | 13.8 | 1 | 24840 | SPRINGS12 | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248402 | lhfrt | 24840 | SPRINGS12 | 13.8 | 2 | 24840 | SPRINGS12 | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248411 | lhfrt | 24841 | SPRINGS34 | 13.8 | 1 | 24841 | SPRINGS34 | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248412 | lhfrt | 24841 | SPRINGS34 | 13.8 | 2 | 24841 | SPRINGS34 | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242421 | lhfrt | 24242 | RERC1G | 13.8 | 1 | 24242 | RERC1G | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242431 | lhfrt | 24243 | RERC2G | 13.8 | 1 | 24243 | RERC2G | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242991 | lhfrt | 24299 | RERC2G3 | 13.8 | 1 | 24299 | RERC2G3 | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243001 | lhfrt | 24300 | RERC2G4 | 13.8 | 1 | 24300 | RERC2G4 | 13.8 | : |  |  | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291011 | lhfrt | 29101 | SENTINEL_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291021 | lhfrt | 29102 | SENTINEL_G2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291031 | lhfrt | 29103 | SENTINEL_G3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291041 | lhfrt | 29104 | SENTINEL_G4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291051 | lhfrt | 29105 | SENTINEL_G5 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291061 | lhfrt | 29106 | SENTINEL_G6 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291071 | lhfrt | 29107 | SENTINEL_G7 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291081 | lhfrt | 29108 | SENTINEL_G8 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252111 | lhfrt | 25211 | CanyonGT 1 | 13.8 | 1 | 25202 | LWIS ANM | 69 | : |  |  | #9 | 60 | 2 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252122 | lhfrt | 25212 | CanyonGT 2 | 13.8 | 2 | 25202 | LWIS ANM | 69 | : |  |  | #9 | 60 | 2 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252133 | lhfrt | 25213 | CanyonGT 3 | 13.8 | 3 | 25202 | LWIS ANM | 69 | : |  |  | #9 | 60 | 2 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252144 | lhfrt | 25214 | CanyonGT 4 | 13.8 | 4 | 25202 | LWIS ANM | 69 | : |  |  | #9 | 60 | 2 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262321A | lhfrt | 26232 | APEXGT1A | 18 | 1A | : | [5 empty] | #9 | 60 | 3 | 1.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 7.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
262331B | lhfrt | 26233 | APEXGT1B | 18 | 1B | : | [5 empty] | #9 | 60 | 3 | 1.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 7.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
26234ST | lhfrt | 26234 | APEXST | 18 | ST | : | [5 empty] | #9 | 60 | 3 | 1.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 7.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
24239C1 | lhfrt | 24239 | MALBRG1G | 13.8 | C1 | : | [5 empty] | #9 | 60 | 5.76 | -3.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24240C2 | lhfrt | 24240 | MALBRG1G | 13.8 | C2 | : | [5 empty] | #9 | 60 | 5.76 | -3.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24241S3 | lhfrt | 24241 | MALBRG3G | 13.8 | S3 | : | [5 empty] | #9 | 60 | 1.2 | 1.8 | -1.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.5 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247871 | lhfrt | 24787 | POOLE | 7.2 | 1 | : | [5 empty] | #9 | 60 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253021 | lhfrt | 25302 | CLTNCTRY | 12 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253022 | lhfrt | 25302 | CLTNCTRY | 12 | 2 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253023 | lhfrt | 25302 | CLTNCTRY | 12 | 3 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253024 | lhfrt | 25302 | CLTNCTRY | 12 | 4 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253011 | lhfrt | 25301 | CLTNDREW_G12 | 12.47 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253012 | lhfrt | 25301 | CLTNDREW_G12 | 12.47 | 2 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254003 | lhfrt | 25400 | CLTNDREW_G34 | 12.47 | 3 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254004 | lhfrt | 25400 | CLTNDREW_G34 | 12.47 | 4 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24070GT | lhfrt | 24070 | ICEGEN | 13.8 | GT | 24356 | ICEGEN | 66 | : |  |  | #9 | 60 | 1.9 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24070ST | lhfrt | 24070 | ICEGEN | 13.8 | ST | 24356 | ICEGEN | 66 | : |  |  | #9 | 60 | 1.9 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252191 | lhfrt | 25219 | KERNRVR 1-1 | 2.4 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252201 | lhfrt | 25220 | KERNRVR 1-2 | 2.4 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252211 | lhfrt | 25221 | KERNRVR 1-3 | 2.4 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252221 | lhfrt | 25222 | KERNRVR 1-4 | 2.4 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292071 | lhfrt | 29207 | BLY1CT1 | 16 | 1 | 25406 | J.HINDS | 230 | : |  |  | #9 | 60 | -3 | -3.6 | -3.6 | 1.8 | 2.4 | 2.4 | 0 | 0 | 0 | 0 | 10.33 | 3.67 | 11 | 10.33 | 3.67 | 11 | 0 | 0 | 0 | 0 | 0
292081 | lhfrt | 29208 | BLY1CT2 | 16 | 1 | 25406 | J.HINDS | 230 | : |  |  | #9 | 60 | -3 | -3.6 | -3.6 | 1.8 | 2.4 | 2.4 | 0 | 0 | 0 | 0 | 10.33 | 3.67 | 11 | 10.33 | 3.67 | 11 | 0 | 0 | 0 | 0 | 0
292091 | lhfrt | 29209 | BLY1ST1 | 16 | 1 | 25406 | J.HINDS | 230 | : |  |  | #9 | 60 | -3 | -3.6 | -3.6 | 1.8 | 2.4 | 2.4 | 0 | 0 | 0 | 0 | 10.33 | 3.67 | 11 | 10.33 | 3.67 | 11 | 0 | 0 | 0 | 0 | 0
243182 | lhfrt | 24318 | MAMOTH2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241071 | lhfrt | 24107 | ORMOND1G | 26 | 1 | : | [5 empty] | #9 | 60 | -1.7 | -2.3 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241082 | lhfrt | 24108 | ORMOND2G | 26 | 2 | : | [5 empty] | #9 | 60 | -1.7 | -2.3 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240621 | lhfrt | 24062 | HARBOR G | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241021 | lhfrt | 24102 | OMAR 1G | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241032 | lhfrt | 24103 | OMAR 2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241043 | lhfrt | 24104 | OMAR 3G | 13.8 | 3 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241054 | lhfrt | 24105 | OMAR 4G | 13.8 | 4 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241431 | lhfrt | 24143 | SYCCYN1G | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241442 | lhfrt | 24144 | SYCCYN2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241453 | lhfrt | 24145 | SYCCYN3G | 13.8 | 3 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241464 | lhfrt | 24146 | SYCCYN4G | 13.8 | 4 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 1
241635 | lhfrt | 24163 | ARCO 5G | 13.8 | 5 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247444 | lhfrt | 24744 | NAVYII4G | 13.8 | 4 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247455 | lhfrt | 24745 | NAVYII5G | 13.8 | 5 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247466 | lhfrt | 24746 | NAVYII6G | 13.8 | 6 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247122 | lhfrt | 24712 | CALGEN2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247133 | lhfrt | 24713 | CALGEN3G | 13.8 | 3 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256481 | lhfrt | 25648 | DVLCYN1G | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256492 | lhfrt | 25649 | DVLCYN2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.7 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256033 | lhfrt | 25603 | DVLCYN3G | 13.8 | 3 | : | [5 empty] | #9 | 60 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256044 | lhfrt | 25604 | DVLCYN4G | 13.8 | 4 | : | [5 empty] | #9 | 60 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247389 | lhfrt | 24738 | LUZ9 G | 13.8 | 9 | : | [5 empty] | #9 | 60 | -1.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249771 | lhfrt | 24977 | GENESIS G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.2 | 2.4 | -1.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0.5 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249781 | lhfrt | 24978 | GENESIS G2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.2 | 2.4 | -1.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0.5 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24580G1 | lhfrt | 24580 | HUNTBCH CTG1 | 18 | G1 | 24578 | AES_HB_ENGY | 230 | : |  |  | #9 | 60 | 3 | -3.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24581G2 | lhfrt | 24581 | HUNTBCH CTG2 | 18 | G2 | 24578 | AES_HB_ENGY | 230 | : |  |  | #9 | 60 | 3 | -3.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24582S1 | lhfrt | 24582 | HUNTBCH STG | 18 | S1 | 24578 | AES_HB_ENGY | 230 | : |  |  | #9 | 60 | 3.61 | -3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24575G1 | lhfrt | 24575 | ALAMT CTG1 | 18 | G1 | 24574 | ALMITOS_ENGY | 230 | : |  |  | #9 | 60 | 3 | -3.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24576G2 | lhfrt | 24576 | ALAMT CTG2 | 18 | G2 | 24574 | ALMITOS_ENGY | 230 | : |  |  | #9 | 60 | 3 | -3.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24577S1 | lhfrt | 24577 | ALAMT STG | 18 | S1 | 24574 | ALMITOS_ENGY | 230 | : |  |  | #9 | 60 | 3.61 | -3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24110D1 | lhfrt | 24110 | OXGEN | 13.8 | D1 | : | [5 empty] | #9 | 60 | -0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258071 | lhfrt | 25807 | BLY_GREEN1_G | 0.21 | 1 | : | [5 empty] | #9 | 60 | -3 | -0.7 | 0.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24107R1 | lhfrt | 24107 | ORMOND1G | 26 | R1 | : | [5 empty] | #9 | 60 | -1.7 | -2.3 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24108R2 | lhfrt | 24108 | ORMOND2G | 26 | R2 | : | [5 empty] | #9 | 60 | -1.7 | -2.3 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256051 | lhfrt | 25605 | EDMON1AP | 14.4 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256062 | lhfrt | 25606 | EDMON2AP | 14.4 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256073 | lhfrt | 25607 | EDMON3AP | 14.4 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256075 | lhfrt | 25607 | EDMON3AP | 14.4 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256084 | lhfrt | 25608 | EDMON4AP | 14.4 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256086 | lhfrt | 25608 | EDMON4AP | 14.4 | 6 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256097 | lhfrt | 25609 | EDMON5AP | 14.4 | 7 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256099 | lhfrt | 25609 | EDMON5AP | 14.4 | 9 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2561010 | lhfrt | 25610 | EDMON6AP | 14.4 | 10 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256108 | lhfrt | 25610 | EDMON6AP | 14.4 | 8 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2561111 | lhfrt | 25611 | EDMON7AP | 14.4 | 11 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2561113 | lhfrt | 25611 | EDMON7AP | 14.4 | 13 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2561212 | lhfrt | 25612 | EDMON8AP | 14.4 | 12 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2561214 | lhfrt | 25612 | EDMON8AP | 14.4 | 14 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256141 | lhfrt | 25614 | OSO A P | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256142 | lhfrt | 25614 | OSO A P | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256143 | lhfrt | 25614 | OSO A P | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256144 | lhfrt | 25614 | OSO A P | 13.2 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256155 | lhfrt | 25615 | OSO B P | 13.2 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256156 | lhfrt | 25615 | OSO B P | 13.2 | 6 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256157 | lhfrt | 25615 | OSO B P | 13.2 | 7 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256158 | lhfrt | 25615 | OSO B P | 13.2 | 8 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256171 | lhfrt | 25617 | PEARBMAP | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256172 | lhfrt | 25617 | PEARBMAP | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256173 | lhfrt | 25617 | PEARBMAP | 13.8 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256184 | lhfrt | 25618 | PEARBMBP | 13.8 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256185 | lhfrt | 25618 | PEARBMBP | 13.8 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256186 | lhfrt | 25618 | PEARBMBP | 13.8 | 6 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256197 | lhfrt | 25619 | PEARBMCP | 13.8 | 7 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256198 | lhfrt | 25619 | PEARBMCP | 13.8 | 8 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256209 | lhfrt | 25620 | PEARBMDP | 13.8 | 9 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256531 | lhfrt | 25653 | ALAMO SC | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256571 | lhfrt | 25657 | MJSIPHON | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.1 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256582 | lhfrt | 25658 | MJSIPHON | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3.1 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256593 | lhfrt | 25659 | MJSIPHON | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3.1 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29011C1 | lhfrt | 29011 | BREAPWR2 | 13.8 | C1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29011C2 | lhfrt | 29011 | BREAPWR2 | 13.8 | C2 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29011C4 | lhfrt | 29011 | BREAPWR2 | 13.8 | C4 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29011S1 | lhfrt | 29011 | BREAPWR2 | 13.8 | S1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29011C3 | lhfrt | 29011 | BREAPWR2 | 13.8 | C3 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247037 | lhfrt | 24703 | BLM E7G | 13.8 | 7 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247048 | lhfrt | 24704 | BLM E8G | 13.8 | 8 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247059 | lhfrt | 24705 | BLM W9G | 13.8 | 9 | : | [5 empty] | #9 | 60 | 2.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29598EQ | lhfrt | 29598 | Voyager2_G2 | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
29599EQ | lhfrt | 29599 | Voyager2_G1 | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
29595EQ | lhfrt | 29595 | Voyager3_G | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
29597EQ | lhfrt | 29597 | Voyager4_G | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
255231 | lhfrt | 25523 | ALMITOS B1_G | 0.645 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
246581 | lhfrt | 24658 | MNZNA_W1 | 0.69 | 1 | 24655 | MANZANA | 230 | : |  |  | #9 | 60 | -2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246611 | lhfrt | 24661 | MNZNA_W2 | 0.69 | 1 | 24655 | MANZANA | 230 | : |  |  | #9 | 60 | -2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247981 | lhfrt | 24798 | ALBAG1 | 16.75 | 1 | : | [5 empty] | #9 | 60 | -3 | -3.5 | -4 | 2.5 | 3 | 3.5 | 0 | 0 | 0 | 0 | 60 | 8 | 1 | 60 | 8 | 1 | 0 | 0 | 0 | 0 | 0
247992 | lhfrt | 24799 | OCASOG2 | 16.75 | 2 | : | [5 empty] | #9 | 60 | -3 | -3.5 | -4 | 2.5 | 3 | 3.5 | 0 | 0 | 0 | 0 | 60 | 8 | 1 | 60 | 8 | 1 | 0 | 0 | 0 | 0 | 0
249211 | lhfrt | 24921 | MNTV-G3A | 18 | 1 | : | [5 empty] | #9 | 60 | 2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249221 | lhfrt | 24922 | MNTV-G3B | 18 | 1 | : | [5 empty] | #9 | 60 | 2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249231 | lhfrt | 24923 | MNTV-ST3 | 18 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249241 | lhfrt | 24924 | MNTV-G4A | 18 | 1 | : | [5 empty] | #9 | 60 | 2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249251 | lhfrt | 24925 | MNTV-G4B | 18 | 1 | : | [5 empty] | #9 | 60 | 2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249261 | lhfrt | 24926 | MNTV-ST4 | 18 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243182 | lhfrt | 24318 | MAMOTH2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257581 | lhfrt | 25758 | WDT1535_G | 0.69 | 1 | 25759 | WDT1535_H | 16 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.08 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
257951 | lhfrt | 25795 | WDT1539_G | 0.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25899EQ | lhfrt | 25899 | WDT1520_G | 0.48 | EQ | 25899 | WDT1520_G | 0.48 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0.16 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
256691 | lhfrt | 25669 | WDT1655G | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
297761 | lhfrt | 29776 | ANT2_SPA_G | 0.6 | 1 | 29772 | ANTLOP2_C1 | 34.5 | : |  |  | #9 | 60 | 1.7 | 0.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 185 | 9 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297761 | lhfrt | 29776 | ANT2_SPA_G | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297711 | lhfrt | 29771 | ANT2_SPB_G | 0.6 | 1 | 29769 | ANT2_SPB_L | 34.5 | : |  |  | #9 | 60 | 1.7 | 0.6 | -2.2 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 185 | 9 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297711 | lhfrt | 29771 | ANT2_SPB_G | 0.6 | 1 | : | [5 empty] | #9 | 60 | 5 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29338G1 | lhfrt | 29338 | CLRWTRCT | 12.47 | G1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29340S1 | lhfrt | 29340 | CLRWTRST | 12.47 | S1 | : | [5 empty] | #9 | 60 | 3 | 2 | -2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 5 | 5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257831 | lhfrt | 25783 | BISHOP3 | 2.4 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257832 | lhfrt | 25783 | BISHOP3 | 2.4 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257833 | lhfrt | 25783 | BISHOP3 | 2.4 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257851 | lhfrt | 25785 | BISHOP4 | 2.4 | 1 | : | [5 empty] | #9 | 60 | 2 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257852 | lhfrt | 25785 | BISHOP4 | 2.4 | 2 | : | [5 empty] | #9 | 60 | 2 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257853 | lhfrt | 25785 | BISHOP4 | 2.4 | 3 | : | [5 empty] | #9 | 60 | 2 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257854 | lhfrt | 25785 | BISHOP4 | 2.4 | 4 | : | [5 empty] | #9 | 60 | 2 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257855 | lhfrt | 25785 | BISHOP4 | 2.4 | 5 | : | [5 empty] | #9 | 60 | 2 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297221 | lhfrt | 29722 | GARLND_G3 | 0.418 | 1 | 29713 | GARLAND | 230 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.1 | 180 | 30 | 0.1 | 0 | 0 | 0
252151 | lhfrt | 25215 | ATHOS_ST1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 5 | 5 | 2 | 2 | 1 | -1 | -2 | -3 | -4 | -4 | 0.15 | 0.15 | 10 | 180 | 300 | 300 | 180 | 30 | 0.75 | 0.15 | 0
252162 | lhfrt | 25216 | ATHOS_ST2 | 0.69 | 2 | : | [5 empty] | #9 | 60 | 5 | 5 | 2 | 2 | 1 | -1 | -2 | -3 | -4 | -4 | 0.15 | 0.15 | 10 | 180 | 300 | 300 | 180 | 30 | 0.75 | 0.15 | 0
252173 | lhfrt | 25217 | ATHOS_ST3 | 0.69 | 3 | : | [5 empty] | #9 | 60 | 5 | 5 | 2 | 2 | 1 | -1 | -2 | -3 | -4 | -4 | 0.15 | 0.15 | 10 | 180 | 300 | 300 | 180 | 30 | 0.75 | 0.15 | 0
252184 | lhfrt | 25218 | ATHOS_ST4 | 0.69 | 4 | : | [5 empty] | #9 | 60 | 5 | 5 | 2 | 2 | 1 | -1 | -2 | -3 | -4 | -4 | 0.15 | 0.15 | 10 | 180 | 300 | 300 | 180 | 30 | 0.75 | 0.15 | 0
291201 | lhfrt | 29120 | DSRTSL_BS3G | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291241 | lhfrt | 29124 | DSRTSL_BS4G | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269671 | lhfrt | 26967 | MKTPV1 | 0.3 | 1 | 26964 | MKTSUB | 500 | : |  |  | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2696072 | lhfrt | 269607 | MKTPV2 | 0.3 | 2 | 26964 | MKTSUB | 500 | : |  |  | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2696173 | lhfrt | 269617 | MKTPV3 | 0.3 | 3 | 26964 | MKTSUB | 500 | : |  |  | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2696274 | lhfrt | 269627 | MKTPV4 | 0.3 | 4 | 26964 | MKTSUB | 500 | : |  |  | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
2696375 | lhfrt | 269637 | MKTBESS1 | 0.3 | 5 | 26964 | MKTSUB | 500 | : |  |  | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
263301 | lhfrt | 26330 | Wind_U_PV1 | 0.385 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 0
263361 | lhfrt | 26336 | Wind_U_BES1 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0
263401 | lhfrt | 26340 | Wind_U_PV2 | 0.385 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0 | 0 | 0 | 0
263431 | lhfrt | 26343 | Wind_U_BES2 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0
2691491 | lhfrt | 269149 | ROS_LV1-PV1 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
2691102 | lhfrt | 269110 | ROS_LV2-PV2 | 0.69 | 2 | : | [5 empty] | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
2691111 | lhfrt | 269111 | ROS_PV3 | 0.27 | 1 | 269142 | ROS_SUB2 | 230.0: |  |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
261961 | lhfrt | 26196 | PPA_MS_PV1 | 0.66 | 1 | : | [5 empty] | #1 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261981 | lhfrt | 26198 | PPA_MS_PV2 | 0.66 | 1 | : | [5 empty] | #1 | 60 | -3 | -1.7 | 0.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271891 | lhfrt | 27189 | ELANDI_PV3 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271911 | lhfrt | 27191 | ELANDI_BESS3 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
269881 | lhfrt | 26988 | ELANDI_PV4 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269801 | lhfrt | 26980 | ELANDI_BESS4 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
269961 | lhfrt | 26996 | ELANDII_PV1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269981 | lhfrt | 26998 | ELANDII_BESS1 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
271961 | lhfrt | 27196 | ELANDII_PV2 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271981 | lhfrt | 27198 | ELANDII_BESS2 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.2 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.2 | 0 | 0 | 0
268723 | lhfrt | 26872 | BCN_ST13 | 0.385 | 3 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.62 | -3 | -2.7 | -2.2 | -1.6 | -0.62 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
268744 | lhfrt | 26874 | BCN_ST14 | 0.385 | 4 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.62 | -3 | -2.7 | -2.2 | -1.6 | -0.62 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
268828 | lhfrt | 26882 | BCN_ST38 | 0.385 | 8 | 26906 | BEACON | 34.5 | : |  |  | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | -5 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 1
268807 | lhfrt | 26880 | BCN_ST37 | 0.385 | 7 | 26906 | BEACON | 34.5 | : |  |  | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | -5 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 1
26884A | lhfrt | 26884 | BCN_ST4A | 0.385 | A | 26906 | BEACON | 34.5 | : |  |  | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | -5 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 1
26886B | lhfrt | 26886 | BCN_ST4B | 0.385 | B | 26906 | BEACON | 34.5 | : |  |  | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | -5 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 1
268765 | lhfrt | 26876 | BCN_ST25 | 0.55 | 5 | : | [5 empty] | #9 | 60 | -3.1 | -2.8 | -2.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
268786 | lhfrt | 26878 | BCN_ST26 | 0.55 | 6 | : | [5 empty] | #9 | 60 | -3.1 | -2.8 | -2.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
268681 | lhfrt | 26868 | BCN_ST51 | 0.55 | 1 | : | [5 empty] | #9 | 60 | -3.1 | -2.8 | -2.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
268702 | lhfrt | 26870 | BCN_ST52 | 0.55 | 2 | : | [5 empty] | #9 | 60 | -3.1 | -2.8 | -2.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
271831 | lhfrt | 27183 | W_PPA_C_W1 | 0.69 | 1 | 27171 | W_PPA_C_SUB | 345 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
271841 | lhfrt | 27184 | W_PPA_C_W2 | 0.69 | 1 | 27171 | W_PPA_C_SUB | 230 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
269101 | lhfrt | 26910 | PPA24_LL_PV | 0.63 | 1 | : | [5 empty] | #4 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.5 | 180 | 30 | 7.5 | 0.75 | 0.2 | 0 | 0 | 0
269201 | lhfrt | 26920 | PPA24_LL-BES | 0.63 | 1 | : | [5 empty] | #4 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.5 | 180 | 30 | 7.5 | 0.75 | 0.2 | 0 | 0 | 0
269511 | lhfrt | 26951 | PPA24_CH_PV | 0.64 | 1 | : | [5 empty] | #1 | 60 | 0.7 | 1.7 | 1.8 | -0.7 | -1.7 | -2.3 | -2.8 | -3.1 | 0 | 0 | 181 | 31 | 0.0001 | 181 | 31 | 8 | 0.8 | 0.0001 | 0.008334 | 0.008334 | 0
269541 | lhfrt | 26954 | PPA24_CH_BESS | 0.64 | 1 | : | [5 empty] | #1 | 60 | 0.7 | 1.7 | 1.8 | -0.7 | -1.7 | -2.3 | -2.8 | -3.1 | 0 | 0 | 181 | 31 | 0.0001 | 181 | 31 | 8 | 0.8 | 0.0001 | 0.008334 | 0.008334 | 0
272213A | lhfrt | 27221 | SPRBKPV3_A | 0.63 | 3A | : | [5 empty] | #99 | 60 | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272243B | lhfrt | 27224 | SPRBKPV3_B | 0.8 | 3B | : | [5 empty] | #10 | 60 | -0.6 | -1.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26976SM | lhfrt | 26976 | MOAPA1PV | 0.36 | SM | : | [5 empty] | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
26977GE | lhfrt | 26977 | MOAPA2PV | 0.55 | GE | : | [5 empty] | #9 | 60 | 3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26978GE | lhfrt | 26978 | MOAPA3PV | 0.55 | GE | : | [5 empty] | #9 | 60 | 3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262081 | lhfrt | 26208 | CMS3PV1 | 0.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 30 | 180 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0
262102 | lhfrt | 26210 | CMS3PV2 | 0.8 | 2 | : | [5 empty] | #9 | 60 | 0.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 30 | 180 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0
261088 | lhfrt | 26108 | SCATT8G | 21 | 8 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261099 | lhfrt | 26109 | SCATT9G | 16 | 9 | : | [5 empty] | #9 | 60 | -1.6 | -3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.03 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0
26110H1 | lhfrt | 26110 | HARB1G | 13.8 | H1 | : | [5 empty] | #9 | 60 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26111H2 | lhfrt | 26111 | HARB2G | 13.8 | H2 | : | [5 empty] | #9 | 60 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26023H5 | lhfrt | 26023 | HARB5G | 13.8 | H5 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2614411 | lhfrt | 26144 | HARBCT11 | 13.8 | 11 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2614512 | lhfrt | 26145 | HARBCT12 | 13.8 | 12 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2614613 | lhfrt | 26146 | HARBCT13 | 13.8 | 13 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
270011 | lhfrt | 27001 | PTWTG | 0.57 | 1 | : | [5 empty] | #9 | 60 | -3.5 | -2.5 | 1.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 31 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2614714 | lhfrt | 26147 | HARBCT14 | 13.8 | 14 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
261574 | lhfrt | 26157 | SCATT4G | 18 | 4 | : | [5 empty] | #9 | 60 | -1.6 | -3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261585 | lhfrt | 26158 | SCATT5G | 13.8 | 5 | : | [5 empty] | #9 | 60 | -1.6 | -3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261596 | lhfrt | 26159 | SCATT6G | 13.8 | 6 | : | [5 empty] | #9 | 60 | -1.6 | -3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261607 | lhfrt | 26160 | SCATT7G | 13.8 | 7 | : | [5 empty] | #9 | 60 | -1.6 | -3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261425 | lhfrt | 26142 | VALLEY5G | 13.8 | 5 | : | [5 empty] | #9 | 60 | -3.7 | -2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 30 | 0.033 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 1
26901B | lhfrt | 26901 | BCN_BESS1 | 0.57 | B | : | [5 empty] | #9 | 60 | -4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260017 | lhfrt | 26001 | CASTAI7G | 11.5 | 7 | : | [5 empty] | #9 | 60 | -1.6 | -3 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.03 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2614310 | lhfrt | 26143 | HARBCT10 | 13.8 | 10 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1
270181 | lhfrt | 27018 | PTSOL | 0.48 | 1 | : | [5 empty] | #9 | 60 | 1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240111 | lhfrt | 24011 | ARCO 1G | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240122 | lhfrt | 24012 | ARCO 2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240133 | lhfrt | 24013 | ARCO 3G | 13.8 | 3 | : | [5 empty] | #9 | 60 | 2.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240144 | lhfrt | 24014 | ARCO 4G | 13.8 | 4 | : | [5 empty] | #9 | 60 | 2.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24139D1 | lhfrt | 24139 | SERRFGEN | 12.47 | D1 | : | [5 empty] | #9 | 60 | -2.5 | -0.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 195 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241646 | lhfrt | 24164 | ARCO 6G | 13.8 | 6 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243401 | lhfrt | 24340 | CHARMIN | 12.47 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -3 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.1 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248613 | lhfrt | 24861 | SILVERSE | 0.55 | 3 | : | [5 empty] | #9 | 60 | -0.62 | -1.6 | -2.2 | -2.7 | -3 | -5 | 0.62 | 1.6 | 1.7 | 5 | 180 | 30 | 7.5 | 0.75 | 10 | 0.001 | 180 | 30 | 10 | 0.001 | 0
248622 | lhfrt | 24862 | SILVERSF | 0.36 | 2 | : | [5 empty] | #9 | 60 | -3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248631 | lhfrt | 24863 | SILVERSG | 0.36 | 1 | : | [5 empty] | #9 | 60 | -3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250791 | lhfrt | 25079 | PRIDGE_B_G | 0.645 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
250861 | lhfrt | 25086 | SIRA_SOLAR_G | 0.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 9999 | 7.5 | 30 | 180 | 9999 | 0.008 | 0.008 | 0.008 | 0
25092EQ | lhfrt | 25092 | MOJAVE_WS_G | 0.8 | EQ | 25193 | SUNSPOT | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 9999 | 7.5 | 30 | 180 | 9999 | 0.008334 | 0.008334 | 0.008334 | 0
251691 | lhfrt | 25169 | PRIDGE_C_G | 0.645 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
251701 | lhfrt | 25170 | PRIDGE_A_G2 | 0.36 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
251711 | lhfrt | 25171 | PRIDGE_A_G | 0.36 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
251801 | lhfrt | 25180 | WDT1250BESS | 0.48 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
251851 | lhfrt | 25185 | WDT1425_G1 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0
251861 | lhfrt | 25186 | WDT1426_G2 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0
251871 | lhfrt | 25187 | WDT1429_BATT | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0
251921 | lhfrt | 25192 | WDT1406_G | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0
25199EQ | lhfrt | 25199 | WINHB_SLRB_G | 0.55 | EQ | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269431 | lhfrt | 26943 | SOVSRPV | 0.38 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
290001 | lhfrt | 29000 | HIDEDST1 | 20 | 1 | 24350 | HIDESERT | 230 | 1 | : |  | #9 | 60 | 2.1 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294182 | lhfrt | 29418 | ALTA_II | 1 | 2 | 29411 | CPC_WEST | 230 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294213 | lhfrt | 29421 | ALTA_III | 1 | 3 | 29411 | CPC_WEST | 230 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294254 | lhfrt | 29425 | ALTA_IV | 1 | 4 | 29422 | CPC_EAST | 230 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294285 | lhfrt | 29428 | ALTA_V | 1 | 5 | 29422 | CPC_EAST | 230 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294316 | lhfrt | 29431 | ALTA_VI | 1 | 6 | 29431 | ALTA_VI | 1 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29490EQ | lhfrt | 29490 | RSTREE_1 | 0.65 | EQ | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295901 | lhfrt | 29590 | Voyager1_G | 0.65 | 1 | : | [5 empty] | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29594EQ | lhfrt | 29594 | Voyager5_G | 0.65 | EQ | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.2 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.2 | 0 | 0 | 0
296972 | lhfrt | 29697 | ASTORIA2G | 0.55 | 2 | : | [5 empty] | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296941 | lhfrt | 29694 | ASTORIA1G | 0.55 | 1 | : | [5 empty] | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297113 | lhfrt | 29711 | SGS_AVG3 | 0.52 | 3 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
297124 | lhfrt | 29712 | SGS_AVG4 | 0.52 | 4 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
297125 | lhfrt | 29712 | SGS_AVG4 | 0.52 | 5 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
299141 | lhfrt | 29914 | WADR_PV | 0.42 | 1 | 29910 | PLAINVEW | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
299171 | lhfrt | 29917 | SSOLAR_GRWKS | 0.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 9999 | 7.5 | 30 | 180 | 9999 | 0.008 | 0.008 | 0.008 | 0
299211 | lhfrt | 29921 | NLR INVTR | 0.42 | 1 | 29910 | PLAINVEW | 66 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
260041 | lhfrt | 26004 | CASTAI1G | 18 | 1 | : | [5 empty] | #9 | 60 | -0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260052 | lhfrt | 26005 | CASTAI2G | 18 | 2 | : | [5 empty] | #9 | 60 | -0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260063 | lhfrt | 26006 | CASTAI3G | 18 | 3 | : | [5 empty] | #9 | 60 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260074 | lhfrt | 26007 | CASTAI4G | 18 | 4 | : | [5 empty] | #9 | 60 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260085 | lhfrt | 26008 | CASTAI5G | 18 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260096 | lhfrt | 26009 | CASTAI6G | 18 | 6 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261101 | lhfrt | 26110 | HARB1G | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261112 | lhfrt | 26111 | HARB2G | 13.8 | 2 | : | [5 empty] | #9 | 60 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260235 | lhfrt | 26023 | HARB5G | 13.8 | 5 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2628711 | lhfrt | 26287 | HAY 11 | 13.8 | 11 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2628812 | lhfrt | 26288 | HAY 12 | 13.8 | 12 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2628913 | lhfrt | 26289 | HAY 13 | 13.8 | 13 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2629014 | lhfrt | 26290 | HAY 14 | 13.8 | 14 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2629115 | lhfrt | 26291 | HAY 15 | 13.8 | 15 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2629216 | lhfrt | 26292 | HAY 16 | 13.8 | 16 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260261 | lhfrt | 26026 | HAYNES1G | 18 | 1 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260272 | lhfrt | 26027 | HAYNES2G | 18 | 2 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261518 | lhfrt | 26151 | HAYNES8G | 18 | 8 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -2.7 | -3.2 | -3.6 | -3.6 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.8 | 0.12 | 0.04 | 0.1 | 0 | 0 | 0
261529 | lhfrt | 26152 | HAYNES9G | 18 | 9 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3.2 | -3.6 | -3.6 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.12 | 0.04 | 0.1 | 0 | 0 | 0 | 0
2615310 | lhfrt | 26153 | HAYNS10G | 18 | 10 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3.2 | -3.6 | -3.6 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.12 | 0.04 | 0.1 | 0 | 0 | 0 | 0
260391 | lhfrt | 26039 | INTERM1G | 26 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.4 | -1.6 | -1.9 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 540 | 180 | 72 | 30 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0
260402 | lhfrt | 26040 | INTERM2G | 26 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.4 | -1.6 | -1.9 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 540 | 180 | 72 | 30 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0
261683 | lhfrt | 26168 | PP2G3 | 7.5 | 3 | : | [5 empty] | #9 | 60 | -3.6 | -3.2 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0
261121 | lhfrt | 26112 | SCATT1G | 18 | 1 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261062 | lhfrt | 26106 | SCATT2G | 18 | 2 | : | [5 empty] | #9 | 60 | -4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261486 | lhfrt | 26148 | VALLEY6G | 18 | 6 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3.2 | -3.2 | -3.6 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.12 | 0.1 | 0.04 | 0 | 0 | 0 | 0
261497 | lhfrt | 26149 | VALLEY7G | 18 | 7 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3.2 | -3.2 | -3.6 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.12 | 0.1 | 0.04 | 0 | 0 | 0 | 0
261508 | lhfrt | 26150 | VALLEY8G | 18 | 8 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -2.7 | -3.2 | -3.2 | -3.6 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.8 | 0.12 | 0.1 | 0.04 | 0 | 0 | 0
269601 | lhfrt | 26960 | RECONCOPV | 0.385 | 1 | 26962 | RECINCO | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.008334 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
272261 | lhfrt | 27226 | SPRBKPV1 | 0.38 | 1 | 27225 | SPRINGBOK | 230 | h1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0.008334 | 0.008334 | 0.008334 | 1
272302 | lhfrt | 27230 | SPRBKPV2 | 0.38 | 2 | 27225 | SPRINGBOK | 230 | h1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 0.75 | 0.1 | 0.008334 | 0.008334 | 0.008334 | 1
269151 | lhfrt | 26915 | GEN_A1 | 0.405 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 99999 | 99999 | 0
269181 | lhfrt | 26918 | GEN_A2 | 0.405 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.2 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 99999 | 99999 | 0
271231 | lhfrt | 27123 | WTGGE2 | 0.57 | 1 | : | [5 empty] | #9 | 60 | 10 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 1
271171 | lhfrt | 27117 | WTGCP | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008333 | 30 | 10 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 1
27119GE | lhfrt | 27119 | WTGGE | 0.57 | GE | : | [5 empty] | #9 | 60 | 10 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 1
344441 | lhfrt | 34444 | RETRQLTYBES1 | 0.53 | 1 | 30794 | RETRQLTY | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3653322 | lhfrt | 365332 | RETRQLTYBES2 | 0.53 | 2 | 30794 | RETRQLTY | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343401 | lhfrt | 34340 | RETRQLTYSPV1 | 0.418 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
3653302 | lhfrt | 365330 | RETRQLTYSPV2 | 0.418 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
338501 | lhfrt | 33850 | CAMANCHE | 4.16 | 1 | 33566 | CAMANCHE | 115 | 1 | 1 | : | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338502 | lhfrt | 33850 | CAMANCHE | 4.16 | 2 | 33566 | CAMANCHE | 115 | 1 | 1 | : | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338503 | lhfrt | 33850 | CAMANCHE | 4.16 | 3 | 33566 | CAMANCHE | 115 | 1 | 1 | : | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340741 | lhfrt | 34074 | BEARDSLEYPH | 6.9 | 1 | 34074 | BEARDSLEYPH | 6.9 | 1 | 1 | : | #9 | 60 | 3 | -1.6 | -3.5 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 120 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324801 | lhfrt | 32480 | BOWMANPH | 4.16 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.2 | -0.6 | 0.6 | 1 | 1.6 | 1.7 | 2 | 0 | 0 | 0.0333 | 7.5 | 180 | 180 | 180 | 30 | 0.0333 | 0.75 | 0 | 0 | 0
318501 | lhfrt | 31850 | BIGCREEKWW | 4.16 | 1 | : | [5 empty] | #9 | 60 | -3 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.12 | 0.5 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0
3186831 | lhfrt | 318683 | LOSTCREEK1 | 4.16 | 1 | : | [5 empty] | #9 | 60 | 3.9 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.573 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3186841 | lhfrt | 318684 | LOSTCREEK2 | 4.16 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.573 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324881 | lhfrt | 32488 | HAYPRESSLWR | 4.16 | 1 | 32416 | HAYPRESSLWR | 60 | 1 | 1 | : | #9 | 60 | 3.06 | -6.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324891 | lhfrt | 32489 | HAYPRESSUPR | 4.16 | 1 | 32417 | HAYPRESSUPR | 60 | 1 | 1 | : | #9 | 60 | 3.06 | -6.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3656041 | lhfrt | 365604 | LILBEAR1SPV | 0.55 | 1 | 365601 | LILBEAR1 | 115 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362201 | lhfrt | 36220 | RIOBRVSLR2S | 0.38 | 1 | 36220 | Q972 | 0.38 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
324761 | lhfrt | 32476 | ROLLINSPH | 6.6 | 1 | : | [5 empty] | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3655041 | lhfrt | 365504 | SUMMERWHTSPV | 0.6 | 1 | : | [5 empty] | #9 | 60 | 2 | 1 | -1 | -2.701 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 200 | 300 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3496831 | lhfrt | 349683 | TWISSLMN1SPV | 0.42 | 1 | : | [5 empty] | #9 | 60 | 0.5 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3496862 | lhfrt | 349686 | TWISSLMN2SPV | 0.42 | 2 | : | [5 empty] | #9 | 60 | 0.5 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
392331 | lhfrt | 39233 | VASCOWIND | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3651801 | lhfrt | 365180 | CRCRNSLRSPV | 0.36 | 1 | 365177 | CRCRNSLR | 115 | 1 | 1 | : | #9 | 60 | 1.7 | -3 | 1.6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3657401 | lhfrt | 365740 | Q1129SBDC | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
3652251 | lhfrt | 365225 | Q1135BESS1 | 34.5 | 1 | 365223 | Q1135Q1391 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652261 | lhfrt | 365226 | Q1135SPV1 | 34.5 | 1 | 365223 | Q1135Q1391 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652272 | lhfrt | 365227 | Q1135BESS2 | 34.5 | 2 | 365223 | Q1135Q1391 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652302 | lhfrt | 365230 | Q1135SPV2 | 0.63 | 2 | 365223 | Q1135Q1391 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652403 | lhfrt | 365240 | Q1135BESS3 | 0.69 | 3 | 365223 | Q1135Q1391 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324981 | lhfrt | 32498 | SPILINCF | 12.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362011 | lhfrt | 36201 | SALR GN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 8 | 3 | 3 | -6 | -3 | -3 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0
319021 | lhfrt | 31902 | HAT CRK1 | 6.6 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3663804 | lhfrt | 366380 | SOLANO4WIND | 0.72 | 4 | 30480 | RUSSELLSMUD | 230 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
3662611 | lhfrt | 366261 | Q1557BESS | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0.008334 | 0
366955RE | lhfrt | 366955 | 2446-RDSPV | 0.64 | RE | 366952 | CRCKERNFRNT | 12.47 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.16 | 0.16 | 6550 | 90 | 5 | 0.16 | 0.16 | 0
3663441 | lhfrt | 366344 | WSTFRDFLTBES | 0.48 | 1 | 30402 | WSFRDFLT | 230 | 1 | 1 | : | #9 | 60 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0.21 | 31 | 181 | 181 | 31 | 7.5 | 0.21 | 0 | 0 | 0 | 0
3656492 | lhfrt | 365649 | Q1835BESS | 0.66 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.15 | 30 | 180 | 0.008334 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
3666081 | lhfrt | 366608 | Q1470BESS | 0.66 | 1 | 366605 | Q1470 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365688RE | lhfrt | 365688 | P66_SUB100-PV | 0.63 | RE | 999901 | ROD-STA | 115 | 1 | 1 | : | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 5000 | 0.2 | 650 | 5000 | 0 | 0 | 0 | 0
3669661 | lhfrt | 366966 | Q1350BESS | 34.5 | 1 | 366133 | Q1350 | 60 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3661301 | lhfrt | 366130 | Q1350SPV1 | 34.5 | 1 | 366133 | Q1350 | 60 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3661311 | lhfrt | 366131 | Q1350SPV2 | 34.5 | 1 | 366133 | Q1350 | 60 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350501 | lhfrt | 35050 | BERRYCOGEN18 | 6.9 | 1 | : | [5 empty] | #9 | 60 | 2.4 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350502 | lhfrt | 35050 | BERRYCOGEN18 | 6.9 | 2 | : | [5 empty] | #9 | 60 | 2.4 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3469121 | lhfrt | 346912 | AVENALSPV1 | 0.385 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3469142 | lhfrt | 346914 | AVENALSPV2 | 0.385 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
393461 | lhfrt | 39346 | 9C1270 | 0.48 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 30 | 180 | 0 | 0 | 1
364301 | lhfrt | 36430 | TOPAZGA1 | 0.324 | 1 | 30921 | TOPAZA | 230 | 1 | 1 | : | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 1
364321 | lhfrt | 36432 | TOPAZGA2 | 0.69 | 1 | 30921 | TOPAZA | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.04 | 30 | 180 | 0.04 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
3643621 | lhfrt | 364362 | TOPAZGA3 | 0.69 | 1 | 30921 | TOPAZA | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.04 | 30 | 180 | 0.04 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
364341 | lhfrt | 36434 | TOPAZGB1 | 0.324 | 1 | 30922 | TOPAZB | 230 | 1 | 1 | : | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 1
364361 | lhfrt | 36436 | TOPAZGB2 | 0.69 | 1 | 30922 | TOPAZB | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.04 | 30 | 180 | 0.04 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
3643631 | lhfrt | 364363 | TOPAZGB3 | 0.69 | 1 | 30922 | TOPAZB | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.04 | 30 | 180 | 0.04 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 1
391851 | lhfrt | 39185 | Q1097 | 0.48 | 1 | 30401 | BEARCNYN | 230 | 1 | 1 | : | #9 | 60 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0.21 | 31 | 181 | 181 | 31 | 7.5 | 0.21 | 0 | 0 | 0 | 0
3652081 | lhfrt | 365208 | Q1120SPV1 | 0.63 | 1 | 365201 | Q1120 | 230 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652092 | lhfrt | 365209 | Q1120BESS1 | 0.48 | 2 | 365201 | Q1120 | 230 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652103 | lhfrt | 365210 | Q1120SPV2 | 0.63 | 3 | 365201 | Q1120 | 230 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652114 | lhfrt | 365211 | Q1120BESS2 | 0.48 | 4 | 365201 | Q1120 | 230 | 1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652191 | lhfrt | 365219 | Q1139SPV1 | 0.63 | 1 | 365212 | Q1139 | 230 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652213 | lhfrt | 365221 | Q1139SPV2 | 0.63 | 3 | 365212 | Q1139 | 230 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0.16 | 185 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652202 | lhfrt | 365220 | Q1139BESS1 | 0.48 | 2 | 365212 | Q1139 | 230 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652224 | lhfrt | 365222 | Q1139BESS2 | 0.48 | 4 | 365212 | Q1139 | 230 | h1 | 1 | : | #9 | 60 | -1.6 | -3 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0.25 | 186 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652331 | lhfrt | 365233 | Q1244SPV1 | 34.5 | 1 | 365231 | Q1244 | 230 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652351 | lhfrt | 365235 | Q1244BES1 | 34.5 | 1 | 365231 | Q1244 | 230 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652372 | lhfrt | 365237 | Q1244SPV2 | 34.5 | 2 | 365231 | Q1244 | 230 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3652392 | lhfrt | 365239 | Q1244BES2 | 0.64 | 2 | 365231 | Q1244 | 230 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3676261 | lhfrt | 367626 | Q1244SPV3 | 34.5 | 1 | 365231 | Q1244 | 230 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3667291 | lhfrt | 366729 | Q1455SPV | 0.6 | 1 | 366725 | Q1455 | 60 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 1 | 1 | 0
3667302 | lhfrt | 366730 | Q1455BESS | 0.6 | 2 | 366725 | Q1455 | 60 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 1 | 1 | 0
3668071 | lhfrt | 366807 | Q1443SPV | 34.5 | 1 | 366805 | Q1443 | 115 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3668062 | lhfrt | 366806 | Q1443BESS | 34.5 | 2 | 366805 | Q1443 | 115 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3651961 | lhfrt | 365196 | Q0954SPV1 | 0.63 | 1 | 365190 | Q0954 | 230 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3651972 | lhfrt | 365197 | Q0954SPV2 | 0.63 | 2 | 365190 | Q0954 | 230 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3651981 | lhfrt | 365198 | Q0954BESS1 | 0.69 | 1 | 365190 | Q0954 | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | 0.7 | 2 | 3 | 4 | 0 | 0 | 6550 | 90 | 10 | 0.01 | 6550 | 90 | 5 | 1 | 0 | 0 | 0
3651992 | lhfrt | 365199 | Q1027BESS2 | 0.69 | 2 | 365190 | Q0954 | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | 0.7 | 2 | 3 | 4 | 0 | 0 | 6550 | 90 | 10 | 0.01 | 6550 | 90 | 5 | 1 | 0 | 0 | 0
3657241 | lhfrt | 365724 | Q1397SPV | 34.5 | 1 | 366359 | Q1398 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3657262 | lhfrt | 365726 | Q1397BESS | 0.52 | 2 | 366359 | Q1398 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3663611 | lhfrt | 366361 | Q1398SPV | 34.5 | 1 | 366359 | Q1398 | 230 | 1 | 1 | : | #9 | 60 | -3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319041 | lhfrt | 31904 | HATCREEK2PH | 6.6 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3651701 | lhfrt | 365170 | BLACKWELLSPV | 0.36 | 1 | 365168 | BLACKWELLSC1 | 12.47 | 1 | 1 | : | #9 | 60 | 0.5 | -3.2 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1667 | 0.0833 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3659941 | lhfrt | 365994 | NRORSPVBDC1 | 0.69 | 1 | 365991 | NROR | 230 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3659982 | lhfrt | 365998 | NRORSPVBDC2 | 0.69 | 2 | 365991 | NROR | 230 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3659993 | lhfrt | 365999 | NRORSPV3 | 0.69 | 3 | 365991 | NROR | 230 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3662411 | lhfrt | 366241 | PLANOBESS1 | 34.5 | 1 | 366241 | PLANOBESS1 | 34.5 | 1 | 1 | : | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3662422 | lhfrt | 366242 | PLANOBESS2 | 34.5 | 2 | 366242 | PLANOBESS2 | 34.5 | 1 | 1 | : | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3662433 | lhfrt | 366243 | PLANOBESS3 | 34.5 | 3 | 366243 | PLANOBESS3 | 34.5 | 1 | 1 | : | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3662444 | lhfrt | 366244 | PLANOBESS4 | 34.5 | 4 | 366244 | PLANOBESS4 | 34.5 | 1 | 1 | : | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383301 | lhfrt | 38330 | CDWR_GEN_EQ | 0.48 | 1 | 38325 | CDWR_GEN | 13.8 | 1 | 1 | : | #9 | 60 | 2 | 2 | -2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.008334 | 0
314651 | lhfrt | 31465 | WHEELBR1 | 12.47 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314652 | lhfrt | 31465 | WHEELBR1 | 12.47 | 2 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314653 | lhfrt | 31465 | WHEELBR1 | 12.47 | 3 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362151 | lhfrt | 36215 | WRIGHTFRMNSL | 0.55 | 1 | 30767 | WRIGHTFRMN | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.06483 | 30.1 | 180.1 | 0.1 | 0.78534 | 7.6 | 30.1 | 180.1 | 0 | 0 | 0
321541 | lhfrt | 32154 | WADHAM | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.583 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318741 | lhfrt | 31874 | SPI-BURN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.5 | -1.5 | -2.5 | 3 | -1.5 | -1.5 | -2.5 | 3 | -1.5 | 0.5 | 2 | 10 | 0.1 | 0.5 | 2 | 10 | 0.1 | 0.5 | 2 | 0
3656481 | lhfrt | 365648 | Q1272BESS | 0.66 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.15 | 30 | 180 | 0.08334 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
3656791 | lhfrt | 365679 | WALMONDSPV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 1 | -1 | -2.701 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 200 | 300 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346852 | lhfrt | 34685 | Q643WBESS | 34.5 | 2 | 30886 | Q643W | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
343191 | lhfrt | 34319 | ADERASLRSPV | 0.42 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
343051 | lhfrt | 34305 | CHWCHLA2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346291 | lhfrt | 34629 | KETTLEMNS | 0.8 | 1 | 34455 | KETTLEMNS | 70 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 9999 | 7.5 | 30 | 180 | 9999 | 0 | 0 | 0 | 0
350701 | lhfrt | 35070 | LAPLM_G1 | 21 | 1 | 35070 | LAPLM_G1 | 21 | 1 | 1 | : | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350711 | lhfrt | 35071 | LAPLM_G2 | 21 | 1 | 35070 | LAPLM_G1 | 21 | 1 | 1 | : | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350721 | lhfrt | 35072 | LAPLM_G3 | 21 | 1 | 35070 | LAPLM_G1 | 21 | 1 | 1 | : | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350731 | lhfrt | 35073 | LAPLM_G4 | 21 | 1 | 35070 | LAPLM_G1 | 21 | 1 | 1 | : | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343351 | lhfrt | 34335 | LOTUSSFSPV | 0.63 | 1 | 34279 | LOTUSSF | 70 | 1 | 1 | : | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 5000 | 0.2 | 650 | 5000 | 0 | 0 | 0 | 0
3652441 | lhfrt | 365244 | BRNYCRKHYDG | 4.16 | 1 | 30190 | SPI-BRNY | 230 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
350741 | lhfrt | 35074 | SUNRISEPRGT1 | 18 | 1 | : | [5 empty] | #9 | 60 | -2 | -3 | -5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 10 | 0.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350751 | lhfrt | 35075 | SUNRISEPRGT2 | 18 | 1 | : | [5 empty] | #9 | 60 | -2 | -3 | -5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 10 | 0.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350791 | lhfrt | 35079 | SUNRISEPRST | 21 | 1 | : | [5 empty] | #9 | 60 | -2.98 | -5.98 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.45 | 4.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324941 | lhfrt | 32494 | YUBACITYCGN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | -6 | 0 | 0 | 0 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3663621 | lhfrt | 366362 | 10C1398SPV | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.7 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
3651571 | lhfrt | 365157 | ALPAUGH3BESS | 0.48 | 1 | : | [5 empty] | #9 | 60 | 0.6 | -0.6 | 1.6 | -1.6 | -2.2 | -2.7 | 3 | 1.7 | 0 | 0 | 180 | 180 | 30 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
3655341 | lhfrt | 365534 | 40XSOLAR INV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3658381 | lhfrt | 365838 | 6XSOLAR INV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.5 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 0.15 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3658391 | lhfrt | 365839 | 40XBESS INV | 0.69 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
3661071 | lhfrt | 366107 | Q1374BESS1 | 0.505 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0.02 | 30.9 | 185.4 | 185.4 | 7.734 | 0.7834 | 0.3 | 0 | 0 | 0 | 0
3661082 | lhfrt | 366108 | Q1374BESS2 | 0.505 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0.02 | 30.9 | 185.4 | 185.4 | 7.734 | 0.7834 | 0.3 | 0 | 0 | 0 | 0
3661093 | lhfrt | 366109 | Q1374BESS3 | 0.505 | 3 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0.02 | 30.9 | 185.4 | 185.4 | 7.734 | 0.7834 | 0.3 | 0 | 0 | 0 | 0
314351 | lhfrt | 31435 | AIDLINGYSR1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314372 | lhfrt | 31437 | AIDLINGYSR2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350121 | lhfrt | 35012 | ALPAUGHNTH | 0.4 | 1 | 34725 | ALPAUGHNTH | 115 | 1 | 1 | : | #9 | 60 | -10 | -3 | -1.6 | 10 | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 0.0167 | 0.05 | 30 | 0.0167 | 0.05 | 30 | 30 | 30 | 30 | 30 | 0
324641 | lhfrt | 32464 | DUTCHFLAT1PH | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343301 | lhfrt | 34330 | ELNIDO | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346231 | lhfrt | 34623 | EXCLSRSLRSPV | 0.38 | 1 | 34395 | EXCLSRSLR | 115 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0
346362 | lhfrt | 34636 | FRIANTDAM | 6.6 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346363 | lhfrt | 34636 | FRIANTDAM | 6.6 | 3 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346364 | lhfrt | 34636 | FRIANTDAM | 6.6 | 4 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387001 | lhfrt | 38700 | THERMLT1 | 13.8 | 1 | 38630 | THERMLTO | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
387051 | lhfrt | 38705 | THERMLT2 | 13.8 | 1 | 38630 | THERMLTO | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
387101 | lhfrt | 38710 | THERMLT3 | 13.8 | 1 | 38630 | THERMLTO | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
387151 | lhfrt | 38715 | THERMLT4 | 13.8 | 1 | 38630 | THERMLTO | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
38705P | lhfrt | 38705 | THERMLT2 | 13.8 | P | 38630 | THERMLTO | 230 | 1 | 1 | : | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38710P | lhfrt | 38710 | THERMLT3 | 13.8 | P | 38630 | THERMLTO | 230 | 1 | 1 | : | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38715P | lhfrt | 38715 | THERMLT4 | 13.8 | P | 38630 | THERMLTO | 230 | 1 | 1 | : | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343131 | lhfrt | 34313 | NORTHSTARSPV | 0.36 | 1 | 34195 | NORTHSTAR | 115 | 1 | 1 | : | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
329011 | lhfrt | 32901 | OAKLND 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318021 | lhfrt | 31802 | PIT 3 | 11.5 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318023 | lhfrt | 31802 | PIT 3 | 11.5 | 3 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3656941 | lhfrt | 365694 | Q1158SPV1 | 0.64 | 1 | 365691 | Q1158 | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
3656952 | lhfrt | 365695 | Q1158BESS1 | 0.66 | 2 | 365691 | Q1158 | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
3656983 | lhfrt | 365698 | Q1158SPV2 | 0.64 | 3 | 365691 | Q1158 | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
3656994 | lhfrt | 365699 | Q1158BESS2 | 0.66 | 4 | 365691 | Q1158 | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
340501 | lhfrt | 34050 | CHINESESTA | 12.47 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331731 | lhfrt | 33173 | BVISTAWND | 0.6 | 1 | : | [5 empty] | #9 | 60 | 1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3658314 | lhfrt | 365831 | Q877BESS | 0.5 | 4 | : | [5 empty] | #9 | 60 | 10 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0.02 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.02 | 0 | 0 | 0
3659451 | lhfrt | 365945 | AQUAMRWSSPV1 | 0.63 | 1 | 365942 | WSPN | 230 | 1 | 1 | : | #9 | 60 | -1.5 | -3 | 0.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 299.2 | 0.1 | 299.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3659482 | lhfrt | 365948 | AQUAMRWSSPV2 | 0.63 | 2 | 365942 | WSPN | 230 | 1 | 1 | : | #9 | 60 | -1.5 | -3 | 0.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 299.2 | 0.1 | 299.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3666131 | lhfrt | 366613 | Q1495SPV | 0.57 | 1 | : | [5 empty] | #9 | 60 | 2.2 | 2 | -2.8 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 5 | 7.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3666142 | lhfrt | 366614 | Q1495B | 0.57 | 2 | : | [5 empty] | #9 | 60 | 2.2 | 2 | -2.8 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 5 | 7.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
395543 | lhfrt | 39554 | Q1244PVG3 | 0.6 | 3 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
395491 | lhfrt | 39549 | Q1244PVG1 | 0.6 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
3667421 | lhfrt | 366742 | Q1493SPV | 34.5 | 1 | 366740 | Q1493 | 70 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
3667432 | lhfrt | 366743 | Q1493BESS | 34.5 | 2 | 366740 | Q1493 | 70 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
3663941 | lhfrt | 366394 | Q1454B | 0.69 | 1 | 366392 | Q1454 | 115 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0.08 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
3655231 | lhfrt | 365523 | Q1036SPV1 | 34.5 | 1 | 365523 | Q1036SPV1 | 34.5 | 1 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | 0.7 | 2 | 3 | 4 | 0 | 0 | 6550 | 90 | 10 | 0.16 | 6550 | 90 | 5 | 0.16 | 0 | 0 | 0
3655242 | lhfrt | 365524 | Q1036SPV2 | 34.5 | 2 | 365524 | Q1036SPV2 | 34.5 | 2 | 1 | : | #9 | 60 | -0.7 | -2 | -3 | -5 | 0.7 | 2 | 3 | 4 | 0 | 0 | 6550 | 90 | 10 | 0.16 | 6550 | 90 | 5 | 0.16 | 0 | 0 | 0
395554 | lhfrt | 39555 | Q1244BTG4 | 0.69 | 4 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
395502 | lhfrt | 39550 | Q1244BTG2 | 0.69 | 2 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3656092 | lhfrt | 365609 | OAKLANDES2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3661031 | lhfrt | 366103 | Q1374BESS | 0.55 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3657691 | lhfrt | 365769 | Q1116 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3657692 | lhfrt | 365769 | Q1116BESS | 0.55 | 2 | 33928 | CH.STN | 115 | 1 | 1 | : | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.05 | 600 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346541 | lhfrt | 34654 | HENRIETTA_D1 | 12.47 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3662111 | lhfrt | 366211 | Q1363WIND | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2.5 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0.2 | 30 | 180 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0
350841 | lhfrt | 35084 | S653B | 0.48 | 1 | : | [5 empty] | #9 | 60 | -3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350842 | lhfrt | 35084 | S653B | 0.48 | 2 | : | [5 empty] | #9 | 60 | -3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3656972 | lhfrt | 365697 | Q1158B | 0.418 | 2 | 365691 | Q1158 | 230 | : |  |  | #9 | 60 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0 | 30 | 180 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0 | 0
346921 | lhfrt | 34692 | CORCORAN_4 | 12.47 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346951 | lhfrt | 34695 | BLACKWLL_1 | 12.47 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346901 | lhfrt | 34690 | CORCORAN_D3 | 12.47 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346891 | lhfrt | 34689 | OROLOMA_D3 | 12.47 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33208VE | lhfrt | 33208 | MARTIN C | 115 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32018VE | lhfrt | 32018 | GOLDHILL | 115 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34548VE | lhfrt | 34548 | KETTLEMN | 70 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34758VE | lhfrt | 34758 | LAMONT | 115 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36256VE | lhfrt | 36256 | MESA_PGE | 115 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30055VE | lhfrt | 30055 | GATES | 500 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30900VE | lhfrt | 30900 | GATES D | 230 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30479VE | lhfrt | 30479 | BDLSWSTA | 230 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30790VE | lhfrt | 30790 | PANOCHE | 230 | VE | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30005VW | lhfrt | 30005 | ROUND MT | 500 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30567VW | lhfrt | 30567 | LONETREE | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30469VW | lhfrt | 30469 | SHILOH 3 | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30030VW | lhfrt | 30030 | VACA-DIX | 500 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30440VW | lhfrt | 30440 | TULUCAY | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30435VW | lhfrt | 30435 | LAKEVILE | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30330VW | lhfrt | 30330 | RIO OSO | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38630VW | lhfrt | 38630 | THERMLTO | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30114VW | lhfrt | 30114 | DELEVAN | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30110VW | lhfrt | 30110 | GLENN | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36350VW | lhfrt | 36350 | CHOLAME | 70 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31015VW | lhfrt | 31015 | BRDGVLLE | 115 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30765VW | lhfrt | 30765 | LOSBANOS | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30905VW | lhfrt | 30905 | TEMPLETN | 230 | VW | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30055VS | lhfrt | 30055 | GATES | 500 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30790VS | lhfrt | 30790 | PANOCHE | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30825VS | lhfrt | 30825 | MCMULLN1 | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30875VS | lhfrt | 30875 | MC CALL | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30881VS | lhfrt | 30881 | HENRIETA | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30873VS | lhfrt | 30873 | HELM | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30900VS | lhfrt | 30900 | GATES D | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
34758VS | lhfrt | 34758 | LAMONT | 115 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30994VS | lhfrt | 30994 | WHEELER | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30940VS | lhfrt | 30940 | STCKDLEA | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
34762VS | lhfrt | 34762 | RENFRO | 115 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30970VS | lhfrt | 30970 | MIDWAY-E | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
30935VS | lhfrt | 30935 | ARCO | 230 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
36256VS | lhfrt | 36256 | MESA_PGE | 115 | VS | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.1 | 0.1 | 6550 | 90 | 5 | 0.1 | 0.1 | 0
358531 | lhfrt | 35853 | GROYPKR3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329033 | lhfrt | 32903 | OAKLAND3GT | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318541 | lhfrt | 31854 | OLSENHYDRO | 4.16 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331781 | lhfrt | 33178 | RVEC_GEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324961 | lhfrt | 32496 | YCEC | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369122 | lhfrt | 36912 | HLSolar | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3656831 | lhfrt | 365683 | Q1103SPV | 34.5 | 1 | 365681 | Q1103 | 115 | 1 | : |  | #9 | 60 | -1.5 | -3 | 0.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 299.2 | 0.1 | 299.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346673 | lhfrt | 34667 | Q877PH3 | 0.6 | 3 | : | [5 empty] | #9 | 60 | -5 | -4 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 1 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 1
325001 | lhfrt | 32500 | ULTR RCK | 12.47 | 1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
358501 | lhfrt | 35850 | GILROYENGCT | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | -3 | -5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 60 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358712 | lhfrt | 35871 | GILROYENGST | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2 | -3 | -5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 62 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3667111 | lhfrt | 366711 | Q1472BESS1 | 34.5 | 1 | 366700 | Q1472 | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
3667122 | lhfrt | 366712 | Q1472BESS2 | 34.5 | 2 | 366700 | Q1472 | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
3667133 | lhfrt | 366713 | Q1472BESS3 | 34.5 | 3 | 366700 | Q1472 | 500 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.1 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
3667154 | lhfrt | 366715 | Q1472BESS4 | 0.63 | 4 | 366700 | Q1472 | 500 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -3 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 5.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344311 | lhfrt | 34431 | GWF_HEP1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344331 | lhfrt | 34433 | GWF_HEP2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353041 | lhfrt | 35304 | RUSCTYECCT1 | 15 | 1 | : | [5 empty] | #9 | 60 | -3.61 | -3.2 | -2.5 | 3.01 | 2.11 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.117 | 10 | 0.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
353052 | lhfrt | 35305 | RUSCTYECCT2 | 15 | 2 | : | [5 empty] | #9 | 60 | -3.61 | -3.2 | -2.5 | 3.01 | 2.11 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.117 | 10 | 0.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
353063 | lhfrt | 35306 | RUSCTYECST1 | 18 | 3 | : | [5 empty] | #9 | 60 | -3.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387201 | lhfrt | 38720 | PINEFLATPH | 13.8 | 1 | 30871 | PINEFLT | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 0.6 | -0.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387202 | lhfrt | 38720 | PINEFLATPH | 13.8 | 2 | 30871 | PINEFLT | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 0.6 | -0.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387203 | lhfrt | 38720 | PINEFLATPH | 13.8 | 3 | 30871 | PINEFLT | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 0.6 | -0.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381231 | lhfrt | 38123 | LODIECCT | 16.5 | 1 | : | [5 empty] | #9 | 60 | -2.4 | -2 | -1.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 30 | 90 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381241 | lhfrt | 38124 | LODIECST | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.4 | -2 | -1.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 30 | 90 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343281 | lhfrt | 34328 | STRWDPNCHGT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343292 | lhfrt | 34329 | STRWDPNCHGT2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381061 | lhfrt | 38106 | NCPA1GY1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
381081 | lhfrt | 38108 | NCPA1GY2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
381101 | lhfrt | 38110 | NCPA2GY1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
381121 | lhfrt | 38112 | NCPA2GY2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
321561 | lhfrt | 32156 | WOODLANDBIOM | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2.9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350661 | lhfrt | 35066 | PSE-BEAR | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.05 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340581 | lhfrt | 34058 | DONNELLS | 13.8 | 1 | : | [5 empty] | #9 | 60 | 63 | 58.4 | 56.5 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 120 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350291 | lhfrt | 35029 | BADGERCK | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0.05 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358601 | lhfrt | 35860 | AGNEWCOGEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362041 | lhfrt | 36204 | AERA_12 | 12 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362042 | lhfrt | 36204 | AERA_12 | 12 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35310RT | lhfrt | 35310 | LFC FIN+ | 9.11 | RT | : | [5 empty] | #9 | 60 | -0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331751 | lhfrt | 33175 | ALTAMONT | 9.11 | 1 | : | [5 empty] | #9 | 60 | -0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353181 | lhfrt | 35318 | FLOWDPTR | 9.11 | 1 | : | [5 empty] | #9 | 60 | -0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338101 | lhfrt | 33810 | RIPONCOGEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1 | -1.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321811 | lhfrt | 32181 | SHILOH1WIND | 0.575 | 1 | 30477 | SHILOH1 | 230 | 1 | 1 | : | #9 | 60 | -3.6 | -3 | 1.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350011 | lhfrt | 35001 | ALPAUGHN_50S | 0.4 | 1 | 34711 | ALPAUGHSTH | 115 | : |  |  | #9 | 60 | -3 | -1.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 30 | 30 | 0.16 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
3656081 | lhfrt | 365608 | FRICKWIND | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314012 | lhfrt | 31401 | SANTAFESTG2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314001 | lhfrt | 31400 | SANTAFESTG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331881 | lhfrt | 33188 | MARSHCT1 | 16.5 | 1 | : | [5 empty] | #9 | 60 | -4.6 | -3 | 1.8 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331892 | lhfrt | 33189 | MARSHCT2 | 16.5 | 2 | : | [5 empty] | #9 | 60 | -4.6 | -3 | 1.8 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331903 | lhfrt | 33190 | MARSHCT3 | 16.5 | 3 | : | [5 empty] | #9 | 60 | -4.6 | -3 | 1.8 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331914 | lhfrt | 33191 | MARSHCT4 | 16.5 | 4 | : | [5 empty] | #9 | 60 | -4.6 | -3 | 1.8 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331071 | lhfrt | 33107 | DEC STG1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 0.6 | -1.9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331081 | lhfrt | 33108 | DEC CTG1 | 18 | 1 | : | [5 empty] | #9 | 60 | 6 | 2.1 | 1.7 | -1.81 | -2.2 | -2.7 | -3.2 | 0 | 0 | 0 | 0.1 | 60 | 1 | 30 | 7.5 | 0.75 | 0.13 | 0 | 0 | 0 | 0
331091 | lhfrt | 33109 | DEC CTG2 | 18 | 1 | : | [5 empty] | #9 | 60 | 6 | 2.1 | 1.7 | -1.81 | -2.2 | -2.7 | -3.2 | 0 | 0 | 0 | 0.1 | 60 | 1 | 30 | 7.5 | 0.75 | 0.13 | 0 | 0 | 0 | 0
331101 | lhfrt | 33110 | DEC CTG3 | 18 | 1 | : | [5 empty] | #9 | 60 | 6 | 2.1 | 1.7 | -1.81 | -2.2 | -2.7 | -3.2 | 0 | 0 | 0 | 0.1 | 60 | 1 | 30 | 7.5 | 0.75 | 0.13 | 0 | 0 | 0 | 0
314061 | lhfrt | 31406 | GEYSR5-6 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314062 | lhfrt | 31406 | GEYSR5-6 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314081 | lhfrt | 31408 | GEYSER78 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314082 | lhfrt | 31408 | GEYSER78 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314121 | lhfrt | 31412 | GEYSER11 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.7 | -0.7 | 1.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 0.03 | 30 | 180 | 0 | 0 | 0 | 0 | 0
314141 | lhfrt | 31414 | GEYSER12 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.7 | -0.7 | 1.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 0.03 | 30 | 180 | 0 | 0 | 0 | 0 | 0
314161 | lhfrt | 31416 | GEYSER13 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314201 | lhfrt | 31420 | GEYSER16 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314221 | lhfrt | 31422 | GEYSER17 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.7 | -0.7 | 1.8 | 1.7 | 0.7 | 0 | 0 | 0 | 0 | 0.03 | 30 | 180 | 0.03 | 30 | 180 | 0 | 0 | 0 | 0 | 0
314241 | lhfrt | 31424 | GEYSER18 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314261 | lhfrt | 31426 | GEYSER20 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358541 | lhfrt | 35854 | LECEFGT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358551 | lhfrt | 35855 | LECEFGT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358561 | lhfrt | 35856 | LECEFGT3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358571 | lhfrt | 35857 | LECEFGT4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358581 | lhfrt | 35858 | LECEFST1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | -3 | 1.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.05 | 180 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321731 | lhfrt | 32173 | LAMBIE | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321743 | lhfrt | 32174 | GOOSEHGT | 13.8 | 3 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321752 | lhfrt | 32175 | CREED | 13.8 | 2 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343011 | lhfrt | 34301 | CHOWCOGN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3656631 | lhfrt | 365663 | Q1127SPVG | 34.5 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | -0.7 | 0.7 | 2 | 3 | 4 | 0 | 0 | 0.01 | 10 | 90 | 6550 | 6550 | 90 | 5 | 0.01 | 0 | 0 | 0
318961 | lhfrt | 31896 | SPIQUINCY | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338131 | lhfrt | 33813 | MARIPCT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338152 | lhfrt | 33815 | MARIPCT2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338173 | lhfrt | 33817 | MARIPCT3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338194 | lhfrt | 33819 | MARIPCT4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325021 | lhfrt | 32502 | DTCHFLT2 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350541 | lhfrt | 35054 | REDCRESTSPV | 0.36 | 1 | : | [5 empty] | #9 | 60 | -3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350591 | lhfrt | 35059 | HAYWORTHSPV | 0.36 | 1 | : | [5 empty] | #9 | 60 | -3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350871 | lhfrt | 35087 | WOODMERESPV | 0.36 | 1 | : | [5 empty] | #9 | 60 | -3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3655931 | lhfrt | 365593 | Q1010WIND | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
3655141 | lhfrt | 365514 | TRNQ8AMRSPV | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.1 | 30.1 | 0.2 | 180.1 | 30.1 | 7.6 | 0.84 | 0.2 | 0 | 0 | 0
3655172 | lhfrt | 365517 | TRNQ8AZLSPV | 0.55 | 2 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.1 | 30.1 | 0.2 | 180.1 | 30.1 | 7.6 | 0.84 | 0.2 | 0 | 0 | 0
3655203 | lhfrt | 365520 | TRNQ8RJOSPV | 0.55 | 3 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.1 | 30.1 | 0.2 | 180.1 | 30.1 | 7.6 | 0.84 | 0.2 | 0 | 0 | 0
3655264 | lhfrt | 365526 | TRNQ8VRDSPV | 0.55 | 4 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.1 | 30.1 | 0.2 | 180.1 | 30.1 | 7.6 | 0.84 | 0.2 | 0 | 0 | 0
340551 | lhfrt | 34055 | SPISONORA | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 8 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346441 | lhfrt | 34644 | BRFRDGFENSPV | 0.55 | 1 | 34470 | GIFFEN | 70 | 1 | 1 | : | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | -5 | 0.6 | 1.6 | 3 | 5 | 181.82 | 30.8219 | 7.7855 | 0.78534 | 60 | 1e-05 | 178.22 | 29.2208 | 60 | 1e-05 | 0
3655631 | lhfrt | 365563 | SKICSPV | 0.36 | 1 | 34978 | SKIC10 | 70 | 1 | 1 | : | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
362121 | lhfrt | 36212 | Q705SPV | 0.38 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
340531 | lhfrt | 34053 | CRWCRKSLR1G | 0.8 | 1 | 34011 | CRWCRKSLR1 | 60 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
350981 | lhfrt | 35098 | WHITERVRW | 0.48 | 1 | 34747 | WHITERVRJCT | 115 | 1 | 1 | : | #9 | 60 | -10 | -3 | 10 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 0.0167 | 0.0167 | 0.0167 | 0.2167 | 0.2167 | 0.2167 | 0.2167 | 0.2167 | 0.2167 | 0.2167 | 0
327411 | lhfrt | 32741 | HILLSIDE_12 | 12.47 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327412 | lhfrt | 32741 | HILLSIDE_12 | 12.47 | 2 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3466312 | lhfrt | 34663 | Q877PH12 | 0.39 | 12 | : | [5 empty] | #9 | 60 | -0.6 | -3.5 | 1.7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350221 | lhfrt | 35022 | MRCPAWESTSPV | 0.385 | 1 | 34877 | MRCPAWEST | 70 | : |  |  | #9 | 60 | 1.7 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346831 | lhfrt | 34683 | MUSTANGSPV1 | 0.38 | 1 | : | [5 empty] | #9 | 60 | 5 | 2.2 | -0.8 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 180 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3653253 | lhfrt | 365325 | MUSTANGSPV3 | 0.38 | 3 | : | [5 empty] | #9 | 60 | 5 | 2.2 | -0.8 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 180 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3653274 | lhfrt | 365327 | MUSTANGSPV4 | 0.38 | 4 | : | [5 empty] | #9 | 60 | 5 | 2.2 | -0.8 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 180 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317501 | lhfrt | 31750 | SPIANDERSON2 | 12.5 | 1 | 31473 | SPIANDERSON2 | 115 | 1 | 1 | : | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 3 | -1.6 | -2 | -2.4 | 3 | -3 | 0.5 | 90 | 30 | 7.5 | 0.5 | 90 | 30 | 7.5 | 0.5 | 90 | 0
3653641 | lhfrt | 365364 | PUMPJACKSPV | 0.8 | 1 | 365361 | PUMPJACK | 115 | 1 | 1 | : | #9 | 60 | -3 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.1 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3653741 | lhfrt | 365374 | WILDWOOD1SPV | 0.8 | 1 | 365371 | WILDWOOD1 | 115 | 1 | 1 | : | #9 | 60 | -3 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.1 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350951 | lhfrt | 35095 | MORELS | 0.406 | 1 | 34907 | MORELS | 70 | 1 | 1 | : | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
350421 | lhfrt | 35042 | RIOBRAVO1SPV | 0.38 | 1 | 34818 | RIOBRAVO1 | 115 | 1 | 1 | : | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350471 | lhfrt | 35047 | WILDWOOD2 | 0.38 | 1 | 34819 | WILDWOOD2 | 115 | 1 | 1 | : | #9 | 60 | -5 | -2.7 | -2.2 | -1.6 | -0.6 | 5 | 1.6 | 0.6 | 0 | 0 | 0 | 0.78534 | 7.7855 | 30.8219 | 181.82 | 0 | 29.2208 | 178.22 | 0 | 0 | 0
346661 | lhfrt | 34666 | KANSASSTHSPV | 0.42 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350911 | lhfrt | 35091 | OLDRIVER1SPV | 0.69 | 1 | 34976 | OLDRIVER1 | 70 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0.04 | 31 | 180 | 0.75 | 7.5 | 31 | 180 | 0 | 0 | 0 | 0
346941 | lhfrt | 34694 | KENTSTH-SPV | 0.69 | 1 | 34569 | KENTSTH | 70 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0.04 | 31 | 180 | 0.75 | 7.5 | 31 | 180 | 0 | 0 | 0 | 0
342651 | lhfrt | 34265 | AVENALPARKSL | 0.3 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342631 | lhfrt | 34263 | SANDDRAG | 0.3 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342571 | lhfrt | 34257 | SUNCITY | 0.3 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364511 | lhfrt | 36451 | HRW .6W1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364532 | lhfrt | 36453 | HRW .6W2 | 0.69 | 2 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364553 | lhfrt | 36455 | HRW .6W3 | 0.69 | 3 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364574 | lhfrt | 36457 | HRW .6W4 | 0.69 | 4 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311521 | lhfrt | 31152 | PAC.LUMB | 13.8 | 1 | : | [5 empty] | #9 | 60 | -4.98 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311522 | lhfrt | 31152 | PAC.LUMB | 13.8 | 2 | : | [5 empty] | #9 | 60 | -4.98 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311533 | lhfrt | 31153 | PAC.LUMB | 2.4 | 3 | : | [5 empty] | #9 | 60 | -4.98 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343261 | lhfrt | 34326 | PANOCHEECCT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343272 | lhfrt | 34327 | PANOCHEECCT2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343363 | lhfrt | 34336 | PANOCHEECCT3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 1.7 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343414 | lhfrt | 34341 | PANOCHEECCT4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 1.7 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381141 | lhfrt | 38114 | STIG CC | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
343201 | lhfrt | 34320 | MCSWAIN | 4.16 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311811 | lhfrt | 31181 | HMBOBAYPPA | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311812 | lhfrt | 31181 | HMBOBAYPPA | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311813 | lhfrt | 31181 | HMBOBAYPPA | 13.8 | 3 | : | [5 empty] | #9 | 60 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311828 | lhfrt | 31182 | HMBOBAYPPC | 13.8 | 8 | : | [5 empty] | #9 | 60 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311829 | lhfrt | 31182 | HMBOBAYPPC | 13.8 | 9 | : | [5 empty] | #9 | 60 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3118210 | lhfrt | 31182 | HMBOBAYPPC | 13.8 | 10 | : | [5 empty] | #9 | 60 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381021 | lhfrt | 38102 | COLLRVL1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381041 | lhfrt | 38104 | COLLRVL2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341421 | lhfrt | 34142 | WHD_PAN2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -5 | -3 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.2 | 10 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318063 | lhfrt | 31806 | PIT5U3U4 | 11.5 | 3 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318064 | lhfrt | 31806 | PIT5U3U4 | 11.5 | 4 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317721 | lhfrt | 31772 | PIT 6 U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317741 | lhfrt | 31774 | PIT 6 U2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324901 | lhfrt | 32490 | GREENLF1CTG1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 50 | 160 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324912 | lhfrt | 32491 | GREENLF1CTG2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 50 | 160 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338201 | lhfrt | 33820 | WESTPOINTPH | 11.5 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318981 | lhfrt | 31898 | DE SABLA | 6.9 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364121 | lhfrt | 36412 | DIABLO 2 | 25 | 1 | : | [5 empty] | #9 | 60 | -1.65 | -2.05 | -2.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 31 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346083 | lhfrt | 34608 | AGRICO | 13.8 | 3 | : | [5 empty] | #9 | 60 | 4 | 3.1 | -2.7 | -2.1 | -2.5 | -3.1 | -6 | 0 | 0 | 0 | 0.51 | 0.51 | 2.02 | 30 | 7.53 | 60.08 | 0.53 | 0 | 0 | 0 | 0
346084 | lhfrt | 34608 | AGRICO | 13.8 | 4 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3657065 | lhfrt | 365706 | WHD_BESS | 0.69 | 5 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
346001 | lhfrt | 34600 | HELMS 1 | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346021 | lhfrt | 34602 | HELMS 2 | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346041 | lhfrt | 34604 | HELMS 3 | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364111 | lhfrt | 36411 | DIABLOCNYN1 | 25 | 1 | : | [5 empty] | #9 | 60 | -1.65 | -2.05 | -2.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 31 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350261 | lhfrt | 35026 | KERNFRNTLTD | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350262 | lhfrt | 35026 | KERNFRNTLTD | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -3 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317861 | lhfrt | 31786 | ROCK CK1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317881 | lhfrt | 31788 | ROCK CK2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321501 | lhfrt | 32150 | CALPEAKVACA | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341861 | lhfrt | 34186 | CALPEAKPNCHE | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362031 | lhfrt | 36203 | KNGCTYCGNCTG | 13.8 | 1 | 36077 | KNGCTYCGN | 60 | 1 | 1 | : | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
362022 | lhfrt | 36202 | KNGCTYCGNSTG | 13.8 | 2 | 36077 | KNGCTYCGN | 60 | 1 | 1 | : | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
318341 | lhfrt | 31834 | KELLYRIDGEPH | 4.16 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324501 | lhfrt | 32450 | COLGATE1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324521 | lhfrt | 32452 | COLGATE2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343221 | lhfrt | 34322 | MERCEDFALLS | 12.5 | 1 | : | [5 empty] | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346161 | lhfrt | 34616 | KINGSRIV | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338221 | lhfrt | 33822 | TIGR CRK | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3655862 | lhfrt | 365586 | Q829P3SPV | 0.418 | 2 | : | [5 empty] | #9 | 60 | 3 | 2 | 1 | -1 | -2 | -3 | 0 | 0 | 0 | 0 | 0.03 | 5 | 190 | 190 | 60 | 0.03 | 0 | 0 | 0 | 0 | 0
318401 | lhfrt | 31840 | BLCKBUTT | 9.11 | 1 | : | [5 empty] | #9 | 60 | -5.75 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318421 | lhfrt | 31842 | CSC HYDR | 9.11 | 1 | : | [5 empty] | #9 | 60 | -5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318422 | lhfrt | 31842 | CSC HYDR | 9.11 | 2 | : | [5 empty] | #9 | 60 | -5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321881 | lhfrt | 32188 | MONTEZUMAW | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331021 | lhfrt | 33102 | 4C687 | 0.31 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340531 | lhfrt | 34053 | Q539 | 0.8 | 1 | 34009 | Q539SS | 60 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
343141 | lhfrt | 34314 | S548 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343151 | lhfrt | 34315 | ADAMSEASTSPV | 0.69 | 1 | 34277 | ADAMSEAST | 70 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 0.04 | 31 | 180 | 0.75 | 7.5 | 31 | 180 | 0 | 0 | 0 | 0
343491 | lhfrt | 34349 | CANTUA_DIST | 12.47 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343492 | lhfrt | 34349 | CANTUA_DIST | 12.47 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343531 | lhfrt | 34353 | SCHINDLER_D | 12.47 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343532 | lhfrt | 34353 | SCHINDLER_D | 12.47 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343533 | lhfrt | 34353 | SCHINDLER_D | 12.47 | 3 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343534 | lhfrt | 34353 | SCHINDLER_D | 12.47 | 4 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344618 | lhfrt | 34461 | GUERNSEY_D1 | 12.47 | 8 | : | [5 empty] | #9 | 60 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344635 | lhfrt | 34463 | GUERNSEY_D2 | 12.47 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344671 | lhfrt | 34467 | GIFFEN_DIST | 12.47 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345571 | lhfrt | 34557 | HURON_DIST | 12.47 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345572 | lhfrt | 34557 | HURON_DIST | 12.47 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345631 | lhfrt | 34563 | STROUD_DIST | 12.47 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345632 | lhfrt | 34563 | STROUD_DIST | 12.47 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346131 | lhfrt | 34613 | GATES_DIST | 12.47 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346132 | lhfrt | 34613 | GATES_DIST | 12.47 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346133 | lhfrt | 34613 | GATES_DIST | 12.47 | 3 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346171 | lhfrt | 34617 | Q581 | 0.385 | 1 | 34678 | Q581C1 | 34.5 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -4 | -4 | 0.7 | 2 | 3 | 4 | 4 | 1000 | 200 | 40 | 5 | 5 | 1000 | 200 | 40 | 2 | 2 | 0
346391 | lhfrt | 34639 | S633 | 0.48 | 1 | : | [5 empty] | #9 | 60 | -0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346421 | lhfrt | 34642 | KINGSBUR | 13.8 | 1 | 34386 | KNGSCOGN | 115 | : |  |  | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346422 | lhfrt | 34642 | KINGSBUR | 13.8 | 2 | 34386 | KNGSCOGN | 115 | : |  |  | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346491 | lhfrt | 34649 | Q965 | 0.55 | 1 | 34438 | Q581 | 115 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.008334 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
346531 | lhfrt | 34653 | Q526 | 0.55 | 1 | 34561 | Q526TP | 70 | 1 | 1 | : | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 30 | 180 | 0 | 0 | 0
346731 | lhfrt | 34673 | Q532 | 0.55 | 1 | 34567 | FIVEPOINTSSS | 70 | 1 | 1 | : | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 30 | 180 | 0 | 0 | 0
346771 | lhfrt | 34677 | C0558 | 21 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346801 | lhfrt | 34680 | RE Kansas | 115 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
346881 | lhfrt | 34688 | Q272 | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
350191 | lhfrt | 35019 | 2C559 | 0.48 | 1 | : | [5 empty] | #9 | 60 | -3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350821 | lhfrt | 35082 | S621A | 0.44 | 1 | : | [5 empty] | #9 | 60 | -3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350891 | lhfrt | 35089 | Q653EA | 0.48 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350924 | lhfrt | 35092 | Q744P4G4 | 0.6 | 4 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 0.5 | 1.7 | 1.5 | 180 | 30 | 7.6 | 0.76 | 0.1 | 180 | 30 | 0.16 | 0.1 | 0.05 | 0
3655262 | lhfrt | 365526 | BARBARO_LV | 0.66 | 2 | 365526 | BARBARO_LV | 0.66 | 2 | 1 | : | #9 | 60 | 3.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365547RN | lhfrt | 365547 | 1257-RD | 0.385 | RN | 365544 | 1257-RD | 70 | : |  |  | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
3655661 | lhfrt | 365566 | SOLANO1WIND | 0.69 | 1 | 365566 | SOLANO1WIND | 0.69 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3655742 | lhfrt | 365574 | SOLANO2WIND | 1 | 2 | 30480 | SLNO-WND | 230 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
3656003 | lhfrt | 365600 | SOLANO3WIND | 1 | 3 | 30480 | RUSSELLSMUD | 230 | : |  |  | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 180 | 30 | 0 | 0 | 0 | 0
3656241 | lhfrt | 365624 | Q356SPV | 0.6 | 1 | : | [5 empty] | #9 | 60 | -7 | -7.6 | -8.2 | -8.7 | -9 | 7 | 7.6 | 7.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.05 | 180 | 30 | 0.05 | 0 | 0 | 0
3656591 | lhfrt | 365659 | ADOBESLRSPV | 0.36 | 1 | 365656 | ADOBESLR | 115 | : |  |  | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
368581 | lhfrt | 36858 | Gia100 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368951 | lhfrt | 36895 | Gia200 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373141 | lhfrt | 37314 | ROBBS PK | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373051 | lhfrt | 37305 | JAYBIRD1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373061 | lhfrt | 37306 | JAYBIRD2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | 1.7 | -3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 30 | 120 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373081 | lhfrt | 37308 | LOON LK | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373071 | lhfrt | 37307 | JONESFRK | 4.16 | 1 | : | [5 empty] | #9 | 60 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373221 | lhfrt | 37322 | COSUMNE2 | 18 | 1 | : | [5 empty] | #9 | 60 | 6 | 5 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.02 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373231 | lhfrt | 37323 | COSUMNE3 | 18 | 1 | : | [5 empty] | #9 | 60 | 6 | 5 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.02 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373211 | lhfrt | 37321 | COSUMNE1 | 16.5 | 1 | : | [5 empty] | #9 | 60 | 1.8 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373101 | lhfrt | 37310 | PROCTER1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.2 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373111 | lhfrt | 37311 | PROCTER2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.2 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373121 | lhfrt | 37312 | PROCTER3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.2 | -1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373151 | lhfrt | 37315 | SRWTPA | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2.5 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5 | 1.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373152 | lhfrt | 37315 | SRWTPA | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2.4 | 1.8 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373161 | lhfrt | 37316 | SRWTPB | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.95 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373091 | lhfrt | 37309 | MCCLELLN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373031 | lhfrt | 37303 | CAMPBEL1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | 2 | -2.9 | -2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 1 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373041 | lhfrt | 37304 | CAMPBEL2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 4.8 | -1.5 | -2.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 7.5 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379401 | lhfrt | 37940 | RDGCT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379411 | lhfrt | 37941 | RDGCT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379421 | lhfrt | 37942 | RDGCT3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379441 | lhfrt | 37944 | RDGSTEAM | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379581 | lhfrt | 37958 | RDGCT4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380711 | lhfrt | 38071 | REP1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380792 | lhfrt | 38079 | REP2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380803 | lhfrt | 38080 | REP3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | -1 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383511 | lhfrt | 38351 | RIPN_1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383531 | lhfrt | 38353 | RIPN_2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383561 | lhfrt | 38356 | WOODLMID | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.7 | -0.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 180 | 0.03 | 180 | 7.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0
383571 | lhfrt | 38357 | WOODLMID | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383572 | lhfrt | 38357 | WOODLMID | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383651 | lhfrt | 38365 | N.HGN DM | 12 | 1 | : | [5 empty] | #9 | 60 | 3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383652 | lhfrt | 38365 | N.HGN DM | 12 | 2 | : | [5 empty] | #9 | 60 | 3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383701 | lhfrt | 38370 | WOD3A | 13.8 | 1 | : | [5 empty] | #9 | 60 | 9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383711 | lhfrt | 38371 | WOD3B | 13.8 | 1 | : | [5 empty] | #9 | 60 | 9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383721 | lhfrt | 38372 | WOD3C | 13.8 | 1 | : | [5 empty] | #9 | 60 | 9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383731 | lhfrt | 38373 | WOD3D | 13.8 | 1 | : | [5 empty] | #9 | 60 | 9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383741 | lhfrt | 38374 | WOD3E | 13.8 | 1 | : | [5 empty] | #9 | 60 | 9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383751 | lhfrt | 38375 | WOD3F | 13.8 | 1 | : | [5 empty] | #9 | 60 | 9 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383801 | lhfrt | 38380 | MTHSE_G | 0.315 | 1 | : | [5 empty] | #9 | 60 | 5 | 0.5 | -0.7 | 0 | -3 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.16 | 0.16 | 0.16 | 0.1 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
387501 | lhfrt | 38750 | DOS AMG1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387502 | lhfrt | 38750 | DOS AMG1 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387503 | lhfrt | 38750 | DOS AMG1 | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387551 | lhfrt | 38755 | DOS AMG2 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387552 | lhfrt | 38755 | DOS AMG2 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387553 | lhfrt | 38755 | DOS AMG2 | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3876010 | lhfrt | 38760 | DELTA E | 13.2 | 10 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3876011 | lhfrt | 38760 | DELTA E | 13.2 | 11 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387658 | lhfrt | 38765 | DELTA D | 13.2 | 8 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387659 | lhfrt | 38765 | DELTA D | 13.2 | 9 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387706 | lhfrt | 38770 | DELTA C | 13.2 | 6 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387707 | lhfrt | 38770 | DELTA C | 13.2 | 7 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387751 | lhfrt | 38775 | BUENAVS1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387752 | lhfrt | 38775 | BUENAVS1 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387753 | lhfrt | 38775 | BUENAVS1 | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387754 | lhfrt | 38775 | BUENAVS1 | 13.2 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387755 | lhfrt | 38775 | BUENAVS1 | 13.2 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387756 | lhfrt | 38775 | BUENAVS1 | 13.2 | 6 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387801 | lhfrt | 38780 | BUENAVS2 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387802 | lhfrt | 38780 | BUENAVS2 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387803 | lhfrt | 38780 | BUENAVS2 | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387804 | lhfrt | 38780 | BUENAVS2 | 13.2 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387851 | lhfrt | 38785 | WHLR RD1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387852 | lhfrt | 38785 | WHLR RD1 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387853 | lhfrt | 38785 | WHLR RD1 | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387854 | lhfrt | 38785 | WHLR RD1 | 13.2 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387855 | lhfrt | 38785 | WHLR RD1 | 13.2 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387901 | lhfrt | 38790 | WHLR RD2 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387902 | lhfrt | 38790 | WHLR RD2 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387903 | lhfrt | 38790 | WHLR RD2 | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387904 | lhfrt | 38790 | WHLR RD2 | 13.2 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387951 | lhfrt | 38795 | WINDGAP1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387952 | lhfrt | 38795 | WINDGAP1 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387953 | lhfrt | 38795 | WINDGAP1 | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388001 | lhfrt | 38800 | WINDGAP2 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388002 | lhfrt | 38800 | WINDGAP2 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388051 | lhfrt | 38805 | WINDGAP3 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388052 | lhfrt | 38805 | WINDGAP3 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388101 | lhfrt | 38810 | WINDGAP4 | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388102 | lhfrt | 38810 | WINDGAP4 | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388154 | lhfrt | 38815 | DELTA B | 13.2 | 4 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388155 | lhfrt | 38815 | DELTA B | 13.2 | 5 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388201 | lhfrt | 38820 | DELTA A | 13.2 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388202 | lhfrt | 38820 | DELTA A | 13.2 | 2 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388203 | lhfrt | 38820 | DELTA A | 13.2 | 3 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388301 | lhfrt | 38830 | HYATT 2 | 12.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388401 | lhfrt | 38840 | HYATT 4 | 12.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388501 | lhfrt | 38850 | HYATT 6 | 12.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358821 | lhfrt | 35882 | MEC CTG2 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.01 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.01 | 0 | 0 | 0
358831 | lhfrt | 35883 | MEC STG1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.01 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.01 | 0 | 0 | 0
3656741 | lhfrt | 365674 | Q1128 | 0.55 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | -0.7 | 0.7 | 2 | 3 | 4 | 0 | 0 | 0.01 | 10 | 90 | 6550 | 6550 | 90 | 5 | 0.01 | 0 | 0 | 0
385441 | lhfrt | 38544 | ALMCT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385451 | lhfrt | 38545 | ALMCT3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385461 | lhfrt | 38546 | ALMCT4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385601 | lhfrt | 38560 | LA GRNGE | 4.16 | 1 | 38456 | LA GRNGE | 69 | 1 | 1 | : | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.01 | 180 | 30 | 0.01 | 0 | 0 | 0
385621 | lhfrt | 38562 | DAWSON | 4.16 | 1 | 38484 | DAWSON | 69 | 1 | 1 | : | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.01 | 180 | 30 | 0.01 | 0 | 0 | 0
385641 | lhfrt | 38564 | ALMONDCT | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 7.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385701 | lhfrt | 38570 | WEC1-CT | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.1 | 180 | 30 | 0 | 0 | 0 | 0 | 0
385741 | lhfrt | 38574 | WEC2-CT | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.1 | 180 | 30 | 0 | 0 | 0 | 0 | 0
3655851 | lhfrt | 365585 | Q829SPV1 | 0.42 | 1 | 365580 | Q829 | 230 | : |  |  | #9 | 60 | 3 | 2 | 1 | -1 | -2 | -3 | 0 | 0 | 0 | 0 | 0.1 | 5 | 180 | 180 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0
3655862 | lhfrt | 365586 | Q829SPV2 | 0.42 | 2 | 365580 | Q829 | 230 | : |  |  | #9 | 60 | 3 | 2 | 1 | -1 | -2 | -3 | 0 | 0 | 0 | 0 | 0.1 | 5 | 180 | 180 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0
3656751 | lhfrt | 365675 | Q1128-5SPVG | 34.5 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | -0.7 | 0.7 | 2 | 3 | 4 | 0 | 0 | 0.01 | 10 | 90 | 6550 | 6550 | 90 | 5 | 0.01 | 0 | 0 | 0
3659361 | lhfrt | 365936 | Q653FSPV1 | 0.12 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
366367RE | lhfrt | 366367 | 1501-WD | 70 | RE | : | [5 empty] | #9 | 60 | -0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365629FW | lhfrt | 365629 | 1320-WD | 12 | FW | 39740 | 1320-WD | 115 | : |  |  | #9 | 60 | 0.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 1
3656731 | lhfrt | 365673 | Q1128-4SPVG | 34.5 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | -0.7 | 0.7 | 2 | 3 | 4 | 0 | 0 | 0.01 | 10 | 90 | 6550 | 6550 | 90 | 5 | 0.01 | 0 | 0 | 0
3659402 | lhfrt | 365940 | Q653FSPV2 | 0.12 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
3659383 | lhfrt | 365938 | Q653FC6BESS | 0.48 | 3 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
382071 | lhfrt | 38207 | MCH_PV_1 | 0.34 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
350651 | lhfrt | 35065 | 7STNDRD_DIST | 21.6 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314301 | lhfrt | 31430 | SONOMAPPGEO | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343251 | lhfrt | 34325 | Q577 | 0.34 | 1 | : | [5 empty] | #9 | 60 | 3 | 1.7 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 2 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350271 | lhfrt | 35027 | HIGHSIERRA | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350272 | lhfrt | 35027 | HIGHSIERRA | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346461 | lhfrt | 34646 | SANGERCGN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346462 | lhfrt | 34646 | SANGERCGN | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338051 | lhfrt | 33805 | GWFTRCY1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338071 | lhfrt | 33807 | GWFTRCY2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -5 | -3 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 60 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338111 | lhfrt | 33811 | GWFTRCY3 | 18 | 1 | : | [5 empty] | #9 | 60 | -2.4 | -2 | -1.6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 30 | 90 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350241 | lhfrt | 35024 | DEXZEL | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317981 | lhfrt | 31798 | BRNYFRST | 13.2 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 3 | 180 | 30 | 7.5 | 0.3 | 0.008334 | 0.008334 | 0.008334 | 0
321941 | lhfrt | 32194 | SHILOH4WIND | 0.57 | 1 | : | [5 empty] | #9 | 60 | -0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321941 | lhfrt | 32194 | SHILOH4WIND | 0.57 | 1 | 32192 | SHILOH4C1 | 34.5 | 1 | 1 | : | #9 | 60 | -3 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 0.0333 | 7.5 | 30 | 180 | 180 | 0.0333 | 0 | 0 | 0 | 0 | 0
3657731 | lhfrt | 365773 | BDES-BESS | 0.69 | 1 | 365770 | BDES-STA | 230 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0 | 0 | 0
350201 | lhfrt | 35020 | RIOBRAVO | 6.9 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
350202 | lhfrt | 35020 | RIOBRAVO | 6.9 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
327411 | lhfrt | 32741 | HILLSIDE_12 | 12.47 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327412 | lhfrt | 32741 | HILLSIDE_12 | 12.47 | 2 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321721 | lhfrt | 32172 | HIGHWINDS | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321722 | lhfrt | 32172 | HIGHWINDS | 0.69 | 2 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346241 | lhfrt | 34624 | BALCH 1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346121 | lhfrt | 34612 | BLCH 2-2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346141 | lhfrt | 34614 | BLCH 2-3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317841 | lhfrt | 31784 | BELDEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317681 | lhfrt | 31768 | JBBLACK1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317701 | lhfrt | 31770 | JBBLACK2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318201 | lhfrt | 31820 | BCKS CRK | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318202 | lhfrt | 31820 | BCKS CRK | 11 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317801 | lhfrt | 31780 | BUTTVLLY | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318101 | lhfrt | 31810 | CRBU 1 | 11.5 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318082 | lhfrt | 31808 | CRBOU2-3 | 11.5 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317821 | lhfrt | 31782 | CRBU 4-5 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319231 | lhfrt | 31923 | COLUSAPPCTG1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0.5 | 90 | 182 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
319242 | lhfrt | 31924 | COLUSAPPCTG2 | 18 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0.5 | 90 | 182 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
319253 | lhfrt | 31925 | COLUSAPPSTG1 | 18 | 3 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2 | -2.4 | -3.6 | 0 | 0 | 0 | 0.5 | 120 | 245 | 120 | 30 | 7.5 | 0.1 | 0 | 0 | 0 | 0
318121 | lhfrt | 31812 | CRESTA | 11.5 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364111 | lhfrt | 36411 | DIABLOCNYN1 | 25 | 1 | : | [5 empty] | #9 | 60 | -1.65 | -2.05 | -2.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 31 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364121 | lhfrt | 36412 | DIABLOCNYN2 | 25 | 1 | : | [5 empty] | #9 | 60 | -1.65 | -2.05 | -2.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 31 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325062 | lhfrt | 32506 | DRUMPH1U3U4 | 6.6 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324641 | lhfrt | 32464 | DUTCHFLAT1PH | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338121 | lhfrt | 33812 | ELECTRA | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338122 | lhfrt | 33812 | ELECTRA | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338123 | lhfrt | 33812 | ELECTRA | 13.8 | 3 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331181 | lhfrt | 33118 | GATEWAY1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -0.6 | -1.6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331191 | lhfrt | 33119 | GATEWAY2 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331201 | lhfrt | 33120 | GATEWAY3 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346101 | lhfrt | 34610 | HAAS | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346102 | lhfrt | 34610 | HAAS | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311811 | lhfrt | 31181 | HMBOBAYPPA | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311812 | lhfrt | 31181 | HMBOBAYPPA | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311813 | lhfrt | 31181 | HMBOBAYPPA | 13.8 | 3 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311804 | lhfrt | 31180 | HMBOBAYPPB | 13.8 | 4 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311805 | lhfrt | 31180 | HMBOBAYPPB | 13.8 | 5 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311806 | lhfrt | 31180 | HMBOBAYPPB | 13.8 | 6 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311807 | lhfrt | 31180 | HMBOBAYPPB | 13.8 | 7 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311828 | lhfrt | 31182 | HMBOBAYPPC | 13.8 | 8 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
311829 | lhfrt | 31182 | HMBOBAYPPC | 13.8 | 9 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
3118210 | lhfrt | 31182 | HMBOBAYPPC | 13.8 | 10 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0
346001 | lhfrt | 34600 | HELMS 1 | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346021 | lhfrt | 34602 | HELMS 2 | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346041 | lhfrt | 34604 | HELMS 3 | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343081 | lhfrt | 34308 | KERCKHOFFPH2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318181 | lhfrt | 31818 | PIT 1 U1 | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318021 | lhfrt | 31802 | PIT 3 | 11.5 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318022 | lhfrt | 31802 | PIT 3 | 11.5 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318023 | lhfrt | 31802 | PIT 3 | 11.5 | 3 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317661 | lhfrt | 31766 | PIT 4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317662 | lhfrt | 31766 | PIT 4 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318041 | lhfrt | 31804 | PIT 5 U1 | 11.5 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318042 | lhfrt | 31804 | PIT 5 U1 | 11.5 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318063 | lhfrt | 31806 | PIT5U3U4 | 11.5 | 3 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318064 | lhfrt | 31806 | PIT5U3U4 | 11.5 | 4 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317761 | lhfrt | 31776 | PIT 7 U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317781 | lhfrt | 31778 | PIT 7 U2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317861 | lhfrt | 31786 | ROCK CK1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317881 | lhfrt | 31788 | ROCK CK2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338001 | lhfrt | 33800 | SALT SPS | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340621 | lhfrt | 34062 | STANISLS | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338221 | lhfrt | 33822 | TIGR CRK | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340621 | lhfrt | 34062 | STANISLAUSPH | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369801 | lhfrt | 36980 | KIRKWD 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369821 | lhfrt | 36982 | KIRKWD 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369861 | lhfrt | 36986 | HOLM 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369881 | lhfrt | 36988 | HOLM 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350361 | lhfrt | 35036 | Mt Poso | 13.8 | 1 | : | [5 empty] | #9 | 60 | 58 | 57 | 55 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 60 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318201 | lhfrt | 31820 | BCKS CRK | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318202 | lhfrt | 31820 | BCKS CRK | 11 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318101 | lhfrt | 31810 | CRBU 1 | 11.5 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319231 | lhfrt | 31923 | COLUSAPPCTG1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0.5 | 90 | 182 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
319242 | lhfrt | 31924 | COLUSAPPCTG2 | 18 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0.5 | 90 | 182 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0
318181 | lhfrt | 31818 | PIT 1 U1 | 11 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317761 | lhfrt | 31776 | PIT 7 U1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379631 | lhfrt | 37963 | RDGCT6 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06667 | 100 | 60 | 0.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368631 | lhfrt | 36863 | DVRaGT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368641 | lhfrt | 36864 | DVRbGT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368651 | lhfrt | 36865 | DVRaST3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.1 | -3.2 | 2.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.0833 | 60 | 0.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385721 | lhfrt | 38572 | WEC3-ST | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.2 | -3 | 1.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364391 | lhfrt | 36439 | CVSR-R1 | 0.342 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364401 | lhfrt | 36440 | CVSR-R2 | 0.27 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364411 | lhfrt | 36441 | CVSR-B1 | 0.342 | 1 | : | [5 empty] | #9 | 60 | 3.1 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350341 | lhfrt | 35034 | ATWELLWSPV | 0.41 | 1 | 34759 | ATWELLW | 115 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | 2.2 | 1.6 | 0.6 | 0 | 0 | 0 | 3 | 30 | 180 | 0.3 | 7.5 | 30 | 180 | 0 | 0 | 0 | 0
3657491 | lhfrt | 365749 | SHILOH2WIND | 0.57 | 1 | 32177 | SHILOH2C1 | 34.5 | 1 | 1 | : | #9 | 60 | -3 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 0.0333 | 7.5 | 30 | 180 | 180 | 0.0333 | 0 | 0 | 0 | 0 | 0
3657491 | lhfrt | 365749 | SHILOH2WIND | 0.57 | 1 | : | [5 empty] | #9 | 60 | -0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321911 | lhfrt | 32191 | SHILOH3WIND | 0.57 | 1 | 32189 | SHILOH3C1 | 34.5 | 1 | 1 | : | #9 | 60 | -3 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 0.0333 | 7.5 | 30 | 180 | 180 | 0.0333 | 0 | 0 | 0 | 0 | 0
321911 | lhfrt | 32191 | SHILOH3WIND | 0.57 | 1 | : | [5 empty] | #9 | 60 | -0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338181 | lhfrt | 33818 | STCKNBIOMASS | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | 2 | -2.8 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 9.14 | 4.67 | 3.1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318122 | lhfrt | 31812 | CRESTA | 11.5 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343061 | lhfrt | 34306 | EXCHQUER | 13.8 | 1 | : | [5 empty] | #9 | 60 | -6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346101 | lhfrt | 34610 | HAAS | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346102 | lhfrt | 34610 | HAAS | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350401 | lhfrt | 35040 | KERNRDGE32G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | 1 | -3 | -2.5 | -2 | -1 | 0 | 0 | 0 | 0 | 0.5 | 180 | 0.05 | 10 | 30 | 180 | 0 | 0 | 0 | 0 | 0
3001402 | lhfrt | 300140 | KERNRDGE32G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 2 | 1 | -3 | -2.5 | -2 | -1 | 0 | 0 | 0 | 0 | 0.5 | 180 | 0.05 | 10 | 30 | 180 | 0 | 0 | 0 | 0 | 0
3001413 | lhfrt | 300141 | KERNRDGE32G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 2 | 1 | -3 | -2.5 | -2 | -1 | 0 | 0 | 0 | 0 | 0.5 | 180 | 0.05 | 10 | 30 | 180 | 0 | 0 | 0 | 0 | 0
350564 | lhfrt | 35056 | KERNRDGELH | 4.16 | 4 | : | [5 empty] | #9 | 60 | 3 | -3 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 1.75 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350565 | lhfrt | 35056 | KERNRDGELH | 4.16 | 5 | : | [5 empty] | #9 | 60 | 3 | -3 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 1.75 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350566 | lhfrt | 35056 | KERNRDGELH | 4.16 | 6 | : | [5 empty] | #9 | 60 | 3 | -3 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 1.75 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346401 | lhfrt | 34640 | ULTR.PWR | 12.47 | 1 | : | [5 empty] | #9 | 60 | -5 | -10 | -15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350371 | lhfrt | 35037 | UNIVRSTY | 12.47 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317941 | lhfrt | 31794 | WOODLEAF | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -1.6 | -2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 90 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3656831 | lhfrt | 365683 | Q1103SPV | 34.5 | 1 | 365681 | Q1103 | 115 | 1 | : |  | #9 | 60 | -1.5 | -3 | 0.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 299.2 | 0.1 | 299.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3745651 | lhfrt | 374565 | SQ3_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.5 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 0.15 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3745661 | lhfrt | 374566 | SQ3_BES | 0.55 | 1 | : | [5 empty] | #9 | 60 | -2.5 | -2 | -1.6 | 1.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0.16 | 2.01 | 30.01 | 0.01 | 30.01 | 0 | 0 | 0 | 0 | 0 | 0
346991 | lhfrt | 34699 | Q529_SPV | 0.385 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358511 | lhfrt | 35851 | GROYPKR1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358521 | lhfrt | 35852 | GROYPKR2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 7.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350761 | lhfrt | 35076 | ELKHIL1G | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350771 | lhfrt | 35077 | ELKHIL2G | 18 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350781 | lhfrt | 35078 | ELKHIL3G | 18 | 1 | : | [5 empty] | #9 | 60 | 2.3 | 1.6 | -1.6 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373181 | lhfrt | 37318 | WHITERK1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
373191 | lhfrt | 37319 | WHITERK2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
4604041 | lhfrt | 460404 | PV EQ | 0.66 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
4604061 | lhfrt | 460406 | BESS EQ | 0.63 | 1 | 460406 | BESS EQ | 0.63 | : |  |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
4610961 | lhfrt | 461096 | 0.6 kV Bus 2 | 0.6 | 1 | 46112 | PAINTHL | 230 | : |  |  | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4610971 | lhfrt | 461097 | 0.6 kV Bus 1 | 0.6 | 1 | 46112 | PAINTHL | 230 | : |  |  | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4739211 | lhfrt | 473921 | BRICKOVEN_G2 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0
4739111 | lhfrt | 473911 | BRICKOVEN_G1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0
4738511 | lhfrt | 473851 | LUND_HILL | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 1.2 | -1.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 300 | 300 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 1
450231 | lhfrt | 45023 | BOYLE 1 | 11 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
450642 | lhfrt | 45064 | BOYLE 2 | 11 | 2 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
430171 | lhfrt | 43017 | BEAVER | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
430172 | lhfrt | 43017 | BEAVER | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
430191 | lhfrt | 43019 | BEAVER | 20 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
430223 | lhfrt | 43022 | BEAVER2 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
430224 | lhfrt | 43022 | BEAVER2 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
430235 | lhfrt | 43023 | BEAVER3 | 13.8 | 5 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
430236 | lhfrt | 43023 | BEAVER3 | 13.8 | 6 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
431191 | lhfrt | 43119 | COYO S1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0
433692 | lhfrt | 43369 | OAKGROVE | 11 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
434071 | lhfrt | 43407 | PELTON | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
434653 | lhfrt | 43465 | RIVRMILL | 11 | 3 | : | [5 empty] | #9 | 60 | -5.5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434664 | lhfrt | 43466 | RIVRMILL2 | 11 | 4 | : | [5 empty] | #9 | 60 | -5.3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434665 | lhfrt | 43466 | RIVRMILL2 | 11 | 5 | : | [5 empty] | #9 | 60 | -5 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434861 | lhfrt | 43486 | ROUND B1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
435561 | lhfrt | 43556 | SULIVAN | 4.16 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47933Z1 | lhfrt | 47933 | BIGLW W1 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47485Z1 | lhfrt | 47485 | VESTAS-WTG2 | 0.72 | Z1 | 47485 | VESTAS-WTG2 | 0.72 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47482Z1 | lhfrt | 47482 | GE-WTG | 0.69 | Z1 | 47482 | GE-WTG | 0.69 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
466721 | lhfrt | 46672 | ALDER2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 2 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41667 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466711 | lhfrt | 46671 | ALDER11 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469133 | lhfrt | 46913 | CUSHMN33 | 12.6 | 3 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467331 | lhfrt | 46733 | LAGRND5 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466231 | lhfrt | 46623 | MAYFILD1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3.6 | -3 | -2.1 | -0.6 | 0 | 0 | 0 | 0.1 | 30 | 180 | 0.1 | 0.8 | 30 | 180 | 0 | 0 | 0 | 0
466242 | lhfrt | 46624 | MAYFILD2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1 | 30 | 180 | 0.1 | 0.8 | 7.5 | 30 | 180 | 0 | 0 | 0
466243 | lhfrt | 46624 | MAYFILD2 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1 | 30 | 180 | 0.1 | 0.8 | 7.5 | 30 | 180 | 0 | 0 | 0
466244 | lhfrt | 46624 | MAYFILD2 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1 | 30 | 180 | 0.1 | 0.8 | 7.5 | 30 | 180 | 0 | 0 | 0
466271 | lhfrt | 46627 | MOSSYRK1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1 | 30 | 180 | 0.1 | 0.8 | 7.5 | 30 | 180 | 0 | 0 | 0
466282 | lhfrt | 46628 | MOSSYRK2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0.1 | 30 | 180 | 0.1 | 0.8 | 7.5 | 30 | 180 | 0 | 0 | 0
476061 | lhfrt | 47606 | BLUERDG2_G1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
476072 | lhfrt | 47607 | BLUERDG2_G2 | 0.69 | 2 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445581 | lhfrt | 44558 | GALAPV | 0.6 | 1 | 45247 | PONDROSA | 115 | 1 | 1 | : | #1 | 60 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445581 | lhfrt | 44558 | GALAPV | 0.6 | 1 | 45247 | PONDROSA | 115 | 1 | 1 | : | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445851 | lhfrt | 44585 | MILCN SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445851 | lhfrt | 44585 | MILCN SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445851 | lhfrt | 44585 | MILCN SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445851 | lhfrt | 44585 | MILCN SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
446031 | lhfrt | 44603 | PRNVL SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
446031 | lhfrt | 44603 | PRNVL SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
446031 | lhfrt | 44603 | PRNVL SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
446031 | lhfrt | 44603 | PRNVL SLR L | 0.63 | 1 | : | [5 empty] | #1 | 60 | -5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42997Z1 | lhfrt | 42997 | SKOOK W1 | 0.65 | Z1 | : | [5 empty] | #9 | 60 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47975Z1 | lhfrt | 47975 | STRPT W1 | 0.6 | Z1 | 47975 | STRPT W1 | 0.6 | : |  |  | #9 | 1 | -0.06 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47887Z1 | lhfrt | 47887 | PEBBL W1 | 0.6 | Z1 | 47887 | PEBBL W1 | 0.6 | : |  |  | #9 | 1 | -0.06 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47974Z1 | lhfrt | 47974 | HCAYN W1 | 0.6 | Z1 | 47974 | HCAYN W1 | 0.6 | : |  |  | #9 | 1 | -0.06 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47872Z1 | lhfrt | 47872 | BIGHR W1 | 0.575 | Z1 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 1.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47873Z1 | lhfrt | 47873 | BIGHR W2 | 0.575 | Z1 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 1.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47799Z1 | lhfrt | 47799 | BIGHR W3 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -2.2 | -1.8 | -1.4 | -1 | 0.7 | 1 | 1.4 | 1.8 | 0 | 0 | 0.02 | 10 | 45 | 240 | 300 | 110 | 29 | 0.02 | 0 | 0 | 0
44885Z1 | lhfrt | 44885 | LEANJ W1 | 0.6 | Z1 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
47806Z1 | lhfrt | 47806 | LJ2 W1 | 0.6 | Z1 | 47806 | LJ2 W1 | 0.6 | : |  |  | #9 | 1 | -0.06 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47810Z1 | lhfrt | 47810 | LJ2 W1 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | 1.5 | 2.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.1 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47912Z1 | lhfrt | 47912 | KLONDIKE_W1 | 0.575 | Z1 | 47327 | KLONDIKE | 115 | : |  |  | #9 | 1 | -0.06 | -0.045 | -0.027 | 0.027 | 0.03 | 0.04 | 0 | 0 | 0 | 0 | 0.02 | 1 | 31 | 31 | 1 | 0.02 | 0 | 0 | 0 | 0 | 1
47917Z1 | lhfrt | 47917 | KLONDIKE_W2 | 0.575 | Z1 | 47327 | KLONDIKE | 115 | : |  |  | #9 | 1 | -0.06 | -0.045 | -0.027 | 0.027 | 0.03 | 0.04 | 0 | 0 | 0 | 0 | 0.02 | 1 | 31 | 31 | 1 | 0.02 | 0 | 0 | 0 | 0 | 1
47997Z1 | lhfrt | 47997 | KLOND W2A | 0.575 | Z1 | 47327 | KLONDIKE | 115 | : |  |  | #9 | 1 | -0.06 | -0.045 | -0.027 | 0.027 | 0.03 | 0.04 | 0 | 0 | 0 | 0 | 0.02 | 1 | 31 | 31 | 1 | 0.02 | 0 | 0 | 0 | 0 | 1
47924Z1 | lhfrt | 47924 | KLONDIKE_W3 | 0.575 | Z1 | 47830 | KLONDSCH | 230 | : |  |  | #9 | 1 | -0.06 | -0.05 | 0.03 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47926Z1 | lhfrt | 47926 | KLONDIKE_W3S | 0.575 | Z1 | 47830 | KLONDSCH | 230 | : |  |  | #9 | 60 | -3 | 2 | 2.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 180 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47921Z1 | lhfrt | 47921 | KLONDIKE_W3A | 0.575 | Z1 | 47830 | KLONDSCH | 230 | : |  |  | #9 | 1 | -0.06 | -0.05 | 0.03 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47389Z1 | lhfrt | 47389 | JNPER_CAN_W1 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -3 | -2.5 | -1 | 0.05 | 1.8 | 2 | 0 | 0 | 0 | 0 | 0.01 | 0.1 | 600 | 600 | 0.1 | 0.01 | 0 | 0 | 0 | 0 | 1
445541 | lhfrt | 44554 | CHOPIN WND | 0.69 | 1 | 44553 | CHOPIN COL | 34.5 | : |  |  | #9 | 60 | 3 | 5 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.1 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420311 | lhfrt | 42031 | FERNDL 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42033L | lhfrt | 42033 | FERNDL L | 13.8 | L | : | [5 empty] | #9 | 60 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420322 | lhfrt | 42032 | FERNDL 2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420111 | lhfrt | 42011 | ENSERCH1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420122 | lhfrt | 42012 | ENSERCH2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420133 | lhfrt | 42013 | ENSERCH3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42014L | lhfrt | 42014 | ENSERCHL | 13.8 | L | : | [5 empty] | #9 | 60 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48860Z1 | lhfrt | 48860 | PALOUSE_W1 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421211 | lhfrt | 42121 | LO BAKER | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.6 | 1.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 30 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42990Z4 | lhfrt | 42990 | PHLNG W1 | 0.69 | Z4 | : | [5 empty] | #9 | 60 | -3 | -15 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42994Z4 | lhfrt | 42994 | DDGJN W1 | 0.69 | Z4 | : | [5 empty] | #9 | 60 | -3 | -15 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455411 | lhfrt | 45541 | SWIFT2-1 | 13.8 | 1 | 45541 | SWIFT2-1 | 13.8 | 1 | 1 | : | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455421 | lhfrt | 45542 | SWIFT2-2 | 13.8 | 1 | 45542 | SWIFT2-2 | 13.8 | 1 | 1 | : | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461701 | lhfrt | 46170 | PRIEST01 | 13.2 | 1 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461712 | lhfrt | 46171 | PRIEST02 | 13.2 | 2 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461723 | lhfrt | 46172 | PRIEST03 | 13.2 | 3 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461745 | lhfrt | 46174 | PRIEST05 | 13.2 | 5 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461767 | lhfrt | 46176 | PRIEST07 | 13.2 | 7 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461778 | lhfrt | 46177 | PRIEST08 | 13.2 | 8 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461789 | lhfrt | 46178 | PRIEST09 | 13.2 | 9 | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46179A | lhfrt | 46179 | PRIEST10 | 13.2 | A | : | [5 empty] | #9 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461801 | lhfrt | 46180 | WANAPM01 | 13.2 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
461823 | lhfrt | 46182 | WANAPM03 | 13.2 | 3 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
461834 | lhfrt | 46183 | WANAPM04 | 13.2 | 4 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
461845 | lhfrt | 46184 | WANAPM05 | 13.2 | 5 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
461867 | lhfrt | 46186 | WANAPM07 | 13.2 | 7 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
461878 | lhfrt | 46187 | WANAPM08 | 13.2 | 8 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
461889 | lhfrt | 46188 | WANAPM09 | 13.2 | 9 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
46189A | lhfrt | 46189 | WANAPM10 | 13.8 | A | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
47983Z1 | lhfrt | 47983 | BIGLW W2 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47985Z1 | lhfrt | 47985 | BIGLW W3 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430441 | lhfrt | 43044 | CARTYCT | 21 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.05 | 180 | 0.05 | 0 | 0 | 0 | 0 | 0
430451 | lhfrt | 43045 | CARTYST | 16 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.05 | 180 | 0.05 | 0 | 0 | 0 | 0 | 0
431111 | lhfrt | 43111 | COYO G1 | 18 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -3 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0
431891 | lhfrt | 43189 | FARADAY | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
433591 | lhfrt | 43359 | NORTH FK | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
433681 | lhfrt | 43368 | OAKGROVE | 11 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
434072 | lhfrt | 43407 | PELTON | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
434073 | lhfrt | 43407 | PELTON | 13.8 | 3 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439051 | lhfrt | 43905 | PORTW G1 | 18 | 1 | : | [5 empty] | #9 | 60 | -1 | -1.6 | -3 | -3.2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 180 | 30 | 0.75 | 0.17 | 180 | 30 | 0 | 0 | 0 | 0 | 0
439071 | lhfrt | 43907 | PORTW S1 | 16.5 | 1 | : | [5 empty] | #9 | 60 | -3 | -3.2 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.167 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
439101 | lhfrt | 43910 | PORTW2A | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439102 | lhfrt | 43910 | PORTW2A | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439103 | lhfrt | 43910 | PORTW2A | 13.8 | 3 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439114 | lhfrt | 43911 | PORTW2B | 13.8 | 4 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439115 | lhfrt | 43911 | PORTW2B | 13.8 | 5 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439116 | lhfrt | 43911 | PORTW2B | 13.8 | 6 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439137 | lhfrt | 43913 | PORTW2C | 13.8 | 7 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439138 | lhfrt | 43913 | PORTW2C | 13.8 | 8 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
439139 | lhfrt | 43913 | PORTW2C | 13.8 | 9 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
4391410 | lhfrt | 43914 | PORTW2D | 13.8 | 10 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
4391411 | lhfrt | 43914 | PORTW2D | 13.8 | 11 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
4391412 | lhfrt | 43914 | PORTW2D | 13.8 | 12 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
434882 | lhfrt | 43488 | ROUND B2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
434903 | lhfrt | 43490 | ROUND B3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
43953Z1 | lhfrt | 43953 | MULLANW1 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43956Z2 | lhfrt | 43956 | MULLANW2 | 0.69 | Z2 | : | [5 empty] | #9 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
476011 | lhfrt | 47601 | BLUERDG1_G1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -9 | -6 | -5 | -3.6 | 3.6 | 5 | 6 | 0 | 0 | 0 | 0.26 | 1.05 | 2 | 63 | 63 | 2 | 0.26 | 0 | 0 | 0 | 0
476021 | lhfrt | 47602 | BLUERDG1_G2 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -9 | -6 | -5 | -3.6 | 3.6 | 5 | 6 | 0 | 0 | 0 | 0.26 | 1.05 | 2 | 63 | 63 | 2 | 0.26 | 0 | 0 | 0 | 0
476871 | lhfrt | 47687 | GEP G1 | 18 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47688L | lhfrt | 47688 | GEC S1 | 13.8 | L | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421371 | lhfrt | 42137 | LO BAKR4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.6 | -1 | 0.8 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
476751 | lhfrt | 47675 | MNTFRM G | 18 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 3 | -1.8 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 1 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420211 | lhfrt | 42021 | SUMAS 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42022L | lhfrt | 42022 | SUMAS L | 13.8 | L | : | [5 empty] | #9 | 60 | -2.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42367Z1 | lhfrt | 42367 | WILDH W1 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42369Z1 | lhfrt | 42369 | WILDH W2 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42372Z1 | lhfrt | 42372 | WILDH W3 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464391 | lhfrt | 46439 | ROSS 42 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
464392 | lhfrt | 46439 | ROSS 42 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
464413 | lhfrt | 46441 | ROSS 44 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
464414 | lhfrt | 46441 | ROSS 44 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
464304 | lhfrt | 46430 | GORGE 4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 10 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467891 | lhfrt | 46789 | CUSHMN1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467902 | lhfrt | 46790 | CUSHMN1 | 13.2 | 2 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469111 | lhfrt | 46911 | CUSHMN2 | 12.6 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469122 | lhfrt | 46912 | CUSHMN2 | 12.6 | 2 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462101 | lhfrt | 46210 | CARMEN | 11.5 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 7.5 | 30 | 180 | 180 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0
462102 | lhfrt | 46210 | CARMEN | 11.5 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 7.5 | 30 | 180 | 180 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0
421111 | lhfrt | 42111 | FREDONA1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421122 | lhfrt | 42112 | FREDONA2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
412981 | lhfrt | 41298 | SMITHFLS | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -0.6 | -0.3 | 0.3 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 30 | 200 | 0 | 0 | 200 | 30 | 0 | 0 | 0 | 0 | 0
420422 | lhfrt | 42042 | WHITHRN2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420433 | lhfrt | 42043 | WHITHRN2 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421143 | lhfrt | 42114 | FREDONA3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -2.2 | -1.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421154 | lhfrt | 42115 | FREDONA4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -2.2 | -1.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421171 | lhfrt | 42117 | Sierra Pacific Industries | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.5 | -3.6 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 9.98 | 0.08 | 5 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421241 | lhfrt | 42124 | UP BAKER | 13.8 | 1 | : | [5 empty] | #9 | 60 | -9 | -3 | 1.8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 60 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421242 | lhfrt | 42124 | UP BAKER | 13.8 | 2 | : | [5 empty] | #9 | 60 | -9 | -3 | 1.8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 60 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421265 | lhfrt | 42126 | CFALLGEN | 6.6 | 5 | : | [5 empty] | #9 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421266 | lhfrt | 42126 | CFALLGEN | 6.6 | 6 | : | [5 empty] | #9 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423511 | lhfrt | 42351 | TOLT RIV | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
427211 | lhfrt | 42721 | FREDERC1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
427222 | lhfrt | 42722 | FREDERC2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | -1.8 | 1.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44843Z1 | lhfrt | 44843 | MARENGO2LT | 0.69 | Z1 | : | [5 empty] | #9 | 60 | 3 | 2 | -3 | -4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 2 | 2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44845Z1 | lhfrt | 44845 | MARENGO1LT | 0.69 | Z1 | : | [5 empty] | #9 | 60 | 3 | 2 | -3 | -4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 2 | 2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462681 | lhfrt | 46268 | WEYCO 4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4646451 | lhfrt | 46464 | BOUNDG51 | 14.4 | 51 | 40145 | BOUNDRYE | 230 | : |  |  | #9 | 60 | 10 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4646652 | lhfrt | 46466 | BOUNDG52 | 14.4 | 52 | 40145 | BOUNDRYE | 230 | : |  |  | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
4646853 | lhfrt | 46468 | BOUNDG53 | 14.4 | 53 | 40145 | BOUNDRYE | 230 | : |  |  | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
4647054 | lhfrt | 46470 | BOUNDG54 | 14.4 | 54 | 40145 | BOUNDRYE | 230 | : |  |  | #9 | 60 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
4647255 | lhfrt | 46472 | BOUNDG55 | 14.4 | 55 | 40145 | BOUNDRYE | 230 | : |  |  | #9 | 60 | 10 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4647456 | lhfrt | 46474 | BOUNDG56 | 14.4 | 56 | 40145 | BOUNDRYE | 230 | : |  |  | #9 | 60 | 10 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466061 | lhfrt | 46606 | TBIO | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 0.03 | 180 | 30 | 0.03 | 0 | 0 | 0 | 0 | 0
466191 | lhfrt | 46619 | HEADWORK | 1.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.752 | 1.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
472161 | lhfrt | 47216 | River Road Generating Plant | 18 | 1 | : | [5 empty] | #9 | 60 | -3.6 | -3.2 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.12 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0
472901 | lhfrt | 47290 | WAUNA | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.9 | -1.2 | -1 | -0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.2 | 18 | 50 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0
475961 | lhfrt | 47596 | GRAYS_HRB_G1 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.6 | -3 | -4 | 1.7 | 2.1 | 0 | 0 | 0 | 30 | 33 | 10 | 0.1 | 0.5 | 0.1 | 0.25 | 0 | 0 | 0 | 0
475971 | lhfrt | 47597 | GRAYS_HRB_G2 | 18 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.6 | -3 | -4 | 1.7 | 2.1 | 0 | 0 | 0 | 30 | 33 | 10 | 0.1 | 0.5 | 0.1 | 0.25 | 0 | 0 | 0 | 0
475981 | lhfrt | 47598 | GT1, GT2, STG | 18 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2 | -2.6 | -3 | -4 | 1.7 | 2.1 | 0 | 0 | 0 | 30 | 33 | 10 | 0.1 | 0.5 | 0.1 | 0.25 | 0 | 0 | 0 | 0
476761 | lhfrt | 47676 | MNTFRM S | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2 | -1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47866Z1 | lhfrt | 47866 | GDNOE W1 | 0.6 | Z1 | : | [5 empty] | #9 | 60 | -1 | -1.6 | -2 | -2.2 | -3 | 0.7 | 0.85 | 1.6 | 1.7 | 2.2 | 540 | 80 | 35 | 8 | 0.05 | 300 | 180 | 30 | 4 | 0.05 | 0
47878Z1 | lhfrt | 47878 | HOPKR W1 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -3.2 | -1 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47879Z1 | lhfrt | 47879 | HOPKR W2 | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -3.2 | -1 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481731 | lhfrt | 48173 | KETTLEAV | 13.8 | 1 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481732 | lhfrt | 48173 | KETTLEAV | 13.8 | 2 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482651 | lhfrt | 48265 | NINEMI12 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482652 | lhfrt | 48265 | NINEMI12 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48359G1 | lhfrt | 48359 | RATHGEN1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48361G2 | lhfrt | 48361 | RATHGEN2 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484821 | lhfrt | 48482 | CWGEN3 | 12 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484831 | lhfrt | 48483 | CWGEN4 | 12 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464191 | lhfrt | 46419 | DIABLO31 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 10 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464202 | lhfrt | 46420 | DIABLO32 | 13.8 | 2 | 46419 | DIABLO31 | 13.8 | : |  |  | #9 | 60 | 10 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
468031A1 | lhfrt | 468031 | CHELAN_A1 | 11 | A1 | : | [5 empty] | #9 | 60 | -1.5 | -2.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
468032A2 | lhfrt | 468032 | CHELAN_A2 | 11 | A2 | : | [5 empty] | #9 | 60 | -1.5 | -2.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46841C1 | lhfrt | 46841 | ROCKYR01 | 15 | C1 | : | [5 empty] | #9 | 60 | -1.5 | -2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46842C2 | lhfrt | 46842 | ROCKYR02 | 15 | C2 | : | [5 empty] | #9 | 60 | -1.5 | -2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46843C3 | lhfrt | 46843 | ROCKYR03 | 15 | C3 | : | [5 empty] | #9 | 60 | -1.5 | -2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46844C4 | lhfrt | 46844 | ROCKYR04 | 15 | C4 | : | [5 empty] | #9 | 60 | -1.5 | -2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46845C5 | lhfrt | 46845 | ROCKYR05 | 15 | C5 | : | [5 empty] | #9 | 60 | -1.5 | -2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46846C6 | lhfrt | 46846 | ROCKYR06 | 15 | C6 | : | [5 empty] | #9 | 60 | -1.5 | -2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46847C7 | lhfrt | 46847 | ROCKYR07 | 15 | C7 | : | [5 empty] | #9 | 60 | -1.5 | -2.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46848C8 | lhfrt | 46848 | ROCKYR08 | 15 | C8 | : | [5 empty] | #9 | 60 | -1.5 | -2.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46849C9 | lhfrt | 46849 | ROCKYR09 | 15 | C9 | : | [5 empty] | #9 | 60 | -1.5 | -2.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46850CA | lhfrt | 46850 | ROCKYR10 | 15 | CA | : | [5 empty] | #9 | 60 | -1.5 | -2.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46851CB | lhfrt | 46851 | ROCKYR11 | 15 | CB | : | [5 empty] | #9 | 60 | -1.5 | -2.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 30 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46889B1 | lhfrt | 46889 | RI STUB1 | 13.8 | B1 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46889B2 | lhfrt | 46889 | RI STUB1 | 13.8 | B2 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46891B3 | lhfrt | 46891 | RI STUB2 | 13.8 | B3 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46891B4 | lhfrt | 46891 | RI STUB2 | 13.8 | B4 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46893B5 | lhfrt | 46893 | RI NORTH | 13.8 | B5 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46893B6 | lhfrt | 46893 | RI NORTH | 13.8 | B6 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46893B7 | lhfrt | 46893 | RI NORTH | 13.8 | B7 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46895B8 | lhfrt | 46895 | RI SOUTH | 13.8 | B8 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46895B9 | lhfrt | 46895 | RI SOUTH | 13.8 | B9 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46895BA | lhfrt | 46895 | RI SOUTH | 13.8 | BA | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46802U1 | lhfrt | 46802 | ROCKI U1 | 6.9 | U1 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46804U2 | lhfrt | 46804 | ROCKI U2 | 6.9 | U2 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46806U3 | lhfrt | 46806 | ROCKI U3 | 6.9 | U3 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46810U4 | lhfrt | 46810 | ROCKI U4 | 6.9 | U4 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46812U5 | lhfrt | 46812 | ROCKI U5 | 6.9 | U5 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46814U6 | lhfrt | 46814 | ROCKI U6 | 6.9 | U6 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46820U7 | lhfrt | 46820 | ROCKI U7 | 6.9 | U7 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46822U8 | lhfrt | 46822 | ROCKI U8 | 6.9 | U8 | : | [5 empty] | #9 | 60 | -1 | -2 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
475681 | lhfrt | 47568 | LANCAS G | 18 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
475691 | lhfrt | 47569 | LANCAS S | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480611 | lhfrt | 48061 | CABGOR12 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480612 | lhfrt | 48061 | CABGOR12 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480633 | lhfrt | 48063 | CABGOR34 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480634 | lhfrt | 48063 | CABGOR34 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481731 | lhfrt | 48173 | KETTLEAV | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481732 | lhfrt | 48173 | KETTLEAV | 13.8 | 2 | : | [5 empty] | #9 | 60 | -1.6 | -2.2 | -3.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.5 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481891 | lhfrt | 48189 | LITFAL12 | 4 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481892 | lhfrt | 48189 | LITFAL12 | 4 | 2 | : | [5 empty] | #9 | 60 | -3.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481913 | lhfrt | 48191 | LITFAL34 | 4 | 3 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481914 | lhfrt | 48191 | LITFAL34 | 4 | 4 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482051 | lhfrt | 48205 | LONGLKG1 | 4 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482072 | lhfrt | 48207 | LONGLKG2 | 4 | 2 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482093 | lhfrt | 48209 | LONGLKG3 | 4 | 3 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482114 | lhfrt | 48211 | LONGLKG4 | 4 | 4 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482411 | lhfrt | 48241 | MONROEA | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482651 | lhfrt | 48265 | NINEMI12 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482652 | lhfrt | 48265 | NINEMI12 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482673 | lhfrt | 48267 | NINEMI34 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482674 | lhfrt | 48267 | NINEMI34 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482751 | lhfrt | 48275 | NORTHEAS | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483211 | lhfrt | 48321 | PLUMMER | 4.16 | 1 | : | [5 empty] | #9 | 60 | -1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3333 | 0.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483311 | lhfrt | 48331 | POSTFL15 | 2.4 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483312 | lhfrt | 48331 | POSTFL15 | 2.4 | 2 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483313 | lhfrt | 48331 | POSTFL15 | 2.4 | 3 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483314 | lhfrt | 48331 | POSTFL15 | 2.4 | 4 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483315 | lhfrt | 48331 | POSTFL15 | 2.4 | 5 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483336 | lhfrt | 48333 | POSTFLS6 | 2.4 | 6 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483351 | lhfrt | 48335 | POSTSTRT | 4.16 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48359G1 | lhfrt | 48359 | RATHGEN1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48361G2 | lhfrt | 48361 | RATHGEN2 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484071 | lhfrt | 48407 | SPKWASTE | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484331 | lhfrt | 48433 | UPRIVER | 2.4 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484332 | lhfrt | 48433 | UPRIVER | 2.4 | 2 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484333 | lhfrt | 48433 | UPRIVER | 2.4 | 3 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484351 | lhfrt | 48435 | UPRIVER | 4.16 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484352 | lhfrt | 48435 | UPRIVER | 4.16 | 2 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484821 | lhfrt | 48482 | CWGEN3 | 12 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484831 | lhfrt | 48483 | CWGEN4 | 12 | 1 | : | [5 empty] | #9 | 60 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485261 | lhfrt | 48526 | BOULDERG | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.133 | 0.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485262 | lhfrt | 48526 | BOULDERG | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.133 | 0.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485263 | lhfrt | 48526 | BOULDERG | 13.8 | 3 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.133 | 0.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485264 | lhfrt | 48526 | BOULDERG | 13.8 | 4 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.133 | 0.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485265 | lhfrt | 48526 | BOULDERG | 13.8 | 5 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.133 | 0.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485266 | lhfrt | 48526 | BOULDERG | 13.8 | 6 | : | [5 empty] | #9 | 60 | -2.5 | -3.2 | 1.8 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.133 | 0.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480365Z1 | lhfrt | 480365 | RATTLESNAKE | 0.69 | Z1 | : | [5 empty] | #9 | 60 | -3.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480367Z2 | lhfrt | 480367 | RATTLESNAKE | 0.69 | Z2 | : | [5 empty] | #9 | 60 | -3.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481871PV | lhfrt | 481871 | LIND | 13.8 | PV | : | [5 empty] | #9 | 60 | -2.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47397Z1 | lhfrt | 47397 | MONTG W1 | 0.6 | Z1 | 47394 | MONTG 1 | 230 | : |  |  | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
473781 | lhfrt | 47378 | MONTAGUE_W2 | 0.6 | 1 | 47398 | MONTG 2 | 230 | : |  |  | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
47489Z1 | lhfrt | 47489 | VESTAS-WTG1 | 0.72 | Z1 | 47489 | VESTAS-WTG1 | 0.72 | : |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44881Z1 | lhfrt | 44881 | CMBHL W1 | 0.6 | Z1 | : | [5 empty] | #9 | 60 | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456871 | lhfrt | 45687 | JACKSON1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0.11667 | 30.0667 | 30.0667 | 7.5667 | 0.81667 | 0.11667 | 0 | 0 | 0 | 0 | 0
456891 | lhfrt | 45689 | JACKSON2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0.11667 | 30.0667 | 30.0667 | 7.5667 | 0.81667 | 0.11667 | 0 | 0 | 0 | 0 | 0
456901 | lhfrt | 45690 | JACKSON34 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0.11667 | 30.0667 | 30.0667 | 7.5667 | 0.81667 | 0.11667 | 0 | 0 | 0 | 0 | 0
456902 | lhfrt | 45690 | JACKSON34 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0.11667 | 30.0667 | 30.0667 | 7.5667 | 0.81667 | 0.11667 | 0 | 0 | 0 | 0 | 0
515581 | lhfrt | 51558 | DKW G1 | 1 | 1 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
515592 | lhfrt | 51559 | DKW G2 | 1 | 2 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
515603 | lhfrt | 51560 | DKW G3 | 1 | 3 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
515614 | lhfrt | 51561 | DKW G4 | 1 | 4 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
515625 | lhfrt | 51562 | DKW G5 | 1 | 5 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
515636 | lhfrt | 51563 | DKW G6 | 1 | 6 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
811431 | lhfrt | 81143 | MLW W | 0.4 | 1 | : | [5 empty] | #9 | 60 | 1.6 | 1.8 | -1.6 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 1 | 40 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
516861 | lhfrt | 51686 | BMW .4W1 | 0.4 | 1 | 51686 | BMW .4W1 | 0.4 | 1 | 1 | : | #9 | 60 | -3.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
516872 | lhfrt | 51687 | BMW .4W2 | 0.4 | 2 | 51687 | BMW .4W2 | 0.4 | 1 | 1 | : | #9 | 60 | -3.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
516883 | lhfrt | 51688 | BMW .4W3 | 0.4 | 3 | 51688 | BMW .4W3 | 0.4 | 1 | 1 | : | #9 | 60 | -3.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
516894 | lhfrt | 51689 | BMW .4W4 | 0.4 | 4 | 51689 | BMW .4W4 | 0.4 | 1 | 1 | : | #9 | 60 | -3.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
804611 | lhfrt | 80461 | ZBK .4 | 0.4 | 1 | 80459 | ZBW 230 | 230 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
804622 | lhfrt | 80462 | SUW .4 | 0.4 | 2 | 80459 | ZBW 230 | 230 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
804501 | lhfrt | 80450 | MKL .6W1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3 | -5 | -9 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 63 | 1.05 | 0.2625 | 63 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
804512 | lhfrt | 80451 | MKL .6W2 | 0.69 | 2 | : | [5 empty] | #9 | 60 | -3 | -5 | -9 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 63 | 1.05 | 0.2625 | 63 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
804523 | lhfrt | 80452 | MKL .6W3 | 0.69 | 3 | : | [5 empty] | #9 | 60 | -3 | -5 | -9 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 63 | 1.05 | 0.2625 | 63 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
804534 | lhfrt | 80453 | MKL .6W4 | 0.69 | 4 | : | [5 empty] | #9 | 60 | -3 | -5 | -9 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 63 | 1.05 | 0.2625 | 63 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
804545 | lhfrt | 80454 | MKL .6W5 | 0.69 | 5 | : | [5 empty] | #9 | 60 | -3 | -5 | -9 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 63 | 1.05 | 0.2625 | 63 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
810216 | lhfrt | 81021 | MKL .6W6 | 0.69 | 6 | : | [5 empty] | #9 | 60 | -3 | -5 | -9 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 63 | 1.05 | 0.2625 | 63 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
807901 | lhfrt | 80790 | PWF .5W | 0.56 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
810891 | lhfrt | 81089 | SWF .5W | 0.56 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
805411 | lhfrt | 80541 | CSS .6A | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
805412 | lhfrt | 80541 | CSS .6A | 0.69 | 2 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
805413 | lhfrt | 80541 | CSS .6A | 0.69 | 3 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
805444 | lhfrt | 80544 | CSS .6A | 0.69 | 4 | : | [5 empty] | #9 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
509591 | lhfrt | 50959 | BR1_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509602 | lhfrt | 50960 | BR1_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509613 | lhfrt | 50961 | BR1_G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509624 | lhfrt | 50962 | BR1_G4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509635 | lhfrt | 50963 | BR2_G5 | 13.8 | 5 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509646 | lhfrt | 50964 | BR2_G6 | 13.8 | 6 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509657 | lhfrt | 50965 | BR2_G7 | 13.8 | 7 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509668 | lhfrt | 50966 | BR2_G8 | 13.8 | 8 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500001 | lhfrt | 50000 | CMS_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500012 | lhfrt | 50001 | CMS_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500021 | lhfrt | 50002 | COM_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
550151 | lhfrt | 55015 | FNG_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
550192 | lhfrt | 55019 | FNG_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.2 | -1.6 | -0.9 | 0.6 | 1.7 | 2.3 | 0 | 0 | 0 | 0 | 7.5 | 60 | 400 | 400 | 30 | 2 | 0 | 0 | 0 | 0 | 0
504951 | lhfrt | 50495 | GMS_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5050410 | lhfrt | 50504 | GMS_G10 | 13.8 | 10 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504962 | lhfrt | 50496 | GMS_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504973 | lhfrt | 50497 | GMS_G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504984 | lhfrt | 50498 | GMS_G4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504995 | lhfrt | 50499 | GMS_G5 | 13.8 | 5 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505006 | lhfrt | 50500 | GMS_G6 | 13.8 | 6 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505017 | lhfrt | 50501 | GMS_G7 | 13.8 | 7 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505028 | lhfrt | 50502 | GMS_G8 | 13.8 | 8 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505039 | lhfrt | 50503 | GMS_G9 | 13.8 | 9 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516281 | lhfrt | 51628 | JHN_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2 | 1.5 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 30 | 90 | 180 | 0.5 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
516292 | lhfrt | 51629 | JHN_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | -2 | 1.5 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 30 | 90 | 180 | 0.5 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
516303 | lhfrt | 51630 | JHN_G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | -2 | 1.5 | 3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 30 | 90 | 180 | 0.5 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
503061 | lhfrt | 50306 | JOR_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507691 | lhfrt | 50769 | KCL_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507702 | lhfrt | 50770 | KCL_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507713 | lhfrt | 50771 | KCL_G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507724 | lhfrt | 50772 | KCL_G4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506371 | lhfrt | 50637 | MCA_G1 | 16 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506382 | lhfrt | 50638 | MCA_G2 | 16 | 2 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506393 | lhfrt | 50639 | MCA_G3 | 16 | 3 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506404 | lhfrt | 50640 | MCA_G4 | 16 | 4 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
511255 | lhfrt | 51125 | MCA_G5 | 16 | 5 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
511266 | lhfrt | 51126 | MCA_G6 | 16 | 6 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505131 | lhfrt | 50513 | PCN_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505142 | lhfrt | 50514 | PCN_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505153 | lhfrt | 50515 | PCN_G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505164 | lhfrt | 50516 | PCN_G4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502991 | lhfrt | 50299 | PUN_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506441 | lhfrt | 50644 | REV_G1 | 16 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506452 | lhfrt | 50645 | REV_G2 | 16 | 2 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506463 | lhfrt | 50646 | REV_G3 | 16 | 3 | : | [5 empty] | #9 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506474 | lhfrt | 50647 | REV_G4 | 16 | 4 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510325 | lhfrt | 51032 | REV_G5 | 16 | 5 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507661 | lhfrt | 50766 | SEV_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507672 | lhfrt | 50767 | SEV_G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507683 | lhfrt | 50768 | SEV_G3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510364 | lhfrt | 51036 | SEV_G4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | 3.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501691 | lhfrt | 50169 | WAH_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506431 | lhfrt | 50643 | WGS_G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804551 | lhfrt | 80455 | QTY .69W1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | 1.06 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 1
804562 | lhfrt | 80456 | QTY .69W2 | 0.69 | 2 | : | [5 empty] | #9 | 60 | 1.06 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 1
804573 | lhfrt | 80457 | QTY .69W3 | 0.69 | 3 | : | [5 empty] | #9 | 60 | 1.06 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 1
804584 | lhfrt | 80458 | QTY .69W4 | 0.69 | 4 | : | [5 empty] | #9 | 60 | 1.06 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 1
521441 | lhfrt | 52144 | ALH-G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
521452 | lhfrt | 52145 | ALH-G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
521611 | lhfrt | 52161 | WAN-G1 | 14.4 | 1 | : | [5 empty] | #9 | 60 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
521622 | lhfrt | 52162 | WAN-G2 | 14.4 | 2 | : | [5 empty] | #9 | 60 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
521661 | lhfrt | 52166 | WAX13G1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.6 | -2.6 | -1.6 | -0.6 | 0.6 | 1.6 | 2.6 | 4.8 | 0 | 0 | 2 | 10 | 60 | 660 | 600 | 60 | 10 | 2 | 0 | 0 | 0
521672 | lhfrt | 52167 | WAX13G2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3.6 | -2.6 | -1.6 | -0.6 | 0.6 | 1.6 | 2.6 | 4.8 | 0 | 0 | 2 | 10 | 60 | 660 | 600 | 60 | 10 | 2 | 0 | 0 | 0
565002G1 | lhfrt | 565002 | GARDENPLAIN1 | 0.69 | G1 | : | [5 empty] | #9 | 60 | -12.01 | -4.81 | -3.61 | 12.01 | 4.81 | 3.61 | 0 | 0 | 0 | 0 | 0.01 | 0.1 | 0.2 | 0.01 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0
5600961 | lhfrt | 560096 | PLNW_GEN | 0.69 | 1 | 560096 | : |  |  |  |  | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561990G2 | lhfrt | 561990 | SHAMROC6 0.65 | 0.65 | G2 | 561990 | : |  |  |  |  | #9 | 60 | 0.94 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560894G1 | lhfrt | 560894 | CLARESHOLM1 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -3 | -1.7 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 1
561632G1 | lhfrt | 561632 | BADLAND6 | 0.69 | G1 | : | [5 empty] | #9 | 60 | -12.01 | -4.81 | -3.61 | 12.01 | 4.81 | 3.61 | 0 | 0 | 0 | 0 | 0.01 | 0.1 | 0.2 | 0.01 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 1
593393 | lhfrt | 59339 | SUMV6 | 1 | 3 | : | [5 empty] | #9 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593393 | lhfrt | 59339 | SUMV6 | 1 | 3 | : | [5 empty] | #9 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593374 | lhfrt | 59337 | SUMV7 | 1 | 4 | : | [5 empty] | #9 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593374 | lhfrt | 59337 | SUMV7 | 1 | 4 | : | [5 empty] | #9 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
567031G1 | lhfrt | 567031 | WINDRISE1 | 0.69 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.2 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 200 | 0.01 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560045G1 | lhfrt | 560045 | Test | 0.69 | G1 | : | [5 empty] | #9 | 60 | -12 | -4.8 | -3.6 | 12 | 4.8 | 3.6 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.1 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0
54266G1 | lhfrt | 54266 | EMPRESA7 | 138 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54266G1 | lhfrt | 54266 | EMPRESA7 | 138 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54266G1 | lhfrt | 54266 | EMPRESA7 | 138 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54266G1 | lhfrt | 54266 | EMPRESA7 | 138 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542701 | lhfrt | 54270 | SUFFIEL7 | 138 | 1 | : | [5 empty] | #1 | 60 | -6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542701 | lhfrt | 54270 | SUFFIEL7 | 138 | 1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542701 | lhfrt | 54270 | SUFFIEL7 | 138 | 1 | : | [5 empty] | #1 | 60 | -160 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542701 | lhfrt | 54270 | SUFFIEL7 | 138 | 1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54275G1 | lhfrt | 54275 | TILLEY 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54275G1 | lhfrt | 54275 | TILLEY 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54275G1 | lhfrt | 54275 | TILLEY 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54275G1 | lhfrt | 54275 | TILLEY 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G1 | lhfrt | 54590 | ENMX24S7 | 138 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G1 | lhfrt | 54590 | ENMX24S7 | 138 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G1 | lhfrt | 54590 | ENMX24S7 | 138 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G1 | lhfrt | 54590 | ENMX24S7 | 138 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G2 | lhfrt | 54590 | ENMX24S7 | 138 | G2 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G2 | lhfrt | 54590 | ENMX24S7 | 138 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G2 | lhfrt | 54590 | ENMX24S7 | 138 | G2 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G2 | lhfrt | 54590 | ENMX24S7 | 138 | G2 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G3 | lhfrt | 54590 | ENMX24S7 | 138 | G3 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G3 | lhfrt | 54590 | ENMX24S7 | 138 | G3 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G3 | lhfrt | 54590 | ENMX24S7 | 138 | G3 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590G3 | lhfrt | 54590 | ENMX24S7 | 138 | G3 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590X1 | lhfrt | 54590 | ENMX24S7 | 138 | X1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590X1 | lhfrt | 54590 | ENMX24S7 | 138 | X1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590X1 | lhfrt | 54590 | ENMX24S7 | 138 | X1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54590X1 | lhfrt | 54590 | ENMX24S7 | 138 | X1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54798G1 | lhfrt | 54798 | HALSBRG1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -13 | -8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54798G1 | lhfrt | 54798 | HALSBRG1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -4.81 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | -2.7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | -0.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.05 | 180.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | -3.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | -2.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.55 | 7.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | -1.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.05 | 30.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55119G1 | lhfrt | 55119 | GOODFAR7 | 138 | G1 | : | [5 empty] | #1 | 60 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -3.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -2.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.55 | 7.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -0.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.05 | 180.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -1.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.05 | 30.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | -2.7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G1 | lhfrt | 55135 | WAPITI 7 | 138 | G1 | : | [5 empty] | #1 | 60 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | -3.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | -2.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.55 | 7.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | -1.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.05 | 30.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | -0.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.05 | 180.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55135G2 | lhfrt | 55135 | WAPITI 7 | 138 | G2 | : | [5 empty] | #1 | 60 | -2.7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55798G2 | lhfrt | 55798 | HALSBRG2 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -4.81 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56308G1 | lhfrt | 56308 | G1_LV | 0.72 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56308G1 | lhfrt | 56308 | G1_LV | 0.72 | G1 | : | [5 empty] | #1 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.45 | 4.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.73 | 10.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.64 | 259.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.23 | 112.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242.5 | 242.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.98 | 20.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -2.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.52 | 48.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -0.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1792.11 | 1792.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -2.19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56401G2 | lhfrt | 56401 | HULL25 | 25 | G2 | : | [5 empty] | #1 | 60 | -1.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.82 | 32.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
568581 | lhfrt | 56858 | SODER5 | 0.57 | 1 | : | [5 empty] | #1 | 60 | -3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 1.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
568581 | lhfrt | 56858 | SODER5 | 0.57 | 1 | : | [5 empty] | #1 | 60 | -2.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.08 | 10.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
568581 | lhfrt | 56858 | SODER5 | 0.57 | 1 | : | [5 empty] | #1 | 60 | -5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.08 | 30.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56990G1 | lhfrt | 56990 | SHAMROC5 | 0.65 | G1 | : | [5 empty] | #1 | 60 | -4.8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G1 | lhfrt | 57286 | ENCHANT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G1 | lhfrt | 57286 | ENCHANT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G1 | lhfrt | 57286 | ENCHANT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -1.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G1 | lhfrt | 57286 | ENCHANT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -3.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G2 | lhfrt | 57286 | ENCHANT8 | 25 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G2 | lhfrt | 57286 | ENCHANT8 | 25 | G2 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G2 | lhfrt | 57286 | ENCHANT8 | 25 | G2 | : | [5 empty] | #1 | 60 | -1.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57286G2 | lhfrt | 57286 | ENCHANT8 | 25 | G2 | : | [5 empty] | #1 | 60 | -3.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57462G1 | lhfrt | 57462 | WR2WF4 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -4.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57462G1 | lhfrt | 57462 | WR2WF4 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57462G1 | lhfrt | 57462 | WR2WF4 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57462G1 | lhfrt | 57462 | WR2WF4 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57462G1 | lhfrt | 57462 | WR2WF4 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57735G2 | lhfrt | 57735 | ARD_04 | 1 | G2 | : | [5 empty] | #1 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57735G2 | lhfrt | 57735 | ARD_04 | 1 | G2 | : | [5 empty] | #1 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
578582 | lhfrt | 57858 | SODER6 | 0.57 | 2 | : | [5 empty] | #1 | 60 | -3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 1.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
578582 | lhfrt | 57858 | SODER6 | 0.57 | 2 | : | [5 empty] | #1 | 60 | -2.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.08 | 10.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
578582 | lhfrt | 57858 | SODER6 | 0.57 | 2 | : | [5 empty] | #1 | 60 | -5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.08 | 30.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58235G1 | lhfrt | 58235 | STAVELY9 | 25 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58235G1 | lhfrt | 58235 | STAVELY9 | 25 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58235G1 | lhfrt | 58235 | STAVELY9 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58235G1 | lhfrt | 58235 | STAVELY9 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58244G1 | lhfrt | 58244 | VULCAN 9 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58244G1 | lhfrt | 58244 | VULCAN 9 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58244G1 | lhfrt | 58244 | VULCAN 9 | 25 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58244G1 | lhfrt | 58244 | VULCAN 9 | 25 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.23 | 112.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -1.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.82 | 32.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -0.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1792.11 | 1792.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242.5 | 242.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.73 | 10.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -2.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -2.19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.52 | 48.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.64 | 259.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -20 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.98 | 20.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58274G2 | lhfrt | 58274 | VAUXHAL9 | 25 | G2 | : | [5 empty] | #1 | 60 | -2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.45 | 4.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G3 | lhfrt | 58286 | ENCHANT9 | 25 | G3 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G3 | lhfrt | 58286 | ENCHANT9 | 25 | G3 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G3 | lhfrt | 58286 | ENCHANT9 | 25 | G3 | : | [5 empty] | #1 | 60 | -1.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G3 | lhfrt | 58286 | ENCHANT9 | 25 | G3 | : | [5 empty] | #1 | 60 | -3.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G4 | lhfrt | 58286 | ENCHANT9 | 25 | G4 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G4 | lhfrt | 58286 | ENCHANT9 | 25 | G4 | : | [5 empty] | #1 | 60 | -1.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G4 | lhfrt | 58286 | ENCHANT9 | 25 | G4 | : | [5 empty] | #1 | 60 | -3.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58286G4 | lhfrt | 58286 | ENCHANT9 | 25 | G4 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58831G1 | lhfrt | 58831 | SEDALIA6 | 0.72 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58831G1 | lhfrt | 58831 | SEDALIA6 | 0.72 | G1 | : | [5 empty] | #1 | 60 | -13 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593374 | lhfrt | 59337 | SUMV7 | 1 | 4 | : | [5 empty] | #1 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593374 | lhfrt | 59337 | SUMV7 | 1 | 4 | : | [5 empty] | #1 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593393 | lhfrt | 59339 | SUMV6 | 1 | 3 | : | [5 empty] | #1 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593393 | lhfrt | 59339 | SUMV6 | 1 | 3 | : | [5 empty] | #1 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59416G1 | lhfrt | 59416 | LANESLK8 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59416G1 | lhfrt | 59416 | LANESLK8 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -4.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59416G1 | lhfrt | 59416 | LANESLK8 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59416G1 | lhfrt | 59416 | LANESLK8 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59416G1 | lhfrt | 59416 | LANESLK8 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59740G1 | lhfrt | 59740 | ARD_07 | 1 | G1 | : | [5 empty] | #1 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59740G1 | lhfrt | 59740 | ARD_07 | 1 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59799G3 | lhfrt | 59799 | HALSBURG3 | 0.69 | G3 | : | [5 empty] | #1 | 60 | -13 | -8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59799G3 | lhfrt | 59799 | HALSBURG3 | 0.69 | G3 | : | [5 empty] | #1 | 60 | -4.81 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542269G1 | lhfrt | 542269 | BURDETT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542269G1 | lhfrt | 542269 | BURDETT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542269G1 | lhfrt | 542269 | BURDETT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542269G1 | lhfrt | 542269 | BURDETT8 | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552340G1 | lhfrt | 552340 | ESSP-1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552340G1 | lhfrt | 552340 | ESSP-1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552340G1 | lhfrt | 552340 | ESSP-1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552340G1 | lhfrt | 552340 | ESSP-1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552433G1 | lhfrt | 552433 | P2059_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552433G1 | lhfrt | 552433 | P2059_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552433G1 | lhfrt | 552433 | P2059_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552433G1 | lhfrt | 552433 | P2059_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552448G1 | lhfrt | 552448 | P1978_G1 | 0.66 | G1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552448G1 | lhfrt | 552448 | P1978_G1 | 0.66 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552448G1 | lhfrt | 552448 | P1978_G1 | 0.66 | G1 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552448G1 | lhfrt | 552448 | P1978_G1 | 0.66 | G1 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552450G3 | lhfrt | 552450 | P1978_G3 | 0.66 | G3 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552450G3 | lhfrt | 552450 | P1978_G3 | 0.66 | G3 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552450G3 | lhfrt | 552450 | P1978_G3 | 0.66 | G3 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552450G3 | lhfrt | 552450 | P1978_G3 | 0.66 | G3 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553246G1 | lhfrt | 553246 | SPRING12 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -3.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553246G1 | lhfrt | 553246 | SPRING12 | 0.55 | G1 | : | [5 empty] | #1 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553246G1 | lhfrt | 553246 | SPRING12 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -1.5 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553246G1 | lhfrt | 553246 | SPRING12 | 0.55 | G1 | : | [5 empty] | #1 | 60 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553256G1 | lhfrt | 553256 | BROOKS01 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553256G1 | lhfrt | 553256 | BROOKS01 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553256G1 | lhfrt | 553256 | BROOKS01 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553256G1 | lhfrt | 553256 | BROOKS01 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553291G2 | lhfrt | 553291 | CONRAD2 | 0.55 | G2 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553291G2 | lhfrt | 553291 | CONRAD2 | 0.55 | G2 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553291G2 | lhfrt | 553291 | CONRAD2 | 0.55 | G2 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553291G2 | lhfrt | 553291 | CONRAD2 | 0.55 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553340G1 | lhfrt | 553340 | ESSP-1 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553340G1 | lhfrt | 553340 | ESSP-1 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553340G1 | lhfrt | 553340 | ESSP-1 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553340G1 | lhfrt | 553340 | ESSP-1 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553448G2 | lhfrt | 553448 | P1978_G2 | 0.66 | G2 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553448G2 | lhfrt | 553448 | P1978_G2 | 0.66 | G2 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553448G2 | lhfrt | 553448 | P1978_G2 | 0.66 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553448G2 | lhfrt | 553448 | P1978_G2 | 0.66 | G2 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554257G2 | lhfrt | 554257 | BROOKS02 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554257G2 | lhfrt | 554257 | BROOKS02 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554257G2 | lhfrt | 554257 | BROOKS02 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554257G2 | lhfrt | 554257 | BROOKS02 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554291G1 | lhfrt | 554291 | CONRAD1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554291G1 | lhfrt | 554291 | CONRAD1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554291G1 | lhfrt | 554291 | CONRAD1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554291G1 | lhfrt | 554291 | CONRAD1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554400G1 | lhfrt | 554400 | MONARCH10 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554400G1 | lhfrt | 554400 | MONARCH10 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554400G1 | lhfrt | 554400 | MONARCH10 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554400G1 | lhfrt | 554400 | MONARCH10 | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5544011 | lhfrt | 554401 | HAYS 49 | 0.63 | 1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5544011 | lhfrt | 554401 | HAYS 49 | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5544011 | lhfrt | 554401 | HAYS 49 | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5544011 | lhfrt | 554401 | HAYS 49 | 0.63 | 1 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554448G1 | lhfrt | 554448 | P2061_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554448G1 | lhfrt | 554448 | P2061_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554448G1 | lhfrt | 554448 | P2061_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554448G1 | lhfrt | 554448 | P2061_1 | 0.55 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554692G2 | lhfrt | 554692 | COALDA10 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554692G2 | lhfrt | 554692 | COALDA10 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554692G2 | lhfrt | 554692 | COALDA10 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554692G2 | lhfrt | 554692 | COALDA10 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554693G3 | lhfrt | 554693 | COALDA11 | 0.63 | G3 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554693G3 | lhfrt | 554693 | COALDA11 | 0.63 | G3 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554693G3 | lhfrt | 554693 | COALDA11 | 0.63 | G3 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554693G3 | lhfrt | 554693 | COALDA11 | 0.63 | G3 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554986G1 | lhfrt | 554986 | P1840DG | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554986G1 | lhfrt | 554986 | P1840DG | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554986G1 | lhfrt | 554986 | P1840DG | 0.63 | G1 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554986G1 | lhfrt | 554986 | P1840DG | 0.63 | G1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557051G1 | lhfrt | 557051 | WHTCRST9 | 0.6 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557051G1 | lhfrt | 557051 | WHTCRST9 | 0.6 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557051G1 | lhfrt | 557051 | WHTCRST9 | 0.6 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557051G1 | lhfrt | 557051 | WHTCRST9 | 0.6 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557269G1 | lhfrt | 557269 | BURDETTSOLAR | 25 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557269G1 | lhfrt | 557269 | BURDETTSOLAR | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557269G1 | lhfrt | 557269 | BURDETTSOLAR | 25 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557269G1 | lhfrt | 557269 | BURDETTSOLAR | 25 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557277G1 | lhfrt | 557277 | WESTFIELDGEN | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557277G1 | lhfrt | 557277 | WESTFIELDGEN | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557277G1 | lhfrt | 557277 | WESTFIELDGEN | 0.63 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557277G1 | lhfrt | 557277 | WESTFIELDGEN | 0.63 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
558316G1 | lhfrt | 558316 | P2249_GEN | 0.66 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
558316G1 | lhfrt | 558316 | P2249_GEN | 0.66 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
558316G1 | lhfrt | 558316 | P2249_GEN | 0.66 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
558316G1 | lhfrt | 558316 | P2249_GEN | 0.66 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560026G1 | lhfrt | 560026 | TRAVERS_1A | 0.63 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560026G1 | lhfrt | 560026 | TRAVERS_1A | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560026G1 | lhfrt | 560026 | TRAVERS_1A | 0.63 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560026G1 | lhfrt | 560026 | TRAVERS_1A | 0.63 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560641G1 | lhfrt | 560641 | FORTYMILE1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560873G1 | lhfrt | 560873 | RATTLESNK_3 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -4.81 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560873G1 | lhfrt | 560873 | RATTLESNK_3 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 12.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560873G1 | lhfrt | 560873 | RATTLESNK_3 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 4.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560873G1 | lhfrt | 560873 | RATTLESNK_3 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560873G1 | lhfrt | 560873 | RATTLESNK_3 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.61 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560873G1 | lhfrt | 560873 | RATTLESNK_3 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 3.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561026G2 | lhfrt | 561026 | TRAVERS_1B | 0.63 | G2 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561026G2 | lhfrt | 561026 | TRAVERS_1B | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561026G2 | lhfrt | 561026 | TRAVERS_1B | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561026G2 | lhfrt | 561026 | TRAVERS_1B | 0.63 | G2 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561641G2 | lhfrt | 561641 | FORTYMILE3 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561894G2 | lhfrt | 561894 | CLARESHOLM6 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561894G2 | lhfrt | 561894 | CLARESHOLM6 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561894G2 | lhfrt | 561894 | CLARESHOLM6 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561894G2 | lhfrt | 561894 | CLARESHOLM6 | 0.63 | G2 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561994G1 | lhfrt | 561994 | GRANLEA6 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 3.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561994G1 | lhfrt | 561994 | GRANLEA6 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 12.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561994G1 | lhfrt | 561994 | GRANLEA6 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561994G1 | lhfrt | 561994 | GRANLEA6 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.61 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561994G1 | lhfrt | 561994 | GRANLEA6 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 4.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561994G1 | lhfrt | 561994 | GRANLEA6 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -4.81 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562026G3 | lhfrt | 562026 | TRAVERS_1C | 0.63 | G3 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562026G3 | lhfrt | 562026 | TRAVERS_1C | 0.63 | G3 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562026G3 | lhfrt | 562026 | TRAVERS_1C | 0.63 | G3 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562026G3 | lhfrt | 562026 | TRAVERS_1C | 0.63 | G3 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562240G1 | lhfrt | 562240 | TCE_SOLR | 0.69 | G1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562240G1 | lhfrt | 562240 | TCE_SOLR | 0.69 | G1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562240G1 | lhfrt | 562240 | TCE_SOLR | 0.69 | G1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562240G1 | lhfrt | 562240 | TCE_SOLR | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562418G2 | lhfrt | 562418 | LANESLK14 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -4.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562418G2 | lhfrt | 562418 | LANESLK14 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562418G2 | lhfrt | 562418 | LANESLK14 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562418G2 | lhfrt | 562418 | LANESLK14 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562418G2 | lhfrt | 562418 | LANESLK14 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562994G2 | lhfrt | 562994 | GRANLEA7 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -12.01 | 12.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562994G2 | lhfrt | 562994 | GRANLEA7 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -12.01 | 3.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562994G2 | lhfrt | 562994 | GRANLEA7 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -3.61 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562994G2 | lhfrt | 562994 | GRANLEA7 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -4.81 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562994G2 | lhfrt | 562994 | GRANLEA7 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -12.01 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562994G2 | lhfrt | 562994 | GRANLEA7 | 0.69 | G2 | : | [5 empty] | #1 | 60 | -12.01 | 4.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
563308G3 | lhfrt | 563308 | G3_LV | 0.72 | G3 | : | [5 empty] | #1 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
563308G3 | lhfrt | 563308 | G3_LV | 0.72 | G3 | : | [5 empty] | #1 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
564990G3 | lhfrt | 564990 | SHAMROC8 | 0.65 | G3 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565002G1 | lhfrt | 565002 | GARDENPLAIN1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565002G1 | lhfrt | 565002 | GARDENPLAIN1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -4.81 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565002G1 | lhfrt | 565002 | GARDENPLAIN1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -3.61 | 12.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565002G1 | lhfrt | 565002 | GARDENPLAIN1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 12.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565002G1 | lhfrt | 565002 | GARDENPLAIN1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 4.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565002G1 | lhfrt | 565002 | GARDENPLAIN1 | 0.69 | G1 | : | [5 empty] | #1 | 60 | -12.01 | 3.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565308G2 | lhfrt | 565308 | G2_LV | 0.72 | G2 | : | [5 empty] | #1 | 60 | -3.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565308G2 | lhfrt | 565308 | G2_LV | 0.72 | G2 | : | [5 empty] | #1 | 60 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59011G1 | lhfrt | 59011 | WINDYGS1 | 0.69 | G1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56990G1 | lhfrt | 56990 | SHAMROC5 0.65 | 0.65 | G1 | 56990 | : |  |  |  |  | #9 | 60 | 0.92 | 1.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603281 | lhfrt | 60328 | JPSR_GEN | 0.63 | 1 | 60328 | JPSR_GEN | 0.63 | : |  |  | #1 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
606731 | lhfrt | 60673 | PVS1_PV | 0.6 | 1 | 60670 | PVS1 | 230 | 1 | 1 | : | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180.01 | 30.01 | 0.16 | 180.01 | 30.01 | 7.51 | 0.76 | 0.16 | 0 | 0 | 0
619901 | lhfrt | 61990 | PCSR_GEN | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
619941 | lhfrt | 61994 | MHSL_GEN | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.3 | 120 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600041 | lhfrt | 60004 | HMWY_BAT | 34.5 | 1 | : | [5 empty] | #9 | 60 | -5 | 5 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
605321 | lhfrt | 60532 | BMSU_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
605301 | lhfrt | 60530 | BMSU_BAT | 0.48 | 1 | : | [5 empty] | #9 | 60 | -5 | 5 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600031 | lhfrt | 60003 | HMWYT501 | 34.5 | 1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
6107711 | lhfrt | 610771 | UNTY-012 | 0.31 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 3 | 180 | 30 | 7.5 | 0.3 | 0 | 0 | 0 | 0
6103811 | lhfrt | 610381 | JMSN-011 | 0.48 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 3 | 180 | 30 | 7.5 | 1 | 0 | 0 | 0 | 0
6100711 | lhfrt | 610071 | CARO-12.5 | 0.6 | 1 | : | [5 empty] | #9 | 60 | 0.5 | 2 | -1.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.16 | 300 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603271 | lhfrt | 60327 | JKPT_GEN | 0.63 | 1 | 60327 | JKPT_GEN | 0.63 | : |  |  | #9 | 60 | -0.6 | -1.6 | -3 | 0.6 | 1.6 | 1.8 | 2 | 0 | 0 | 0 | 1300 | 30 | 0.1 | 600 | 30 | 0.1 | 0.04 | 0 | 0 | 0 | 0
600251 | lhfrt | 60025 | AMERFLS1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600252 | lhfrt | 60025 | AMERFLS2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600253 | lhfrt | 60025 | AMERFLS3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600361 | lhfrt | 60036 | BLISS 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600371 | lhfrt | 60037 | BLISS 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600381 | lhfrt | 60038 | BLISS 3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600961 | lhfrt | 60096 | BRWNL 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600971 | lhfrt | 60097 | BRWNL 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600981 | lhfrt | 60098 | BRWNL 3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600991 | lhfrt | 60099 | BRWNL 4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601001 | lhfrt | 60100 | BRWNL 5 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601161 | lhfrt | 60116 | SHSNFALS | 6.6 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601511 | lhfrt | 60151 | HELSCYN1 | 14.4 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601521 | lhfrt | 60152 | HELSCYN2 | 14.4 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601531 | lhfrt | 60153 | HELSCYN3 | 14.4 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601961 | lhfrt | 60196 | L MALAD | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602011 | lhfrt | 60201 | L SAMN 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602021 | lhfrt | 60202 | L SAMN 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602031 | lhfrt | 60203 | L SAMN 3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602041 | lhfrt | 60204 | L SAMN 4 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602461 | lhfrt | 60246 | MILNER | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602462 | lhfrt | 60246 | MILNER | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60268C1 | lhfrt | 60268 | CC_CT C1 | 16.5 | C1 | : | [5 empty] | #9 | 60 | -4.6 | -3 | 1.8 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60269S1 | lhfrt | 60269 | CC_ST S1 | 13.8 | S1 | : | [5 empty] | #9 | 60 | -3 | -1.2 | 1.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 180 | 180 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602761 | lhfrt | 60276 | OXBOW1-2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602762 | lhfrt | 60276 | OXBOW1-2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602773 | lhfrt | 60277 | OXBOW3-4 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602774 | lhfrt | 60277 | OXBOW3-4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603211 | lhfrt | 60321 | STRIKE 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603221 | lhfrt | 60322 | STRIKE 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603231 | lhfrt | 60323 | STRIKE 3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603311 | lhfrt | 60331 | SWANFALL | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603312 | lhfrt | 60331 | SWANFALL | 6.9 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603521 | lhfrt | 60352 | TWINFALS | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603531 | lhfrt | 60353 | TWINFALS | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603611 | lhfrt | 60361 | U SAMN 1 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603621 | lhfrt | 60362 | U SAMN 2 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603631 | lhfrt | 60363 | U SAMN 3 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603641 | lhfrt | 60364 | U SAMN 4 | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60391C1 | lhfrt | 60391 | DNPR CT1 | 18 | C1 | : | [5 empty] | #9 | 60 | -3.2 | -2.5 | -1.5 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0.117 | 10 | 600 | 180 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
60392C2 | lhfrt | 60392 | DNPR CT2 | 12 | C2 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
60393C3 | lhfrt | 60393 | DNPR CT3 | 12 | C3 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
60397C1 | lhfrt | 60397 | BTMT CT1 | 18 | C1 | : | [5 empty] | #9 | 60 | -3.6 | -2.5 | 2.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 10 | 10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600321 | lhfrt | 60032 | TUANAGEN | 0.69 | 1 | 61916 | TUANAGEN | 138 | 1 | : |  | #9 | 60 | -3.6 | -6 | -9 | 3.6 | 6 | 0 | 0 | 0 | 0 | 0 | 10.1 | 1.01 | 0.26 | 10.01 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0
601211 | lhfrt | 60121 | AFSR_GEN | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.15 | 0.0001 | 0.0001 | 0
603671 | lhfrt | 60367 | HGWP_GEN | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
604171 | lhfrt | 60417 | HIGHMESA | 0.6 | 1 | : | [5 empty] | #9 | 60 | 3 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
604311 | lhfrt | 60431 | BCS GEN | 0.385 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.008334 | 180 | 30 | 7.5 | 0.5 | 0.008334 | 0.008334 | 0.008334 | 0
609951 | lhfrt | 60995 | RKWP_GEN | 0.7 | 1 | 60997 | RKWP_SUB | 34.5 | : |  |  | #9 | 60 | 5 | 2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.33 | 1 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610151 | lhfrt | 61015 | CSCAD PP | 6.9 | 1 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610152 | lhfrt | 61015 | CSCAD PP | 6.9 | 2 | : | [5 empty] | #9 | 60 | -3 | 1.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612931 | lhfrt | 61293 | BTCKWIND | 0.6 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
613001 | lhfrt | 61300 | GVSR_GEN | 0.41 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.008334 | 180 | 30 | 7.5 | 0.5 | 0.008334 | 0.008334 | 0.008334 | 0
6193812 | lhfrt | 61938 | CAWP_12_GEN | 0.6 | 12 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
619433 | lhfrt | 61943 | CAWP_3_GEN | 0.6 | 3 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603671 | lhfrt | 60367 | HGWP_GEN | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
604411 | lhfrt | 60441 | FKLN_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.61 | -3.1 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 0.15 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
604421 | lhfrt | 60442 | FKLN_BS | 0.63 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225731 | lhfrt | 622573 | SOUTHPK GEN1 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225731 | lhfrt | 622573 | SOUTHPK GEN1 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225741 | lhfrt | 622574 | SOUTHPK GEN2 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225741 | lhfrt | 622574 | SOUTHPK GEN2 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235651 | lhfrt | 623565 | MT SUN PVGEN | 0.63 | 1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235651 | lhfrt | 623565 | MT SUN PVGEN | 0.63 | 1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235651 | lhfrt | 623565 | MT SUN PVGEN | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235651 | lhfrt | 623565 | MT SUN PVGEN | 0.63 | 1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235661 | lhfrt | 623566 | MDWLRK SOLAR | 0.6 | 1 | 623266 | MDWLRK SOLAR | 161 | 1 | 1 | : | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235661 | lhfrt | 623566 | MDWLRK SOLAR | 0.6 | 1 | 623266 | MDWLRK SOLAR | 161 | 1 | 1 | : | #1 | 60 | -2.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.05 | 10.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235661 | lhfrt | 623566 | MDWLRK SOLAR | 0.6 | 1 | 623266 | MDWLRK SOLAR | 161 | 1 | 1 | : | #1 | 60 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235661 | lhfrt | 623566 | MDWLRK SOLAR | 0.6 | 1 | 623266 | MDWLRK SOLAR | 161 | 1 | 1 | : | #1 | 60 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235031 | lhfrt | 623503 | COLSTRIP GN3 | 26 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
6235041 | lhfrt | 623504 | COLSTRIP GN4 | 26 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0
6215511 | lhfrt | 621551 | APEX_GEN1 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215511 | lhfrt | 621551 | APEX_GEN1 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215511 | lhfrt | 621551 | APEX_GEN1 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215511 | lhfrt | 621551 | APEX_GEN1 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -160 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215511 | lhfrt | 621551 | APEX_GEN1 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -160 | 1.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215511 | lhfrt | 621551 | APEX_GEN1 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -160 | 1.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215521 | lhfrt | 621552 | APEX_GEN2 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -1.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215521 | lhfrt | 621552 | APEX_GEN2 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215521 | lhfrt | 621552 | APEX_GEN2 | 0.8 | 1 | : | [5 empty] | #1 | 60 | -3.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215521 | lhfrt | 621552 | APEX_GEN2 | 0.8 | 1 | : | [5 empty] | #1 | 60 | 40 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215521 | lhfrt | 621552 | APEX_GEN2 | 0.8 | 1 | 621551 | APEX_GEN1 | 0.8 | 1 | 1 | : | #1 | 60 | -160 | 1.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215521 | lhfrt | 621552 | APEX_GEN2 | 0.8 | 1 | 621551 | APEX_GEN1 | 0.8 | 1 | 1 | : | #1 | 60 | -160 | 1.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215531 | lhfrt | 621553 | APEX_ESS | 0.69 | 1 | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235211 | lhfrt | 623521 | CLRWTR GEN 1 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235211 | lhfrt | 623521 | CLRWTR GEN 1 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235221 | lhfrt | 623522 | CLRWTR GEN 2 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235221 | lhfrt | 623522 | CLRWTR GEN 2 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235231 | lhfrt | 623523 | CLRWTR GEN 3 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235231 | lhfrt | 623523 | CLRWTR GEN 3 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235241 | lhfrt | 623524 | CLRWTR GEN 4 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235241 | lhfrt | 623524 | CLRWTR GEN 4 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235251 | lhfrt | 623525 | CLRWTR GEN 5 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235251 | lhfrt | 623525 | CLRWTR GEN 5 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235261 | lhfrt | 623526 | CLRWTR GEN 6 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235261 | lhfrt | 623526 | CLRWTR GEN 6 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235271 | lhfrt | 623527 | CLRWTR GEN 7 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235271 | lhfrt | 623527 | CLRWTR GEN 7 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235281 | lhfrt | 623528 | CLRWTR GEN 8 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6235281 | lhfrt | 623528 | CLRWTR GEN 8 | 0.69 | 1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225311 | lhfrt | 622531 | RYAN GEN1-3 | 6.6 | 1 | : | [5 empty] | #1 | 60 | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225312 | lhfrt | 622531 | RYAN GEN1-3 | 6.6 | 2 | : | [5 empty] | #1 | 60 | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225313 | lhfrt | 622531 | RYAN GEN1-3 | 6.6 | 3 | : | [5 empty] | #1 | 60 | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225324 | lhfrt | 622532 | RYAN GEN4-6 | 6.6 | 4 | : | [5 empty] | #1 | 60 | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225325 | lhfrt | 622532 | RYAN GEN4-6 | 6.6 | 5 | : | [5 empty] | #1 | 60 | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225326 | lhfrt | 622532 | RYAN GEN4-6 | 6.6 | 6 | : | [5 empty] | #1 | 60 | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6245111 | lhfrt | 624511 | JUDTHGAP GN1 | 0.57 | 1 | : | [5 empty] | #1 | 60 | -3.6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 1.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6245111 | lhfrt | 624511 | JUDTHGAP GN1 | 0.57 | 1 | : | [5 empty] | #1 | 60 | -3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.08 | 31.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6245112 | lhfrt | 624511 | JUDTHGAP GN1 | 0.57 | 2 | : | [5 empty] | #1 | 60 | -2.7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 1.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6245112 | lhfrt | 624511 | JUDTHGAP GN1 | 0.57 | 2 | : | [5 empty] | #1 | 60 | -1.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.08 | 31.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225151 | lhfrt | 622515 | RAINBOW GEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295211 | lhfrt | 629521 | THOMPSNGN1-3 | 6.6 | 1 | : | [5 empty] | #9 | 60 | -4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295212 | lhfrt | 629521 | THOMPSNGN1-3 | 6.6 | 2 | : | [5 empty] | #9 | 60 | -4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295213 | lhfrt | 629521 | THOMPSNGN1-3 | 6.6 | 3 | : | [5 empty] | #9 | 60 | -4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295224 | lhfrt | 629522 | THOMPSNGN4-6 | 6.6 | 4 | : | [5 empty] | #9 | 60 | -4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295225 | lhfrt | 629522 | THOMPSNGN4-6 | 6.6 | 5 | : | [5 empty] | #9 | 60 | -4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295226 | lhfrt | 629522 | THOMPSNGN4-6 | 6.6 | 6 | : | [5 empty] | #9 | 60 | -4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295247 | lhfrt | 629524 | THOMPSNGN7 | 13.8 | 7 | : | [5 empty] | #9 | 60 | -4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215311 | lhfrt | 621531 | DAVEGATESGN1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215321 | lhfrt | 621532 | DAVEGATESGN2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6215331 | lhfrt | 621533 | DAVEGATESGN3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6245311 | lhfrt | 624531 | GORDONBUTTE1 | 0.69 | 1 | : | [5 empty] | #9 | 60 | -3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295111 | lhfrt | 629511 | EKI - SKQ Dam Unit #1 | 13.8 | 1 | : | #9 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295121 | lhfrt | 629512 | EKI - SKQ Dam Unit #2 | 13.8 | 1 | : | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6295131 | lhfrt | 629513 | EKI - SKQ Dam Unit #3 | 13.8 | 1 | : | #9 | 60 | -4 | -3.1 | -2 | 1.8 | 2 | 4 | 0 | 0 | 0 | 0 | 0.167 | 0.03 | 60 | 0.03 | 60 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225511 | lhfrt | 622551 | MORONY GEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -6 | -3.1 | 1.8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225512 | lhfrt | 622551 | MORONY GEN | 13.8 | 2 | : | [5 empty] | #9 | 60 | -6 | -3.1 | 1.8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6225411 | lhfrt | 622541 | COCHRANE GEN | 13.8 | 1 | : | [5 empty] | #9 | 60 | -6 | -4 | -2 | 2 | 4 | 5 | 6 | 0 | 0 | 0 | 10 | 10 | 60 | 60 | 10 | 10 | 10 | 0 | 0 | 0 | 0
6225412 | lhfrt | 622541 | COCHRANE GEN | 13.8 | 2 | : | [5 empty] | #9 | 60 | -6 | -4 | -2 | 2 | 4 | 5 | 6 | 0 | 0 | 0 | 10 | 10 | 60 | 60 | 10 | 10 | 10 | 0 | 0 | 0 | 0
6417531 | lhfrt | 641753 | TS SOLAR1 PV | 0.69 | 1 | 641753 | TS SOLAR1 PV | 0.69 | 1 | 1 | : | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
6417551 | lhfrt | 641755 | TS SOLAR2 PV | 0.69 | 1 | 641755 | TS SOLAR2 PV | 0.69 | 1 | 1 | : | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
6414461 | lhfrt | 641446 | LIBRA PV1 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
6414511 | lhfrt | 641451 | LIBRA PV2 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
6414561 | lhfrt | 641456 | LIBRA PV3 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
6414611 | lhfrt | 641461 | LIBRA PV4 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
6414661 | lhfrt | 641466 | LIBRA PV5 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
6414471 | lhfrt | 641447 | LIBRA BS1 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 5 | 3.5 | 2 | -2 | -3.5 | -5 | 0 | 0 | 0 | 0 | 0.1 | 1 | 300 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0
6414521 | lhfrt | 641452 | LIBRA BS2 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 5 | 3.5 | 2 | -2 | -3.5 | -5 | 0 | 0 | 0 | 0 | 0.1 | 1 | 300 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0
6414571 | lhfrt | 641457 | LIBRA BS3 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 5 | 3.5 | 2 | -2 | -3.5 | -5 | 0 | 0 | 0 | 0 | 0.1 | 1 | 300 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0
6414621 | lhfrt | 641462 | LIBRA BS4 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 5 | 3.5 | 2 | -2 | -3.5 | -5 | 0 | 0 | 0 | 0 | 0.1 | 1 | 300 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0
6414671 | lhfrt | 641467 | LIBRA BS5 G | 0.66 | 1 | 641442 | LIBRA SLR HV | 345 | 1 | 1 | : | #9 | 60 | 5 | 3.5 | 2 | -2 | -3.5 | -5 | 0 | 0 | 0 | 0 | 0.1 | 1 | 300 | 300 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0
6412611 | lhfrt | 641261 | SIERRA2_PV | 0.6 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0.3 | 0.75 | 7.5 | 30 | 180 | 0.2 | 30 | 180 | 0.008334 | 0.008334 | 0
6412531 | lhfrt | 641253 | SIERRA_PV | 0.6 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.7 | 1.6 | 0.6 | 0 | 0 | 0.3 | 0.75 | 7.5 | 30 | 180 | 0.2 | 30 | 180 | 0.008334 | 0.008334 | 0
649291 | lhfrt | 64929 | BATMNPV-G | 0.63 | 1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 0.5 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6411271 | lhfrt | 641127 | DGEFLT_PV | 0.63 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6411281 | lhfrt | 641128 | DGEFLT_BS | 0.645 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6409111 | lhfrt | 640911 | FISHSP_PV | 0.63 | 1 | 64900 | FT SAGE | 345 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6409121 | lhfrt | 640912 | FISHSP_BS | 0.645 | 1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6401731 | lhfrt | 640173 | TURQ_GEN50 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.5 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
6401751 | lhfrt | 640175 | TURQ_GEN10 | 0.645 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647881 | lhfrt | 64788 | STEAMGEOLS | 12.47 | 1 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 2.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647882 | lhfrt | 64788 | STEAMGEOLS | 12.47 | 2 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 2.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645381 | lhfrt | 64538 | SPRING VAL G | 0.69 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649231 | lhfrt | 64923 | MCGINESS2 | 12 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.1 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649232 | lhfrt | 64923 | MCGINESS2 | 12 | 2 | : | [5 empty] | #9 | 60 | -3 | -2.1 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649233 | lhfrt | 64923 | MCGINESS2 | 12 | 3 | : | [5 empty] | #9 | 60 | -3 | -2.1 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649561 | lhfrt | 64956 | MCGINESS | 12 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.1 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649562 | lhfrt | 64956 | MCGINESS | 12 | 2 | : | [5 empty] | #9 | 60 | -3 | -2.1 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649563 | lhfrt | 64956 | MCGINESS | 12 | 3 | : | [5 empty] | #9 | 60 | -3 | -2.1 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641201 | lhfrt | 64120 | TRACY G4 | 14 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 7.5 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0
641211 | lhfrt | 64121 | TRACY G5 | 14 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 7.5 | 30 | 180 | 30 | 0 | 0 | 0 | 0 | 0
644691 | lhfrt | 64469 | DESRT P2 | 14 | 1 | : | [5 empty] | #8 | 60 | -3.5 | -6 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644692 | lhfrt | 64469 | DESRT P2 | 14 | 2 | : | [5 empty] | #8 | 60 | -3.5 | -6 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649311 | lhfrt | 64931 | TUNGSTEN P1 | 12 | 1 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 2.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649651 | lhfrt | 64965 | MCGINESS3 | 12 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.8 | -1.6 | -0.7 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0.5 | 0.75 | 30 | 180 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0
649652 | lhfrt | 64965 | MCGINESS3 | 12 | 2 | : | [5 empty] | #9 | 60 | -3 | -2.8 | -1.6 | -0.7 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0.5 | 0.75 | 30 | 180 | 30 | 0.5 | 0 | 0 | 0 | 0 | 0
6400631 | lhfrt | 640063 | LUNING G | 0.55 | 1 | : | [5 empty] | #9 | 60 | 0.62 | 1.6 | 1.7 | 5 | -0.62 | -1.6 | -2.2 | -2.7 | -3 | -5 | 180 | 30 | 10 | 0.001 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0.001 | 0
640281 | lhfrt | 64028 | CLARKMT3 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640291 | lhfrt | 64029 | CLARKMT4 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640461 | lhfrt | 64046 | FT CH G1 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640471 | lhfrt | 64047 | FT CH G2 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641051 | lhfrt | 64105 | CAITHNES | 12.3 | 1 | : | [5 empty] | #8 | 60 | 1 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641061 | lhfrt | 64106 | STILLWTR-GEO | 13.8 | 1 | : | [5 empty] | #8 | 60 | 1.7 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.05 | 180 | 180 | 30 | 7.5 | 0.05 | 0 | 0 | 0 | 0 | 0
641062 | lhfrt | 64106 | STILLWTR-GEO | 13.8 | 2 | : | [5 empty] | #8 | 60 | 1.7 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.05 | 180 | 180 | 30 | 7.5 | 0.05 | 0 | 0 | 0 | 0 | 0
641063 | lhfrt | 64106 | STILLWTR-GEO | 13.8 | 3 | : | [5 empty] | #8 | 60 | 1.7 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.05 | 180 | 180 | 30 | 7.5 | 0.05 | 0 | 0 | 0 | 0 | 0
641064 | lhfrt | 64106 | STILLWTR-GEO | 13.8 | 4 | : | [5 empty] | #8 | 60 | 1.7 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.05 | 180 | 180 | 30 | 7.5 | 0.05 | 0 | 0 | 0 | 0 | 0
641191 | lhfrt | 64119 | TRACY G3 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -3 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 0 | 0 | 0 | 0 | 0.05 | 7.5 | 30 | 180 | 180 | 0.05 | 0 | 0 | 0 | 0 | 0
641311 | lhfrt | 64131 | VALMY G1 | 22 | 1 | : | [5 empty] | #8 | 60 | -1.2 | -3 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641321 | lhfrt | 64132 | VALMY G2 | 18 | 1 | : | [5 empty] | #8 | 60 | -3 | -3.5 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641501 | lhfrt | 64150 | BEOWAWE | 4.16 | 1 | : | [5 empty] | #8 | 60 | 3 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641502 | lhfrt | 64150 | BEOWAWE | 4.16 | 2 | : | [5 empty] | #8 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641591 | lhfrt | 64159 | FAR WST1 | 4.16 | 1 | : | [5 empty] | #8 | 60 | 1 | -0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641592 | lhfrt | 64159 | FAR WST1 | 4.16 | 2 | : | [5 empty] | #8 | 60 | 1 | -0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641603 | lhfrt | 64160 | FAR WST2 | 4.16 | 3 | : | [5 empty] | #8 | 60 | 1 | -0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641604 | lhfrt | 64160 | FAR WST2 | 4.16 | 4 | : | [5 empty] | #8 | 60 | 1 | -0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642671 | lhfrt | 64267 | JERSEYV | 13.8 | 1 | : | [5 empty] | #8 | 60 | -3 | -3.2 | 3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642672 | lhfrt | 64267 | JERSEYV | 13.8 | 2 | : | [5 empty] | #8 | 60 | -3 | -3.2 | 3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
643112 | lhfrt | 64311 | WILDROSE2 | 12.47 | 2 | : | [5 empty] | #8 | 60 | -2.1 | -3 | 2.1 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644641 | lhfrt | 64464 | DOVEGEN2 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644642 | lhfrt | 64464 | DOVEGEN2 | 13.8 | 2 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644643 | lhfrt | 64464 | DOVEGEN2 | 13.8 | 3 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644644 | lhfrt | 64464 | DOVEGEN2 | 13.8 | 4 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644645 | lhfrt | 64464 | DOVEGEN2 | 13.8 | 5 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644646 | lhfrt | 64464 | DOVEGEN2 | 13.8 | 6 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644647 | lhfrt | 64464 | DOVEGEN2 | 13.8 | 7 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644651 | lhfrt | 64465 | DOVEGEN1 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644652 | lhfrt | 64465 | DOVEGEN1 | 13.8 | 2 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644653 | lhfrt | 64465 | DOVEGEN1 | 13.8 | 3 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644654 | lhfrt | 64465 | DOVEGEN1 | 13.8 | 4 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644655 | lhfrt | 64465 | DOVEGEN1 | 13.8 | 5 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644656 | lhfrt | 64465 | DOVEGEN1 | 13.8 | 6 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644657 | lhfrt | 64465 | DOVEGEN1 | 13.8 | 7 | : | [5 empty] | #8 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644671 | lhfrt | 64467 | GALENA | 13.8 | 1 | : | [5 empty] | #8 | 60 | -3.5 | -6 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644672 | lhfrt | 64467 | GALENA | 13.8 | 2 | : | [5 empty] | #8 | 60 | -3.5 | -6 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644701 | lhfrt | 64470 | GALENA3 | 13.8 | 1 | : | [5 empty] | #8 | 60 | -3.5 | -6 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644702 | lhfrt | 64470 | GALENA3 | 13.8 | 2 | : | [5 empty] | #8 | 60 | -3.5 | -6 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644881 | lhfrt | 64488 | PATUA | 12.47 | 1 | : | [5 empty] | #8 | 60 | -2 | -3 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 30 | 60 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644882 | lhfrt | 64488 | PATUA | 12.47 | 2 | : | [5 empty] | #8 | 60 | -2 | -3 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 30 | 60 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644883 | lhfrt | 64488 | PATUA | 12.47 | 3 | : | [5 empty] | #8 | 60 | -2 | -3 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 30 | 60 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645021 | lhfrt | 64502 | SALTWELL | 4.16 | 1 | : | [5 empty] | #8 | 60 | 1.7 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.05 | 180 | 180 | 30 | 7.5 | 0.05 | 0 | 0 | 0 | 0 | 0
645771 | lhfrt | 64577 | WILDROSE | 12.47 | 1 | : | [5 empty] | #8 | 60 | -2.1 | -3 | 2.1 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647891 | lhfrt | 64789 | TUSCARORA | 12.47 | 1 | : | [5 empty] | #8 | 60 | -3 | -3.2 | 3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647892 | lhfrt | 64789 | TUSCARORA | 12.47 | 2 | : | [5 empty] | #8 | 60 | -3 | -3.2 | 3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
648551 | lhfrt | 64855 | NEWMONT | 18 | 1 | : | [5 empty] | #8 | 60 | -1.6 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649451 | lhfrt | 64945 | USGEMPR1 | 12.47 | 1 | : | [5 empty] | #8 | 60 | 0.6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649521 | lhfrt | 64952 | TRACY W8 | 18 | 1 | : | [5 empty] | #8 | 60 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649531 | lhfrt | 64953 | TRACY W9 | 18 | 1 | : | [5 empty] | #8 | 60 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649541 | lhfrt | 64954 | TRACYW10 | 18 | 1 | : | [5 empty] | #8 | 60 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640981 | lhfrt | 64098 | SODAPH2 | 13.8 | 1 | : | [5 empty] | #8 | 60 | 1.75 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
643461 | lhfrt | 64346 | CRSNT DUNE | 18 | 1 | : | [5 empty] | #8 | 60 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6411731 | lhfrt | 641173 | HOTPOT_PV1 | 0.38 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6411761 | lhfrt | 641176 | HOTPOT_PV2 | 0.38 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6411791 | lhfrt | 641179 | HOTPOT_PV3 | 0.38 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6412121 | lhfrt | 641212 | IRONPT2_PV1 | 0.38 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6412151 | lhfrt | 641215 | IRONPT2_PV2 | 0.38 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -1.6 | 2.2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677851 | lhfrt | 67785 | JACK_WND2 | 0.69 | 1 | 60342 | JACK | 345 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677771 | lhfrt | 67777 | JACK_WND1 | 0.69 | 1 | 60342 | JACK | 345 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
660061 | lhfrt | 66006 | CLOVERCK_SG | 0.63 | 1 | 66006 | CLOVERCK_SG | 0.63 | 1 | 1 | : | #9 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
690401 | lhfrt | 69040 | HINSHAW_WG | 0.69 | 1 | 69040 | HINSHAW_WG | 0.69 | 1 | 1 | : | #9 | 60 | -4.8 | -3 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 2 | 90 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663281 | lhfrt | 66328 | SWEETWTR_SG | 0.55 | 1 | : | [5 empty] | #9 | 60 | -2.5 | -1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 300 | 200 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697821 | lhfrt | 69782 | SIGURD_SG | 0.63 | 1 | 69779 | SIGURD_HS | 230 | 1 | 1 | : | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697861 | lhfrt | 69786 | MILFORD_SG | 0.63 | 1 | 69783 | PEARSON | 345 | 1 | 1 | : | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 5000 | 0.2 | 650 | 5000 | 0 | 0 | 0 | 0
697901 | lhfrt | 69790 | COVE MTN1_SG | 0.63 | 1 | : | [5 empty] | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0.1 | 30.01 | 180.01 | 180.01 | 30.01 | 7.51 | 0.1 | 0 | 0 | 0 | 0
697941 | lhfrt | 69794 | COVE MTN2_SG | 0.63 | 1 | : | [5 empty] | #1 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30.01 | 180.01 | 180.01 | 30.01 | 7.51 | 0.76 | 0.1 | 0 | 0 | 0
697981 | lhfrt | 69798 | HUNTER_SG | 0.63 | 1 | 69798 | HUNTER_SG | 0.63 | 1 | 1 | : | #9 | 60 | 0.7 | 2 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0.5 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
676871 | lhfrt | 67687 | EKOLA_FL1_WG | 0.8 | 1 | 67687 | EKOLA_FL1_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
676901 | lhfrt | 67690 | EKOLA_FL2_WG | 0.8 | 1 | 67690 | EKOLA_FL2_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
676971 | lhfrt | 67697 | EKOLA_FL3_WG | 0.69 | 1 | 67697 | EKOLA_FL3_WG | 0.69 | 1 | 1 | : | #9 | 60 | 3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
698281 | lhfrt | 69828 | PRYORMTN1_WG | 0.69 | 1 | 69828 | PRYORMTN1_WG | 0.69 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
698321 | lhfrt | 69832 | PRYORMTN2_WG | 0.69 | 1 | 69832 | PRYORMTN2_WG | 0.69 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
660941 | lhfrt | 66094 | SAGE_SG | 0.55 | 1 | 66090 | SAGE_WY | 69 | 1 | : |  | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | 0 | 0 | 0 | 0.008334 | 30 | 180 | 0.16 | 0.75 | 7.5 | 30 | 0.008334 | 0.008334 | 0.008334 | 0
677131 | lhfrt | 67713 | TB FLAT11_WG | 0.8 | 1 | 67713 | TB FLAT11_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677161 | lhfrt | 67716 | TB FLAT12_WG | 0.8 | 1 | 67716 | TB FLAT12_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677191 | lhfrt | 67719 | TB FLAT13_WG | 0.8 | 1 | 67719 | TB FLAT13_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677241 | lhfrt | 67724 | TB FLAT21_WG | 0.8 | 1 | 67724 | TB FLAT21_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677271 | lhfrt | 67727 | TB FLAT22_WG | 0.8 | 1 | 67727 | TB FLAT22_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
690271 | lhfrt | 69027 | 7MIHILL_WG | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 1
690731 | lhfrt | 69073 | HIPLAINS_WG | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 60 | 0.2625 | 60 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
690321 | lhfrt | 69032 | DUNLAP_WG | 0.69 | 1 | : | [5 empty] | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 60 | 0.2625 | 60 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 1
697531 | lhfrt | 69753 | IRON SPRG_SG | 0.418 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.01 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.01 | 0.008334 | 0.008334 | 0
697651 | lhfrt | 69765 | GRANT MTE_SG | 0.418 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.01 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.01 | 0.008334 | 0.008334 | 0
697691 | lhfrt | 69769 | GRANT MTW_SG | 0.418 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.01 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.01 | 0.008334 | 0.008334 | 0
653861 | lhfrt | 65386 | J BRIDGER G1 | 22 | 1 | 65386 | J BRIDGER G1 | 22 | 1 | 1 | : | #9 | 60 | 1.8 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0
653871 | lhfrt | 65387 | J BRIDGER G2 | 22 | 1 | 65387 | J BRIDGER G2 | 22 | 1 | 1 | : | #9 | 60 | 1.8 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0
690031 | lhfrt | 69003 | GLENROCK_WG | 0.69 | 1 | : | [5 empty] | #9 | 60 | 1.5 | 2.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.02 | 10 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
690041 | lhfrt | 69004 | ROLLNG HL_WG | 0.69 | 1 | : | [5 empty] | #9 | 60 | 1.5 | 2.5 | -2.5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.02 | 10 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697131 | lhfrt | 69713 | RED HILLS_SG | 0.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 180 | 30 | 0.0001 | 180 | 30 | 7.5 | 0.75 | 0.0001 | 0 | 0 | 0
690921 | lhfrt | 69092 | 3BUTTES_WG | 0.69 | 1 | 69092 | 3BUTTES_WG | 0.69 | 1 | 1 | : | #9 | 60 | 2 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 60 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664371 | lhfrt | 66437 | LAKESD1CT1 G | 16.5 | 1 | 66437 | LAKESD1CT1 G | 16.5 | 1 | 1 | : | #9 | 60 | 3 | 2.1 | 1.8 | -2.5 | -3.2 | -3.6 | 0 | 0 | 0 | 0 | 0.1 | 10 | 30 | 10 | 0.12 | 0.1 | 0 | 0 | 0 | 0 | 0
664381 | lhfrt | 66438 | LAKESD1CT2 G | 16.5 | 1 | 66438 | LAKESD1CT2 G | 16.5 | 1 | 1 | : | #9 | 60 | 3 | 2.1 | 1.8 | -2.5 | -3.2 | -3.6 | 0 | 0 | 0 | 0 | 0.1 | 10 | 30 | 10 | 0.12 | 0.1 | 0 | 0 | 0 | 0 | 0
679061 | lhfrt | 67906 | LAKESD2CT1 G | 16.5 | 1 | 67906 | LAKESD2CT1 G | 16.5 | 1 | 1 | : | #9 | 60 | 3.3 | 1.8 | -3 | -4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679071 | lhfrt | 67907 | LAKESD2CT2 G | 16.5 | 1 | 67907 | LAKESD2CT2 G | 16.5 | 1 | 1 | : | #9 | 60 | 3.3 | 1.8 | -3 | -4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679081 | lhfrt | 67908 | LAKESD2ST G | 18 | 1 | 67908 | LAKESD2ST G | 18 | 1 | 1 | : | #9 | 60 | 3.3 | 1.8 | -3 | -4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 30 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656101 | lhfrt | 65610 | GADSBY G3 | 13.8 | 1 | 65610 | GADSBY G3 | 13.8 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.03 | 0 | 0 | 0 | 0 | 0
656121 | lhfrt | 65612 | GADSBY G4 | 13.8 | 1 | 65612 | GADSBY G4 | 13.8 | 1 | 1 | : | #9 | 60 | 1.8 | 1.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 900 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656131 | lhfrt | 65613 | GADSBY G5 | 13.8 | 1 | 65613 | GADSBY G5 | 13.8 | 1 | 1 | : | #9 | 60 | 1.8 | 1.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 900 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656141 | lhfrt | 65614 | GADSBY G6 | 13.8 | 1 | 65614 | GADSBY G6 | 13.8 | 1 | 1 | : | #9 | 60 | 1.8 | 1.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 900 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653911 | lhfrt | 65391 | CURRANTCT1 G | 18 | 1 | 65391 | CURRANTCT1 G | 18 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
653921 | lhfrt | 65392 | CURRANTCT2 G | 18 | 1 | 65392 | CURRANTCT2 G | 18 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
653931 | lhfrt | 65393 | CURRNTS1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
654301 | lhfrt | 65430 | D JOHNSTN G1 | 13.8 | 1 | 65430 | D JOHNSTN G1 | 13.8 | 1 | 1 | : | #9 | 60 | 1.7 | 1.5 | -1.5 | -2.2 | -3.1 | -3.6 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 7.5 | 0.12 | 0.03 | 0 | 0 | 0 | 0 | 0
654351 | lhfrt | 65435 | D JOHNSTN G2 | 13.8 | 1 | 65435 | D JOHNSTN G2 | 13.8 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
654401 | lhfrt | 65440 | D JOHNSTN G3 | 13.8 | 1 | 65440 | D JOHNSTN G3 | 13.8 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
654451 | lhfrt | 65445 | D JOHNSTN G4 | 22 | 1 | 65445 | D JOHNSTN G4 | 22 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
660551 | lhfrt | 66055 | NAUGHTON G1 | 18 | 1 | 66055 | NAUGHTON G1 | 18 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
660601 | lhfrt | 66060 | NAUGHTON G2 | 20 | 1 | 66060 | NAUGHTON G2 | 20 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
660651 | lhfrt | 66065 | NAUGHTON G3 | 24 | 1 | 66065 | NAUGHTON G3 | 24 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
657951 | lhfrt | 65795 | HUNTNGTN G1 | 22 | 1 | 65795 | HUNTNGTN G1 | 22 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
658001 | lhfrt | 65800 | HUNTNGTN G2 | 22 | 1 | 65800 | HUNTNGTN G2 | 22 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
654901 | lhfrt | 65490 | E HUNTER G1 | 24 | 1 | 65490 | E HUNTER G1 | 24 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
654951 | lhfrt | 65495 | E HUNTER G2 | 24 | 1 | 65495 | E HUNTER G2 | 24 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
651701 | lhfrt | 65170 | Blundell 1 | 12.5 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
651711 | lhfrt | 65171 | Blundell 2 | 12.5 | 1 | : | [5 empty] | #9 | 60 | 5 | 4 | 3.5 | 3 | -2.5 | -3 | 0 | 0 | 0 | 0 | 0.03 | 30 | 60 | 10 | 10 | 60 | 0 | 0 | 0 | 0 | 1
656001 | lhfrt | 65600 | GADSBY 1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
656051 | lhfrt | 65605 | GADSBY 2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
653881 | lhfrt | 65388 | BRIDGER3 | 22 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
653891 | lhfrt | 65389 | BRIDGER4 | 22 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
655001 | lhfrt | 65500 | E HUNTER G3 | 22 | 1 | 65500 | E HUNTER G3 | 22 | 1 | 1 | : | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 0
657951 | lhfrt | 65795 | HUNTN G1 | 22 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
658001 | lhfrt | 65800 | HUNTN G2 | 22 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
667301 | lhfrt | 66730 | WYODAK 1 | 22 | 1 | : | [5 empty] | #9 | 60 | 1.8 | 0.6 | -0.6 | -1.6 | -2.2 | -3.2 | 0 | 0 | 0 | 0 | 0.03 | 180 | 180 | 30 | 7.5 | 0.12 | 0 | 0 | 0 | 0 | 1
664391 | lhfrt | 66439 | LAKSDST1 | 16.5 | 1 | : | [5 empty] | #9 | 60 | 3 | 2.1 | 1.8 | -2.5 | -3.2 | -3.6 | 0 | 0 | 0 | 0 | 0.1 | 10 | 30 | 10 | 0.12 | 0.1 | 0 | 0 | 0 | 0 | 1
475881 | lhfrt | 47588 | CHEH G1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -2.2 | -2.7 | -3.1 | -3.2 | -3.5 | -3.6 | 0 | 0.1 | 30 | 180 | 7.5 | 0.8 | 0.75 | 0.1 | 0.12 | 0.1 | 0 | 1
475892 | lhfrt | 47589 | CHEH G2 | 18 | 2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -2.2 | -2.7 | -3.1 | -3.2 | -3.5 | -3.6 | 0 | 0.1 | 30 | 180 | 7.5 | 0.8 | 0.75 | 0.1 | 0.12 | 0.1 | 0 | 1
455461 | lhfrt | 45546 | SWIFT1-3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
453511 | lhfrt | 45351 | YALE GEN | 13.2 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 181 | 31 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
453512 | lhfrt | 45351 | YALE GEN | 13.2 | 2 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 181 | 31 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
475901 | lhfrt | 47590 | CHEH S1 | 18 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -3 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.76 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
697581 | lhfrt | 69758 | STEVENSVL_SG | 0.6 | 1 | : | [5 empty] | #9 | 60 | -0.62 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 1
452561 | lhfrt | 45256 | LEMOLO1 | 12 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
452901 | lhfrt | 45290 | LEMOLO2 | 11.5 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
453401 | lhfrt | 45340 | MERWIN 1 | 13.2 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
453421 | lhfrt | 45342 | MERWIN 2 | 13.2 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
453441 | lhfrt | 45344 | MERWIN 3 | 13.2 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
454861 | lhfrt | 45486 | SLIDECRK | 6.9 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
455441 | lhfrt | 45544 | SWIFT1-1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
455451 | lhfrt | 45545 | SWIFT1-2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 1.5 | -1.5 | -2.1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 30 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
651911 | lhfrt | 65191 | BONANZA | 24 | 1 | : | [5 empty] | #9 | 60 | 1.7 | -0.8 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0 | 0 | 0.03 | 180 | 30 | 7.5 | 0.75 | 0.03 | 0 | 0 | 0 | 0 | 0
655831 | lhfrt | 65583 | FT CREEK_WG | 0.6 | 1 | : | [5 empty] | #9 | 60 | -0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697291 | lhfrt | 69729 | Enterprise Solar, LLC | 138 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
697341 | lhfrt | 69734 | Escalante Solar I | 345 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
697401 | lhfrt | 69740 | Escalante Solar III | 345 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
697481 | lhfrt | 69748 | ROOT CK_LS | 34.5 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697481 | lhfrt | 69748 | ROOT CK_WG | 0.69 | 1 | 69746 | ROOT CK_LS | 34.5 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697481 | lhfrt | 69748 | ROOT CK_WG | 0.69 | 1 | 69748 | ROOT CK_WG | 0.69 | 1 | 1 | : | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
697071 | lhfrt | 69707 | CONCHO WIND | 0.69 | 1 | 69705 | CONCHO | 34.5 | 1 | 1 | : | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697071 | lhfrt | 69707 | CONCHO WIND | 0.69 | 1 | 69707 | CONCHO WIND | 0.69 | 1 | 1 | : | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.2625 | 63 | 1.05 | 0.2625 | 0 | 0 | 0 | 0 | 0 | 0
655861 | lhfrt | 65586 | FT CREEK1_WG | 0.8 | 1 | 65586 | FT CREEK1_WG | 0.8 | 1 | 1 | : | #9 | 60 | 3.6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
660681 | lhfrt | 66068 | NEBOPPGT | 13.8 | 1 | 66068 | NEBOPPGT | 13.8 | 1 | 1 | : | #9 | 60 | 0.7 | 1.7 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0.1 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
660691 | lhfrt | 66069 | NEBOPPST | 13.8 | 1 | 66069 | NEBOPPST | 13.8 | 1 | 1 | : | #9 | 60 | 0.7 | 1.7 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0.1 | 30 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700196W1 | lhfrt | 700196 | LV_WTG | 0.72 | W1 | 700193 | HV_MPT | 345 | 1 | 1 | : | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
700262S | lhfrt | 700262 | SUN_MTN_S | 0.66 | S | 700259 | SN_MTN_S_3 | 230 | : |  |  | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
72746PV | lhfrt | 72746 | GRNTMSA_GEN | 0.63 | PV | 79103 | GARNET M | 115 | 1 | 1 | : | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.008334 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.008334 | 0.008334 | 0.008334 | 0
700076W1 | lhfrt | 700076 | 24_12_W1 | 0.72 | W1 | 700069 | PI_2024_12 | 345 | : |  |  | #99 | 60 | 6 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700077W2 | lhfrt | 700077 | 24_12_W2 | 0.72 | W2 | 700069 | PI_2024_12 | 345 | : |  |  | #99 | 60 | 6 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700078W3 | lhfrt | 700078 | 24_12_W3 | 0.72 | W3 | 700069 | PI_2024_12 | 345 | : |  |  | #99 | 60 | 6 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700151S1 | lhfrt | 700151 | 2021_6_S1 | 34.5 | S1 | 700154 | 2021_6_S1_3 | 230 | : |  |  | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
700182W | lhfrt | 700182 | 24_28_W | 0.69 | W | 700185 | 5RSC_24_28 | 345 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700172S | lhfrt | 700172 | 14_6_S | 0.63 | S | : | [5 empty] | #9 | 60 | 2 | 0.5 | -3 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 600 | 0.15 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700173B | lhfrt | 700173 | 14_6_B | 0.48 | B | : | [5 empty] | #9 | 60 | 1.8 | 1.7 | 0.7 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.02 | 31 | 181 | 181 | 31 | 7.5 | 0.75 | 0.2 | 0 | 0 | 0
700119S1 | lhfrt | 700119 | 21_1_S1 | 0.66 | S1 | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
700120S2 | lhfrt | 700120 | 21_1_S2 | 0.66 | S2 | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
700121S3 | lhfrt | 700121 | 21_1_S3 | 0.66 | S3 | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
700122B1 | lhfrt | 700122 | 21_1_B1 | 0.69 | B1 | : | [5 empty] | #9 | 60 | -1.7 | -3 | 0 | 0 | 0 | 0.7 | 2 | 0 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 0
700123B2 | lhfrt | 700123 | 21_1_B2 | 0.69 | B2 | : | [5 empty] | #9 | 60 | -1.7 | -3 | 0 | 0 | 0 | 0.7 | 2 | 0 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 0
700124B3 | lhfrt | 700124 | 21_1_B3 | 0.69 | B3 | : | [5 empty] | #9 | 60 | -1.7 | -3 | 0 | 0 | 0 | 0.7 | 2 | 0 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 600 | 0.5 | 0 | 0 | 0 | 0
700215S1 | lhfrt | 700215 | 24_1_S1 | 0.66 | S1 | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
700216S2 | lhfrt | 700216 | 24_1_S2 | 0.66 | S2 | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
700217S3 | lhfrt | 700217 | 24_1_S3 | 0.66 | S3 | : | [5 empty] | #8 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
700067W1 | lhfrt | 700067 | 24_13_W1 | 0.72 | W1 | 700066 | PI_2024_13 | 345 | : |  |  | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0
700057W2 | lhfrt | 700057 | 24_13_W2 | 0.72 | W2 | 700066 | PI_2024_13 | 345 | : |  |  | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0
700060W3 | lhfrt | 700060 | 24_13_W3 | 0.72 | W3 | 700066 | PI_2024_13 | 345 | : |  |  | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0
700063W4 | lhfrt | 700063 | 24_13_W4 | 0.72 | W4 | 700066 | PI_2024_13 | 345 | : |  |  | #9 | 60 | -3.6 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0
700004G | lhfrt | 700004 | 24_5_G | 0.48 | G | : | [5 empty] | #1 | 60 | -2 | -3.5 | -5 | 2 | 3.5 | 5 | 0 | 0 | 0 | 0 | 300 | 1 | 0.2 | 300 | 1 | 0.2 | 0 | 0 | 0 | 0 | 0
700079W1 | lhfrt | 700079 | 24_9_W1 | 0.72 | W1 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700082W2 | lhfrt | 700082 | 24_9_W2 | 0.72 | W2 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700085W3 | lhfrt | 700085 | 24_9_W3 | 0.72 | W3 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700088W4 | lhfrt | 700088 | 24_9_W4 | 0.72 | W4 | : | [5 empty] | #1 | 60 | -3.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700100B | lhfrt | 700100 | 24_11_B | 0.66 | B | 700097 | PI_2024_11 | 345 | 1 | 1 | : | #1 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.2 | 0.2 | 6550 | 90 | 5 | 0.2 | 0.2 | 0
700142S1 | lhfrt | 700142 | 20_10_S1 | 0.63 | S1 | : | [5 empty] | #1 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700146S2 | lhfrt | 700146 | 20_10_S2 | 0.63 | S2 | : | [5 empty] | #1 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700144B1 | lhfrt | 700144 | 20_10_B1 | 0.9 | B1 | : | [5 empty] | #1 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
700147B2 | lhfrt | 700147 | 20_10_B2 | 0.9 | B2 | : | [5 empty] | #1 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
700036B | lhfrt | 700036 | 5RSC_24_9_B | 0.63 | B | 700036 | 5RSC_24_9_B | 0.63 | B | 1 | : | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
700222S | lhfrt | 700222 | 24_8_S | 0.63 | S | 700222 | 24_8_S | 0.63 | : |  |  | #99 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700223B | lhfrt | 700223 | 24_8_B | 0.434 | B | 700223 | 24_8_B | 0.434 | : |  |  | #99 | 60 | 3 | 5 | 0 | 0 | 0 | -3 | -5 | 0 | 0 | 0 | 60 | 0.001 | 0 | 0 | 0 | 60 | 0.001 | 0 | 0 | 0 | 0
700044B | lhfrt | 700044 | 24_7_B | 0.9 | B | : | [5 empty] | #9 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
700018S | lhfrt | 700018 | 24_15_S | 34.5 | S | 700016 | 24_15_SB_1 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700020B | lhfrt | 700020 | 24_15_B | 0.645 | B | 700016 | 24_15_SB_1 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700051B | lhfrt | 700051 | 24_16_B | 0.645 | B | 700048 | PI_2024_16 | 345 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700010S | lhfrt | 700010 | 24_17_S | 34.5 | S | 700008 | PI_2024_17 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700043B | lhfrt | 700043 | 24_14_B | 0.645 | B | 700040 | PI_2024_14 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700025S1 | lhfrt | 700025 | 24_18_S1 | 0.66 | S1 | : | [5 empty] | #9 | 60 | 2 | 0.8 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 700 | 600 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700027B1 | lhfrt | 700027 | 24_18_B1 | 0.7 | B1 | : | [5 empty] | #9 | 60 | 2 | 0.8 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 700 | 600 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700029S2 | lhfrt | 700029 | 24_18_S2 | 0.63 | S2 | : | [5 empty] | #9 | 60 | 2 | 0.8 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 700 | 600 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700031B2 | lhfrt | 700031 | 24_18_B2 | 0.63 | B2 | : | [5 empty] | #9 | 60 | 2 | 0.8 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 700 | 600 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -160 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -160 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -160 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -2.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -2.2 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -1.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RH_PV_GEN | 0.6 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -0.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -160 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -160 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -160 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -2.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -2.2 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -1.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78024PV | lhfrt | 78024 | RPS_PV_GEN | 0.42 | PV | 78020 | RAWHIDE_PV | 34.5 | 1 | 1 | : | #1 | 60 | -0.6 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | -0.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6550 | 6550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | -2 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | -5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78034S1 | lhfrt | 78034 | SEV_GEN | 0.66 | S1 | : | [5 empty] | #1 | 60 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78053W1 | lhfrt | 78053 | RD_1_GEN | 0.69 | W1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78053W1 | lhfrt | 78053 | RD_1_GEN | 0.69 | W1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70692S1 | lhfrt | 70692 | 2021-1_S1 | 0.66 | S1 | 70691 | REPL-2021-1 | 230 | : |  |  | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
70682S2 | lhfrt | 70682 | GI-2020-10_S | 0.63 | S2 | : | [5 empty] | #1 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70686S3 | lhfrt | 70686 | GI-2020-10_S | 0.63 | S3 | : | [5 empty] | #1 | 60 | 2 | 0.7 | -1.7 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 600 | 600 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70684B2 | lhfrt | 70684 | GI-2020-10_B | 0.9 | B2 | : | [5 empty] | #1 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
70687B3 | lhfrt | 70687 | GI-2020-10_B | 0.9 | B3 | : | [5 empty] | #1 | 60 | 2 | 2 | 2 | 2 | 0.7 | -3 | -3 | -3 | -3 | -1.7 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0.5 | 0.5 | 0.5 | 0.5 | 600 | 0
70782S1 | lhfrt | 70782 | GI-2020-16_S | 0.66 | S1 | 70779 | GI-2020-16 | 230 | : |  |  | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
70806S1 | lhfrt | 70806 | GI-2021-6_S1 | 34.5 | S1 | 70809 | GI-2021-6_S1 | 230 | : |  |  | #9 | 60 | 3 | 1.7 | -6 | -4 | -3 | 0 | 0 | 0 | 0 | 0 | 2 | 1000 | 5 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
70866S1 | lhfrt | 70866 | GI-2020-1_S1 | 0.66 | S1 | 70869 | GI-2020-1 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70871S2 | lhfrt | 70871 | GI-2020-4_S2 | 0.66 | S2 | 70652 | MIRASOL | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70909S1 | lhfrt | 70909 | GI-2020-3_S1 | 0.66 | S1 | 70905 | GI-2020-3 | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70859S1 | lhfrt | 70859 | SUN_MTN_S1 | 0.66 | S1 | 70856 | SUN_MTN | 230 | : |  |  | #9 | 60 | 5 | 3 | 2 | 0.6 | -5 | -3 | -2.5 | 0 | 0 | 0 | 0.2 | 350 | 650 | 650 | 0.2 | 650 | 650 | 0 | 0 | 0 | 0
70878S1 | lhfrt | 70878 | BIGHORN_S | 0.63 | S1 | : | [5 empty] | #9 | 60 | -3 | -5 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.15 | 60 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70443W1 | lhfrt | 70443 | ARRIBA_W1 | 0.69 | W1 | : | [5 empty] | #9 | 60 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70442W2 | lhfrt | 70442 | ARRIBA_W2 | 0.69 | W2 | : | [5 empty] | #9 | 60 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70704W1 | lhfrt | 70704 | TBI_GEN | 0.575 | W1 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 1.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 1
70010W | lhfrt | 70010 | TWII_GEN | 0.69 | W | : | [5 empty] | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
70708W1 | lhfrt | 70708 | CO_GRN_E GEN | 0.575 | W1 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 1.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 1
70256W2 | lhfrt | 70256 | CO_GRN_W GEN | 0.575 | W2 | : | [5 empty] | #9 | 60 | -3.6 | -3 | 1.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 20 | 31 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 1
70852S1 | lhfrt | 70852 | FRNTRNG_S1 | 0.6 | S1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.5 | -1 | 0 | 0 | 0 | 0 | 2 | 90 | 660 | 10 | 100 | 1800 | 0 | 0 | 0 | 0 | 0
70715W2 | lhfrt | 70715 | SPRNGCAN2_W2 | 0.69 | W2 | 70716 | SPRG_CN2_2 | 34.5 | 1 | 1 | : | #9 | 60 | 3 | 5 | -3 | -5 | -9 | 0 | 0 | 0 | 0 | 0 | 63 | 0.263 | 63 | 1.05 | 0.263 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0.008333 | 0
70635W1 | lhfrt | 70635 | LIMON1_W | 34.5 | W1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70636W2 | lhfrt | 70636 | LIMON2_W | 34.5 | W2 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70637W3 | lhfrt | 70637 | LIMON3_W | 34.5 | W3 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70739W1 | lhfrt | 70739 | CHEYRGW_W1 | 0.69 | W1 | : | [5 empty] | #1 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70742W2 | lhfrt | 70742 | CHEYRGW_W2 | 0.69 | W2 | : | [5 empty] | #1 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70733W1 | lhfrt | 70733 | CHEYRGE_W1 | 0.69 | W1 | : | [5 empty] | #1 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70775W3 | lhfrt | 70775 | CHEYRGE_W3 | 0.69 | W3 | : | [5 empty] | #1 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70736W2 | lhfrt | 70736 | CHEYRGE_W2 | 0.69 | W2 | : | [5 empty] | #1 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70763S1 | lhfrt | 70763 | THNDWLF_S1 | 0.66 | S1 | 70759 | CEP_5_PV_BES | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70761B1 | lhfrt | 70761 | THNDWLF_B1 | 0.48 | B1 | 70759 | CEP_5_PV_BES | 230 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70758S1 | lhfrt | 70758 | NEPTUNE_S1 | 0.66 | S1 | 70754 | CEP_6_PV_BES | 345 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70756B1 | lhfrt | 70756 | NEPTUNE_B1 | 0.48 | B1 | 70754 | CEP_6_PV_BES | 345 | : |  |  | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
709141 | lhfrt | 70914 | CEP7_S1 | 0.63 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1.5 | -1 | 0 | 0 | 0 | 0 | 0.16 | 2 | 540 | 0.16 | 33 | 540 | 0 | 0 | 0 | 0 | 0
73720S1 | lhfrt | 73720 | GYAK_PV1 | 0.6 | S1 | : | [5 empty] | #9 | 60 | 3.5 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78529S1 | lhfrt | 78529 | WC PVPLANT | 0.63 | S1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 0
70502S1 | lhfrt | 70502 | PIONEER_CR_S | 0.645 | S1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -2.2 | -2.7 | 0 | 0 | 0 | 0 | 0.1 | 30 | 180 | 180 | 7.5 | 0.75 | 0 | 0 | 0 | 0 | 0
70767W1 | lhfrt | 70767 | RUSHCK1_W1 | 0.69 | W1 | : | [5 empty] | #1 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70770W2 | lhfrt | 70770 | RUSHCK1_W2 | 0.69 | W2 | : | [5 empty] | #1 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70771W3 | lhfrt | 70771 | RUSHCK2_W3 | 0.69 | W3 | : | [5 empty] | #9 | 1 | -0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70616S1 | lhfrt | 70616 | TITAN_S1 | 0.6 | S1 | : | [5 empty] | #9 | 60 | -3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700171 | lhfrt | 70017 | SI_GEN | 0.6 | 1 | : | [5 empty] | #9 | 60 | 3.25 | 1.8 | 0.6 | -3 | -1 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 650 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 0
70935S1 | lhfrt | 70935 | SUNPOWER | 34.5 | S1 | : | [5 empty] | #9 | 60 | 0.6 | 1.6 | 1.7 | -0.6 | -1.6 | -2.2 | -3 | 0 | 0 | 0 | 180 | 30 | 0.008334 | 180 | 30 | 7.5 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
70933S1 | lhfrt | 70933 | ALMSA_S1 | 0.48 | S1 | : | [5 empty] | #9 | 60 | 2 | 0.7 | -3.1 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 300 | 0.2 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70188G1 | lhfrt | 70188 | FT_LUPTN_12 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 4.8 | 6 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
70188G2 | lhfrt | 70188 | FT_LUPTN_12 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 4.8 | 6 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
70818W1 | lhfrt | 70818 | MTNBRZ_W1 | 34.5 | W1 | : | [5 empty] | #9 | 60 | -5 | -3 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 60 | 60 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70104SC | lhfrt | 70104 | RMOND1 | 230 | SC | : | [5 empty] | #9 | 60 | 4 | 1.6 | 0.6 | -0.6 | -2.2 | -4 | 0 | 0 | 0 | 0 | 2 | 30.5 | 180.5 | 180.5 | 8 | 5 | 0 | 0 | 0 | 0 | 0
70498G3 | lhfrt | 70498 | QF_BCP2T | 13.8 | G3 | : | [5 empty] | #9 | 60 | 1.8 | 1.6 | 0.6 | -0.6 | -1.6 | -2.7 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0
70498ST | lhfrt | 70498 | QF_BCP2T | 13.8 | ST | : | [5 empty] | #9 | 60 | 1.8 | 1.6 | 0.6 | -0.6 | -1.6 | -2.7 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0
71001G1 | lhfrt | 71001 | BAC_MSA GEN1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 183.6 | 3.8 | 0 | 0 | 0 | 0
71002G1 | lhfrt | 71002 | BAC_MSA GEN2 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 183.6 | 3.8 | 0 | 0 | 0 | 0
71003G1 | lhfrt | 71003 | BAC_MSA GEN4 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
71003G2 | lhfrt | 71003 | BAC_MSA GEN4 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
71003S1 | lhfrt | 71003 | BAC_MSA GEN4 | 13.8 | S1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
71004G1 | lhfrt | 71004 | BAC_MSA GEN5 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
71004G2 | lhfrt | 71004 | BAC_MSA GEN5 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
71004S1 | lhfrt | 71004 | BAC_MSA GEN5 | 13.8 | S1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.7 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
71005G1 | lhfrt | 71005 | BAC_MSA GEN6 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 183.6 | 3.18 | 0 | 0 | 0 | 0
70823W1 | lhfrt | 70823 | CEDARCK_1A (GEN MHI) | 34.5 | W1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.1 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.1 | 0 | 0 | 0
70069HA | lhfrt | 70069 | CABCRKA | 13.8 | HA | : | [5 empty] | #9 | 60 | 6 | 2 | -1.8 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70070HB | lhfrt | 70070 | CABCRKB | 13.8 | HB | : | [5 empty] | #9 | 60 | 6 | 2 | -1.8 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70589G2 | lhfrt | 70589 | RMEC2 | 15 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | 1.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.75 | 7.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70486G2 | lhfrt | 70486 | ALMSACT2 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 4.2 | 6 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
70106G4 | lhfrt | 70106 | CHEROK4 | 22 | G4 | : | [5 empty] | #9 | 60 | -3 | 5.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0.008334 | 0
70120C2 | lhfrt | 70120 | Comanche 2 | 24 | C2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 6 | 6.5 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
70145G5 | lhfrt | 70145 | Cherokee 5 | 18 | G5 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.05 | 0 | 0 | 0
70146G6 | lhfrt | 70146 | Cherokee 6 | 18 | G6 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.05 | 0 | 0 | 0
70147ST | lhfrt | 70147 | Cherokee 7 | 18 | ST | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.05 | 0 | 0 | 0
70487G4 | lhfrt | 70487 | JMSHAFR2 | 13.8 | G4 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
70487G5 | lhfrt | 70487 | JMSHAFR2 | 13.8 | G5 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
70490G3 | lhfrt | 70490 | JMSHAFR1 | 13.8 | G3 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
70490ST | lhfrt | 70490 | JMSHAFR1 | 13.8 | ST | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
70493ST | lhfrt | 70493 | JMSHAFR2 | 13.8 | ST | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
70495G1 | lhfrt | 70495 | JMSHAFR1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
70495G2 | lhfrt | 70495 | JMSHAFR1 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.03 | 0.75 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
70499G4 | lhfrt | 70499 | QF_B4-4T | 13.8 | G4 | : | [5 empty] | #9 | 60 | 2 | 1.6 | -0.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 30 | 180 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70499G5 | lhfrt | 70499 | QF_B4-4T | 13.8 | G5 | : | [5 empty] | #9 | 60 | 2 | 1.6 | -0.6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 30 | 180 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70500G1 | lhfrt | 70500 | QF_CPP1T | 13.8 | G1 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70500G2 | lhfrt | 70500 | QF_CPP1T | 13.8 | G2 | : | [5 empty] | #9 | 60 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70501ST | lhfrt | 70501 | QF_CPP3T | 13.8 | ST | : | [5 empty] | #9 | 60 | 2 | 1.6 | 0.6 | -0.6 | -1.6 | -3 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 180 | 30 | 0.75 | 0 | 0 | 0 | 0 | 0
70553G5 | lhfrt | 70553 | Arapahoe Unit 5 | 13.8 | G5 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70553G6 | lhfrt | 70553 | Arapahoe Unit 6 | 13.8 | G6 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70554ST | lhfrt | 70554 | Arapahoe Unit 7 | 13.8 | ST | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70556ST | lhfrt | 70556 | QF_B4D4T | 12.5 | ST | : | [5 empty] | #9 | 60 | 1.6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70557G7 | lhfrt | 70557 | Valmont Unit 7 | 13.8 | G7 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70558G8 | lhfrt | 70558 | Valmont Unit 8 | 13.8 | G8 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70563G2 | lhfrt | 70563 | Blue Spruce 2 | 18 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 6 | 0 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
70565G1 | lhfrt | 70565 | BRTNNUG1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
70566G2 | lhfrt | 70566 | KNUTSON2 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
70577G1 | lhfrt | 70577 | Fountain Valley Unit 1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70577G2 | lhfrt | 70577 | Fountain Valley Unit 2 | 13.8 | G2 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70578G3 | lhfrt | 70578 | Fountain Valley Unit 3 | 13.8 | G3 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70578G4 | lhfrt | 70578 | Fountain Valley Unit 4 | 13.8 | G4 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70579G5 | lhfrt | 70579 | Fountain Valley Unit 5 | 13.8 | G5 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70579G6 | lhfrt | 70579 | Fountain Valley Unit 6 | 13.8 | G6 | : | [5 empty] | #9 | 60 | 1.73 | 1.6 | -2.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0.75 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70585G1 | lhfrt | 70585 | PLNENDG3 | 13.8 | G1 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70585G2 | lhfrt | 70585 | PLNENDG3 | 13.8 | G2 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70585G3 | lhfrt | 70585 | PLNENDG3 | 13.8 | G3 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70585G4 | lhfrt | 70585 | PLNENDG3 | 13.8 | G4 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70585G5 | lhfrt | 70585 | PLNENDG3 | 13.8 | G5 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70585G6 | lhfrt | 70585 | PLNENDG3 | 13.8 | G6 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70585G7 | lhfrt | 70585 | PLNENDG3 | 13.8 | G7 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70586G1 | lhfrt | 70586 | PLNENDG4 | 13.8 | G1 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70586G2 | lhfrt | 70586 | PLNENDG4 | 13.8 | G2 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70586G3 | lhfrt | 70586 | PLNENDG4 | 13.8 | G3 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70586G4 | lhfrt | 70586 | PLNENDG4 | 13.8 | G4 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70586G5 | lhfrt | 70586 | PLNENDG4 | 13.8 | G5 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70586G6 | lhfrt | 70586 | PLNENDG4 | 13.8 | G6 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70586G7 | lhfrt | 70586 | PLNENDG4 | 13.8 | G7 | : | [5 empty] | #9 | 60 | 7.5 | -3 | 1.7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.033333 | 0.033333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70591ST | lhfrt | 70591 | Rocky Mountain Energy Center 3 | 23 | ST | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | 1.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 7.5 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70593G1 | lhfrt | 70593 | GT1 | 18 | G1 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | -2.2 | -2.7 | -3.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.7 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
70594G2 | lhfrt | 70594 | GT2 | 18 | G2 | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | -2.2 | -2.7 | -3.2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 30 | 7.5 | 0.7 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
70721W1 | lhfrt | 70721 | Spring Canyon 2 | 230 | W1 | : | [5 empty] | #9 | 60 | -4 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0.083 | 30 | 180 | 180 | 30 | 0.083 | 0 | 0 | 0 | 0 | 0
70721W1 | lhfrt | 70721 | SPRNGCAN1 | 34.5 | W1 | 73579 | SPRNGCAN | 230 | : |  |  | #9 | 60 | 2.5 | 1.6 | -3.5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 31 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70724W1 | lhfrt | 70724 | Spring Canyon 3 | 230 | W1 | : | [5 empty] | #9 | 60 | -4 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0.083 | 30 | 180 | 180 | 30 | 0.083 | 0 | 0 | 0 | 0 | 0
70951G6 | lhfrt | 70951 | Ft St Vrain 6 | 18 | G6 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 6 | 0 | 0 | 0 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
78011C1 | lhfrt | 78011 | RAWHIDE | 24 | C1 | : | [5 empty] | #9 | 60 | -0.6 | -2.6 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.05 | 180 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
78012GA | lhfrt | 78012 | RAWHIDE | 13.8 | GA | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0.05 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
78013GB | lhfrt | 78013 | RAWHIDE | 13.8 | GB | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0.05 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
78014GC | lhfrt | 78014 | RAWHIDE | 13.8 | GC | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0.05 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
78015GD | lhfrt | 78015 | RAWHIDE | 13.8 | GD | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -2.7 | -3 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.75 | 0.05 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
78016GF | lhfrt | 78016 | RAWHIDE | 18 | GF | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 1.7 | 0 | 0 | 65.535 | 30 | 7.5 | 0.75 | 0.05 | 65.535 | 30 | 0.06 | 0 | 0 | 0
70853B1 | lhfrt | 70853 | T-2021-3_B1 | 0.6 | B1 | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -3.5 | -3.5 | 0.7 | 2 | 3 | 3.5 | 3.5 | 6550 | 90 | 10 | 1 | 1 | 6550 | 90 | 5 | 1 | 1 | 0
73381G1 | lhfrt | 73381 | BIRDSAL1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.14 | 0.75 | 0 | 0 | 0 | 0 | 0
73418C1 | lhfrt | 73418 | RD_NIXON | 20 | C1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.13 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73424H1 | lhfrt | 73424 | Tesla | 13.8 | H1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | -3 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 10 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 0
73434G1 | lhfrt | 73434 | NIXONCT1 | 12.5 | G1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73435G1 | lhfrt | 73435 | NIXONCT2 | 12.5 | G1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72023PV | lhfrt | 72023 | DAVIS_TS | 69 | PV | : | [5 empty] | #9 | 60 | -0.7 | -2 | -3 | -5 | -5 | 0.7 | 2 | 3 | 4 | 4 | 6550 | 90 | 10 | 0.01 | 0.01 | 6550 | 90 | 5 | 0.01 | 0.01 | 0
74635PV | lhfrt | 74635 | FALLRVR_PV | 0.55 | PV | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74635PV | lhfrt | 74635 | FALLRVR_PV | 0.55 | PV | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74635PV | lhfrt | 74635 | FALLRVR_PV | 0.55 | PV | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74635PV | lhfrt | 74635 | FALLRVR_PV | 0.55 | PV | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74712W1 | lhfrt | 74712 | RNDHS_WIND | 0.7 | W1 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74712W1 | lhfrt | 74712 | RNDHS_WIND | 0.7 | W1 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74773W2 | lhfrt | 74773 | RNDHS_WIND2 | 0.7 | W2 | : | [5 empty] | #1 | 60 | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74773W2 | lhfrt | 74773 | RNDHS_WIND2 | 0.7 | W2 | : | [5 empty] | #1 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.08 | 60.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74716PV | lhfrt | 74716 | SOCHEY_PV | 0.6 | PV | : | [5 empty] | #1 | 60 | -3 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74716PV | lhfrt | 74716 | SOCHEY_PV | 0.6 | PV | : | [5 empty] | #1 | 60 | -1.7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74716PV | lhfrt | 74716 | SOCHEY_PV | 0.6 | PV | : | [5 empty] | #1 | 60 | -160 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74716PV | lhfrt | 74716 | SOCHEY_PV | 0.6 | PV | : | [5 empty] | #1 | 60 | -160 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72739W | lhfrt | 72739 | NIYOL_GEN | 0.69 | W | 72738 | NIYOL_LV2 | 34.5 | : |  |  | #9 | 60 | -3 | -5 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0.4 | 60 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72719W | lhfrt | 72719 | CT_GEN | 0.69 | W | : | [5 empty] | #9 | 60 | 1.06 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72703W | lhfrt | 72703 | CRSL_GEN | 0.7 | W | 73036 | BURLNGTN | 230 | : |  |  | #9 | 60 | -3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
732891 | lhfrt | 73289 | RCCT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.0526 | 0.7853 | 7.7855 | 30.8219 | 181.8181 | 189.3069 | 32.0454 | 0.0486 | 0 | 0 | 0
732912 | lhfrt | 73291 | RCCT2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.0526 | 0.7853 | 7.7855 | 30.8219 | 181.8181 | 189.3069 | 32.0454 | 0.0486 | 0 | 0 | 0
732923 | lhfrt | 73292 | RCCT3 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.0526 | 0.7853 | 7.7855 | 30.8219 | 181.8181 | 189.3069 | 32.0454 | 0.0486 | 0 | 0 | 0
732934 | lhfrt | 73293 | RCCT4 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.0526 | 0.7853 | 7.7855 | 30.8219 | 181.8181 | 189.3069 | 32.0454 | 0.0486 | 0 | 0 | 0
74061G1 | lhfrt | 74061 | CPGSTN_1 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.2 | -1.6 | 1.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0.03 | 23.3564 | 90 | 87.6623 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
74061G2 | lhfrt | 74061 | CPGSTN_1 | 13.8 | G2 | : | [5 empty] | #9 | 60 | -3 | -2.2 | -1.6 | 1.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0.03 | 23.3564 | 90 | 87.6623 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
74061S1 | lhfrt | 74061 | CPGSTN_1 | 13.8 | S1 | : | [5 empty] | #9 | 60 | -3 | -1.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74062G1 | lhfrt | 74062 | CPGSTN_2 | 13.8 | G1 | : | [5 empty] | #9 | 60 | -3 | -2.2 | -1.6 | 1.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0.03 | 23.3564 | 90 | 87.6623 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0
740291 | lhfrt | 74029 | LNG_CT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0 | 5 | 30 | 180 | 180 | 30 | 0.0324 | 0 | 0 | 0 | 0 | 0
740141 | lhfrt | 74014 | NSS_CT1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
740151 | lhfrt | 74015 | NSS_CT2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0 | 0.7853 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0
740161 | lhfrt | 74016 | Wygen | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.1 | -2.8 | -2.3 | -1.7 | -0.7 | 0.7 | 1.7 | 1.8 | 0 | 0 | 0.1 | 0.75 | 7.58 | 31.1 | 191.2 | 191.2 | 32.9 | 0.1 | 0 | 0 | 0
740171 | lhfrt | 74017 | Wygen2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3.7 | -2.7 | -2.2 | -1.6 | -0.6 | 0.7 | 1.7 | 1.8 | 0 | 0 | 0.03 | 0.75 | 15 | 30 | 180 | 191.2 | 32.9 | 0.03 | 0 | 0 | 0
740181 | lhfrt | 74018 | Wygen3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 1.7 | 0 | 0 | 0.03 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0.03 | 0 | 0 | 0
796421 | lhfrt | 79642 | NAV1 | 14 | 1 | 79643 | NAVAJO | 115 | : |  |  | #9 | 60 | 1.68 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
796422 | lhfrt | 79642 | NAV1 | 14 | 2 | 79643 | NAVAJO | 115 | : |  |  | #9 | 60 | 1.68 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
731291 | lhfrt | 73129 | MBPP-1 | 24 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3.2 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0
731301 | lhfrt | 73130 | MBPP-2 | 24 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3.2 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0
733021 | lhfrt | 73302 | BRLNGTN1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | 1.7 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 5 | 240 | 1 | 0 | 0 | 0 | 0 | 0 | 0
733031 | lhfrt | 73303 | BRLNGTN2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | 1.7 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 5 | 240 | 1 | 0 | 0 | 0 | 0 | 0 | 0
733412 | lhfrt | 73341 | NSS2 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -0.6 | 0.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 191.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
764041 | lhfrt | 76404 | DRYFRK1 | 19 | 1 | : | [5 empty] | #9 | 60 | 2 | -3 | -3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.37 | 0.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78022PV | lhfrt | 78022 | RAWHIDE | 0.6 | PV | : | [5 empty] | #9 | 60 | 1.7 | 1.6 | 0.6 | -3 | -2.7 | -2.2 | -1.6 | -0.6 | 0 | 0 | 0 | 30 | 180 | 0 | 0.75 | 7.5 | 30 | 180 | 0 | 0 | 0
733831 | lhfrt | 73383 | BIRDSAL3 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 1.7 | 0 | 0 | 0 | 0 | 180 | 30 | 7.5 | 0.75 | 0.14 | 0.75 | 0 | 0 | 0 | 0 | 0
790151 | lhfrt | 79015 | CRAIG 1 | 22 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
790161 | lhfrt | 79016 | CRAIG 2 | 22 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
790171 | lhfrt | 79017 | CRAIG 3 | 22 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
792511 | lhfrt | 79251 | QFATLAS1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
792512 | lhfrt | 79251 | QFATLAS1 | 13.8 | 2 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
792523 | lhfrt | 79252 | QFATLAS2 | 13.8 | 3 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
792524 | lhfrt | 79252 | QFATLAS2 | 13.8 | 4 | : | [5 empty] | #9 | 60 | -2.7 | -2.2 | -1.6 | -0.6 | 0.6 | 1.6 | 0 | 0 | 0 | 0 | 0.75 | 7.5 | 30 | 180 | 180 | 30 | 0 | 0 | 0 | 0 | 0
796121 | lhfrt | 79612 | BLUFFVW13.80 | 14 | 1 | 79614 | BLUFVIEW | 115 | : |  |  | #9 | 60 | 1.68 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
796122 | lhfrt | 79612 | BLUFFVW13.80 | 14 | 2 | 79614 | BLUFVIEW | 115 | : |  |  | #9 | 60 | 1.68 | 1.6 | 0.6 | -0.6 | -1.6 | -2.2 | -2.7 | -3 | 0 | 0 | 0.05 | 30 | 180 | 180 | 30 | 7.5 | 0.75 | 0.05 | 0 | 0 | 0
735321 | lhfrt | 73532 | LINCOLN1 | 13.8 | 1 | : | [5 empty] | #9 | 60 | 0.6 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.99 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
735331 | lhfrt | 73533 | LINCOLN2 | 13.8 | 1 | : | [5 empty] | #9 | 60 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
790401 | lhfrt | 79040 | HAYDEN1 | 18 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 1.6666 | 2.1333 | 2.5 | 3 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
790411 | lhfrt | 79041 | HAYDEN2 | 22 | 1 | : | [5 empty] | #9 | 60 | -3 | -2.7 | -2.2 | -1.6 | 1.6 | 1.7 | 1.8167 | 3 | 3.2167 | 4.45 | 0.05 | 0.75 | 7.5 | 30 | 30 | 0.05 | 0 | 0 | 0 | 0 | 0
73507G1 | lhfrt | 73507 | FTRNG1CC | 18 | G1 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73508G2 | lhfrt | 73508 | FTRNG2CC | 18 | G2 | : | [5 empty] | #9 | 60 | -0.6 | -2.2 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7.5 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73509S1 | lhfrt | 73509 | FTRNG3CC | 21 | S1 | : | [5 empty] | #9 | 60 | -2.2 | -2.7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.75 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ensure this column is text. (Convert to text if necessary, =text(a2,0)