## WI Risk Register
#VALUE! |  | WESTERN INTERCONNECTION RISK REGISTER
Reliability Risks |  |  |  | WECC Risk Management Program Analysis |  |  |  | WECC Reliability Risk Committee Evaluation
ID NO. | CATEGORY | RISK TITLE | RISK STATEMENT (Double click to see more info) | CONSEQUENCE / IMPACT LEVEL | LIKELIHOOD LEVEL | WEIGHTING SCORE | WEIGHTING VALUE | RISK PROBABILITY | MATERIALITY (40%) | CONTROLLABILITY (40%) | SPAN (10%) | VELOCITY (10%) | INITIAL RANKING SCORE | INITIAL RANKING | RISK MITIGATION DECISION | INFORMED RISK MITIGATION DECISION COMMENTARY
CYB-001 | Cybersecurity | Artificial Intelligence | Condition: Successful use of AI for reconnaissance, weaponization, and delivery of an exploit on the WECC top ~20 registered generation entities, or WECC top ~35 registered transmission entities. Consequence: The first significant use of AI against the WI BPS will likely result in a generation loss of <500MW, or loss of a single transmission facility, or inoperability at a single operator. Cause: Public development of AI is rapidly growing and is out of entity control. | Minor | Possible | 7 | Medium-Low | Likely | Low | Uncontrollable | > 2 Months | < Month | 14.8 | Medium | Accept
CYB-002 | Cybersecurity | Compromised Hardware/Software Supply Chain | Condition: Critical/key BPS operations software or microprocessor-based hardware (defined: software/hardware installed on BPS-controlled assets or utilized across 20% of WI operations) within the asset/owner/operator Operational Technology (i.e., SCADA) networks that are actively compromised or have been publicly disclosed as compromisable. Consequence: A critical BA/TOP/GOP asset is compromised or damaged for >30 minutes, impacting >230kV and >500MW. Cause: Intentional compromise of the supplier's assets by a threat actor or unintentional failures due to supplier negligence. | Minor | Unlikely | 6 | Medium-Low | Possible | High Moderate | Low | > 2 Months | Overnight | 12.6 | Medium | Transfer
CYB-004 | Cybersecurity | Insider Threat | Condition: A trusted insider uses their authorized access to deliberately compromise assets or exfiltrate BPS-confidential information for use by a sufficiently resourced external threat (e.g., Nation State). Consequence: Operational loss, control, visibility at a single site, control center, data center impacting an entity until restoration is completed. - or - Loss of BPS-confidential information or credentials that is used to successfully breach an entity. Cause:1. Disgruntled employee 2. Bribe, threat, or coercion of an employee by an external threat actor. | Minor | Possible | 7 | Medium-Low | Almost Certain | High Moderate | Moderate | Days | Overnight | 17.5 | High | Reduce
CYB-005 | Cybersecurity | Internet of Things (IoT) | Condition: Consumer Internet of Things (IoT) devices connected to the grid’s distribution network. Consequence: Malicious threat actors could compromise many high-wattage IoT devices (such as air conditioners, heaters, charging stations, Distributed Energy Resources (DER), etc.) and turn them into a botnet. The malicious actors could then use the botnet to launch a coordinated attack aimed at manipulating the demand across distribution grids. Cause: Because they can. | Minor | Likely | 13 | Medium | Possible | Low | Uncontrollable | > 2 Months | < Month | 11.1 | Medium | Accept
CYB-006 | Cybersecurity | Malware | Condition: Malware infection, from any source, of at least one critical asset within an entity's Operating Technology network. Consequence: Loss of visibility/control at a single entity or single-site operations through ransomware, IOControl Malware, data corruption of control systems, or DoS. Cause: Threat actors motivation to control, damage, or extort. | Minor | Unlikely | 6 | Medium-Low | Almost Certain | Moderate | Moderate | 1-2 Weeks | Overnight | 16 | High | Reduce
CYB-007 | Cybersecurity | Operational Network Breach | Condition: Operational network at a larger entity (CIP Medium/High-impact) successfully compromised by a remote threat actor. Consequence: Leading to inoperability up to 8 hours of >1% of load or > 230kV transmission. Cause:1. Geopolitical motivation to create instability in the BPS or create fear. 2. Ransom | Minor | Possible | 7 | Medium-Low | Possible | High Moderate | Controllable | Hours | Overnight | 7.8 | Medium | Accept
CYB-008 | Cybersecurity | Perimeterless Operational Technology | Condition: Non-entity-owned/controlled assets, systems, or software used to peripherally interact or transmit to operational cyber assets. Consequence: May lead to ineffective change management or misinformation. Impact will likely be case-by-case and on a few assets at a time within a single entity. Cause: Integrating BYOD, IoT, or other external operational technology assets as an extension of the BPS is a growing trend and may be necessary for future operations. | Negligible | Unlikely | 2 | Low | Possible | Low | Strong | > 2 Months | Overnight | 7.8 | Medium | Accept
CYB-009 | Cybersecurity | Phishing and Social Engineering | Condition: Threat actor exploits trusted single insider access to harm critical cyber assets. Consequence: Unauthorized operation of cyber assets. Cause: Desire to control, often financial motivation. | Minor | Likely | 13 | Medium | Likely | Low | Moderate | Hours | Overnight | 10.4 | Medium | Accept
CYB-010 | Cybersecurity | Physical Attacks on Cyber Assets | Condition: Insufficient physical controls to protect against unauthorized physical access to cyber assets. Consequence: Threat actors can exploit hardware and software that they can gain physical access to. Cause: Desire to control. | Minor | Likely | 13 | Medium | Likely | Low | Moderate | Hours | Overnight | 10.4 | Medium | Accept
CYB-011 | Cybersecurity | Public Cloud / Cloud Computing | Condition: Cloud computing is a model for enabling universal, convenient, and on-demand network access to a shared pool of configurable computing resources, such as networks, servers, storage (data), applications, and services that can be quickly provisioned and discarded with minimal internal management effort or interaction with the cloud services provider. Consequence: Using such services to maintain or control Western Interconnection (WI) BPS resources can introduce a new threat vector for threat actors to exploit that is outside the ownership of Registered Entities. Cause: | Moderate | Possible | 16 | High | Unlikely | Moderate | Controllable | 1-2 Months | Overnight | 5 | Low | Accept
CYB-012 | Cybersecurity | Third Party Operations | Condition: Unvetted and unmonitored 3rd-parties operation of cyber assets. Consequence: Unverified security controls of 3rd-parties can lead to unintended misoperation of cyber assets. Cause: 3rd-party operation of cyber assets may be necessary as a cost-benefit and may have improved security controls over what a Registered Entity could afford to implement. | Minor | Likely | 13 | Medium | Possible | Low | Strong | > 2 Months | Overnight | 7.8 | Medium | Accept
CYB-013 | Cybersecurity | Unauthorized Software & Hardware | Condition: Unauthorized software and hardware within an organizational network. This includes authorized software and hardware that is end-of-life or unmaintained to the point of vulnerability. Consequence: Threat actors can exploit hardware and software that is unknown to entity personnel or is in a vulnerable state, leading to attack on the entity network. Cause: Desire to control. | Minor | Unlikely | 6 | Medium-Low | Likely | Low | Controllable | 1-2 Weeks | Overnight | 8 | Medium | Accept
CYB-014 | Cybersecurity | Zero-Day Exploit | Condition: A computer software/firmware vulnerability that is previously unknown to those who are interested in its mitigation and is exploitable from a remote threat across multiple WECC-registered entities or BPS assets. Consequence: Typical infiltration of the asset to allow 1. remote control, or 2. exfiltration of data, or 3. denial of service, or 4. Living-off-land exploit. Cause: A vulnerability unknown to the asset's original software/hardware provider that has not been patched. | Negligible | Unlikely | 2 | Low | Likely | Moderate | Low | Days | Overnight | 14 | Medium | Reduce
CYB-015 | Cybersecurity | Technology Availability Risk | Condition: Out-of-date systems (electro-mechanical) Consequence: Functionally unusable to current staff because of the difference between new and old technology. Systems or data are unavailable to the right people at the right time. Cause: Not investing in consistent technology or an increasing gap between new and old technology. | Major | Unlikely | 9 | Medium-Low | Possible | Low | Controllable | 1-2 Months | < Month | 6 | Low | Accept
ENE-001 | Extreme Natural Events | Drought (Aridification) | Condition: An extended drought (prolonged period of drier-than-normal conditions) reduces water availability as a fuel resource. Consequence: Current trends suggest a possible 30% reduction in hydro generation in the Southwest subregion (Colorado Basin) in the next 20 years. Potential drought conditions are expected to worsen, with a possible average of 7.5% reduction across all other regions. Totaling ~7,600 MW potential decrease in 20 years. Cause: Aridification is a slow process that creates long-term visibility for entities for planning purposes. | Moderate | Unlikely | 10 | Medium-Low | Likely | High Moderate | Uncontrollable | > 2 Months | < 5 Years | 17.2 | High | Accept
ENE-002 | Extreme Natural Events | Heat Wave/Dome | Condition: Heat wave/dome events (3+ days of temperature exceeding 10% higher than normal peak, and 10% higher than normal peak nighttime lows, for a subregion) combined with unusual causal events, that include one or more of the following: - Generation or transmission asset operating outside the design parameters. - Maintenance or equipment failure. Consequence: - Transmission assets within the heat wave can experience derates. - Reduced capacity of generation due to heat may create a shortfall. - Implementation of EEAs, up to and including load shedding. Cause: Rising background temperatures amplify persistent heat domes in the upper atmosphere. | Minor | Possible | 7 | Medium-Low | Likely | High | Uncontrollable | > 2 Months | < 5 Years | 18.8 | High | Reduce
ENE-003 | Extreme Natural Events | Wildfire | Condition: Major infrastructure (>230kV) within close proximity and common corridors within one mile of large areas of dense, dry vegetation that have ignited, regardless of cause. (High-heat-level impact conditions, smoke density impact conditions, and facility designs vary by operating entity and should be considered.) (Entities' liability concerns may go beyond the NERC standards and may employ more stringent wildfire management practices.) Consequence: Implementation of EEAs, up to and including load shedding of greater than 5,000 MW. Damage caused by unusual fire & wind conditions (firenado) and operational impact (possibly several days) from fire suppression/retardant methods. Cause: Any ignition source. | Severe | Unlikely | 21 | Extreme | Likely | High Moderate | Uncontrollable | 1-2 Months | < Month | 17.6 | High | Reduce
ENE-004 | Extreme Natural Events | Prolonged Cold Weather | Condition: Prolonged cold weather, combined with unusual causal events, that include one or more of the following: - Generation asset operating outside the design parameters. - Above-average snowfall, precipitation, or moisture accumulation (during low temperatures, but not necessarily extreme or below average). - Reduction of Natural Gas resources. - Maintenance or equipment failure. Consequence: Implementation of EEAs, up to and including load shedding. Cause: Polar Vortex Cold Air Damming Blizzard Lake-effect Snow Freezing Rain Ice Storm Freezing Fog | Negligible | Likely | 4 | Low | Likely | High Moderate | Uncontrollable | > 2 Months | < Month | 18 | High | Reduce
ENE-005 | Extreme Natural Events | Geomagnetic Disturbance | Condition: G5 geomagnetic disturbance (severe geomagnetic storms, the highest level on the NOAA Space Weather Scale) and primarily transmission assets (Transmission Operator with a Transmission Operator Area that includes a power transformer with a high side wye-grounded winding with terminal voltage greater than 200 kV) located above the 45th parallel. (British Columbia, Alberta, NorthWest Regions) Consequence: During a GMD event, geomagnetic-induced currents may cause transformer hot-spot heating or damage, loss of reactive power sources, increased reactive power demand, an​d protection system malfunction, the combination of which may result in voltage collapse and potential blackouts. Extremely strong GMD events, although rare, can induce strong quasi-DC currents in the electric power grid, which could affect system voltages, relay and protection system performance, and the operation and health of transmission assets. Cause: G5 geomagnetic disturbance (highest) occurs about four times during an 11-year solar cycle, particularly during the solar maximum phase when solar activity is at its peak.(The Earth is currently in Solar Cycle 25, and the solar maximum for this cycle occurred in Q4 2024 and is declining to 2030.) (Solar Cycle 26 is expected to have a solar maximum around 2035.) | Negligible | Unlikely | 2 | Low | Likely | Low | Moderate | Days | < Month | 10.4 | Medium | Accept
ENE-008 | Extreme Natural Events | Rising Oceans and Coastal Erosion | Condition: Rising sea level and resulting erosion along the West Coast. Consequence: Generation facilities 1000MW or greater and transmission infrastructures of 500kV along the West Coast may be more susceptible to damage. Cause: Various causes. | Moderate | Very Unlikely | 8 | Medium-Low | Possible | Moderate | Uncontrollable | > 2 Months | > 5 Years | 11.4 | Medium | Accept
ENE-009 | Extreme Natural Events | Extreme Winds | Condition: Extreme winds beyond the infrastructure design criteria. Consequence: Adverse impact to real-time operations and potential longer-term damage to generation (1400MW and greater) and transmission infrastructure (345kV and greater) for greater than 6 months. Cause: Extreme winds are primarily caused by severe thunderstorms. | Major | Very Unlikely | 13 | Medium | Likely | Moderate | Low | Hours | Overnight | 13.6 | Medium | Reduce
ENE-010 | Extreme Natural Events | Earthquake | Condition: Within the next 50 years, at least one of the WI fault zones may rupture: Cascadia (9.0), San Andreas (7.0), Wasatch (6.75), or Las Vegas Valley (6.5). Consequence: A rupture on the Cascadia or San Andreas faults will likely have a significant impact on up to eight 500kV WECC paths at high risk. Six 500kV WECC paths are at moderate risk from Cascadia, San Andreas, or Las Vegas Valley zones. This could lead to grid cascading/uncontrolled separation/islanding. A rupture in the Wasatch or Las Vegas Valley would likely have a more localized impact specific to those areas. Natural Gas pipeline disruption will likely affect NG generators, even those not within an impact zone. Cause: Seismic waves are created when the Earth's surface shakes, resulting from a sudden release of energy in the Earth's lithosphere. | Severe | Very Unlikely | 16 | High | Unlikely | High Moderate | Uncontrollable | > 2 Months | Overnight | 9.2 | Medium | Accept
ENE-011 | Extreme Natural Events | Tsunami | Condition: A tsunami impacting generation and or transmission BPS facilities within an inundation zone (~100 miles up to 600 for a megatsunami) along the West Coast of the Western Interconnection. Consequence: Tsunami inundation on the West Coast along British Columbia, Washington, Oregon, and California impacting 500kV or greater transmission facilities, and 1000MW or greater generation facilities. Cause: Generated by an earthquake, volcanic eruption, or other event in the Pacific Ocean. | Moderate | Very Unlikely | 8 | Medium-Low | Unlikely | Moderate | Uncontrollable | 1-2 Months | Overnight | 8.2 | Medium | Accept
ENE-012 | Extreme Natural Events | Volcanic Eruption | Condition: Volcanic eruption and the resulting ash near generation and transmission infrastructure. Consequence: Generation and transmission infrastructure is rendered both operationally and long-term unavailable for many months and years, depending upon the accessibility, damage, and replacement equipment availability. Cause: A rupture in the Earth's crust allows hot lava, volcanic ash, and gases to escape the magma chamber below the surface. | Severe | Very Unlikely | 16 | High | Very Unlikely | Moderate | Uncontrollable | > 2 Months | < Month | 4.1 | Low | Accept
FRP-001 | Frequency Performance | Time of Use / EV Charging Impacts to Grid | Condition: Various rate-incentivized programs for Time of Use/Day and EV Charging, combined with precise clock synchronization and increasing programmable end-user assets (e.g., EV, home battery storage, IoT, 3rd-party non-affiliated program) at the distribution level (residential, commercial, industrial customers). Consequence: The top-of-the-hour frequency excursions have a significant MW quantity (~800MW) at specific hours of the day (0000; 1600; 1700; 2100HRS). Cause: Historical Time of Use/Day is now combined with an increasing number of programmable consumer-level products that also use centralized time synchronization (e.g., GPS, atomic clock/NTP). | Minor | Almost Certain | 12 | Medium | [5 empty] | 1 | Low
GLL-001 | GT: Grid Large Loads | Large Loads - Dynamic Modeling | Condition: Insufficient modeling of the newer Large Loads may result in existing planning and operations of the WI not identifying regional and/or interconnection reliability inadequacies for newer Large Loads greater than 500 MW at a single BPS POI. Consequence: With these newer Large Load types, a number of reliability areas regarding dynamic modeling, including but not limited to ride-through, frequency/voltage stability (short-mid-long-term) and oscillations, may impact the reliability of the WI BPS.​ Cause: Significant forecasts of newer Large Loads with significantly different operating characteristics than existing large loads (Residential, C&I, EV, traditional data centers, pumps, arc-furnaces, mining, etc.). | Minor | Likely | 12 | Medium | [5 empty] | 1 | Low
GLL-002 | GT: Grid Large Loads | Large Loads - Transmission Adequacy | Condition: Insufficient transmission infrastructure at 345kV AC or above, with a demand of 2000MW or more to interconnect newer large loads. Consequence: Newer large loads may not be able to interconnect to the transmission system in the desired timeframe. Cause: Significant forecasts of newer large loads with either the existing or new transmission infrastructure. | Negligible | Likely | 4 | Low | [5 empty] | 1 | Low
IBR-004 | GT: IBR | Applicability of GO Registration and NERC Reliability Standards | Condition: Non-BES IBRs that affect the BES with an aggregate nameplate capacity of 20 MVA or more connected to a common point at a voltage of 60kV or higher are not required to follow some or all of the NERC Reliability Standards. Consequence: "An ERO analysis identified a reliability gap associated with the increasing integration of IBR owners and operators currently not meeting the criteria thresholds required to register with NERC, and, as such, not required to adhere to NERC Reliability Standards." (NERC Report) Cause: Interconnection of non-BES IBRs in the WI. | Moderate | Very Unlikely | 8 | Medium-Low | Almost Certain | High Moderate | Controllable | 1-2 Weeks | < 5 Years | 12.5 | Medium | Transfer
IBR-006 | GT: IBR | Increasing number of long-term frequency deviations | Condition: Non-BES IBRs that affect the BES with an aggregate nameplate capacity of 20 MVA or more connected to a common point at a voltage of 60kV or higher are not required to follow some or all of the NERC Reliability Standards. Consequence: "An ERO analysis identified a reliability gap associated with the increasing integration of IBR owners and operators currently not meeting the criteria thresholds required to register with NERC, and, as such, not required to adhere to NERC Reliability Standards." (NERC Report) Cause: Interconnection of non-BES IBRs in the WI. | Moderate | Very Unlikely | 8 | Medium-Low | Almost Certain | Low | Moderate | 1-2 Months | < Year | 13.5 | Medium | Reduce
IBR-008 | GT: IBR | Modeling, Performance, Interconnection Requirements, Data Availability, and Validation | Condition: Insufficient modeling and modeling quality based on inadequate interconnection requirements, as well as data availability either through performance testing or disturbance monitoring equipment, combined with simulating actual IBR performance of stand-alone, hybrid, and/or co-located facilities with a capability of 750MW BESS at a single point of interconnection, 700MW PV/400MW BESS at a single point of interconnection, or electrical proximity of IBRs in BA/TOP areas, and or sub-regions. Consequence: - Inability to accurately validate the IBR performance in power flow/stability studies - Historical loss of over 2000MW of IBR generation - During normal clearing faults, with expected protection operations on the BPS, resulting in likely unexpected loss of IBR generation over 2000MW occurring once per year - Increasing loss as additional IBRs (doubling to tripling 2023 IBR levels in 10 years) are interconnected to the grid in concentrated areas or sub-regions. - Forced oscillations from IBRs Cause: Interconnection of transmission level IBRs in the WI BPS without sufficient modeling, modeling requirements, data quality, best-practices, personnel resources (testing, modeling, validating), and monitoring equipment. Study tools and methodologies (EMT, positive sequence assumptions, etc.) | Major | Likely | 20 | High | [5 empty] | 1 | Low
IBR-009 | GT: IBR | Grid Transformation - IBRs and Inertia | ​Condition: Insufficient modeling of the forecasted inertia levels in the Western Interconnection. Consequence: With this transition, existing planning and operations of the WI may not identify regional and/or interconnection reliability inadequacies regarding inertia, and impacts may include WI inertia levels, imbalance of inertia levels, oscillation damping (inter-area focused), OFSPR, and WECC-1 RAS. Cause: Significant current and forecasted transition from conventional synchronous generation to non-synchronous generation driven by individual State mandates (e.g., Renewable Portfolio Standards, Clean Air Acts). ​ | Major | Unlikely | 15 | Medium | [5 empty] | 1 | Low
IBR-010 | GT: IBR | IBR - System Restoration - GFM (BESS, PV, Wind) | Condition: Synchronous generation with System restoration capabilities continues to retire, and non-synchronous generation is added to the system, all/most of which is Grid-Following. System restoration capability requirements are insufficiently defined for Grid-Forming (Advanced Grid Support Functions/Services) resources such as BESS, PV, and Wind, including stand-alone, hybrid, and/or co-located facilities to provide initial blackstart, cranking paths, and System restoration capability.) Consequence: Potential inability to, or delay in, blackstarting all or subregions of the Western Interconnection. Cause: Grid Transformation to IBRs without requirements for Grid-Forming capability. | Negligible | Very Unlikely | 1 | Low | [5 empty] | 1 | Low
INF-001 | Infrastructure | Supply Chain Constraints | Condition: Supply chain constraints for generation and transmission equipment, such as transformers, circuit breakers, and switches for new BPS facilities, including generators, substations, and lines rated at 345kV and above with 1500MVA and above. Consequence: Supply chain constraints may result in delays in interconnecting new BPS projects, which could lead to resource insufficiency for load-serving BPS interconnections, and implementation of EEAs. Cause: Competition in the form of regulations (such as clean air/renewable portfolio standards) and global disruption (e.g., financial, pandemics, war) have delayed the COD of new BPS infrastructure. | Moderate | Very Unlikely | 8 | Medium-Low | Likely | Low | Uncontrollable | > 2 Months | < 5 Years | 14 | Medium | Reduce
INF-004 | Infrastructure | Facility Rating - Ambient Temperature Impacts on Transmission Capacity | Condition: Planning/seasonal transmission equipment ratings don't consider ambient adjusted ratings and/or differ from operations/real-time ambient transmission equipment ratings for BPS facilities (i.e., FERC Order 881) focusing on 345kV and above and 1500MVA and above. Consequence: Operations/real-time ambient ratings decrease the thermal conductor ratings (transmission capacity), reducing transmission transfer capability between regions/sub-regions, or generation curtailments as compared to the planning/seasonal ratings. Potential implementation of EEAs. Cause: FERC Order 881 (for jurisdictional entities) - Managing Transmission Line Ratings - Effective December 15, 2026 requires entities to utilize ambient adjusted ratings (AARs) in real-time operations, and may differ from planning/seasonal transmission facility ratings. These differences are not addressed by the FERC Order or the NERC Reliability Standards, and create a potential reliability gap. |  | Unlikely | 10 | Medium-Low | Almost Certain | Low | Controllable | 1-2 Months | < Month | 10 | Medium | Reduce
OTH-001 | Other | Planning Case Accuracy | Condition: Independent transmission developers' projects of 230kV AC and above, and/or +/-500kV DC and above, are not required by regulation to submit transmission projects to WECC for inclusion in future transmission planning assessments until they are registered with NERC as a Transmission Owner/Operator. Consequence: Transmission planning assessments may not address the impacts these transmission projects have on the interconnected system (path flows, generation dispatch, RAS operation, etc.) within a timeframe to coordinate mitigation. Cause: Independent transmission developer projects don't require a designated TP or PC to provide the information until the facility nears commercial operation or NERC registration as a TO and/or TOP. | Major | Unlikely | 15 | Medium | Almost Certain | Moderate | Moderate | > 2 Months | < 5 Years | 15.5 | High | Reduce
OTH-002 | Other | Congested Radio Spectrum | Condition: The radio spectrum is used for various services that ensure reliable control and protection of the WI BPS equipment. These services are provided by electric utility owners and operators that operate high-capacity microwave radio networks. Radio spectrum is required to operate electric power systems in many instances where other communications (e.g., fiber optic networks) cannot provide the reliability electric utilities need. Consequence: Potential interference levels have been proven substantial in the field. The impact is two-fold: increased interference with existing utility networks decreases reliability for both protection and control, and directly affects regulatory compliance and the operation of the WI BPS. Additionally, the increased congestion prevents growth to meet demand for incorporating wind and solar generation and other grid demands. These impacts are in relatively small geographic areas. Cause: In recent years, regulators of the radio spectrum have proposed and allowed other services to enter the microwave radio bands used by utilities through band sharing, unlicensed radio applications, and repurposing portions of these bands for other services, leading to increased congestion and interference. | Negligible | Possible | 3 | Low | Likely | Negligible | Low | Hours | < 5 Years | 9.2 | Medium | Accept
PER-001 | Personnel | Workforces Skillset Shortage | Condition: A skilled workforce, from entry-level to expert, is required to plan, design, build, operate, and maintain the BPS. Consequence: Inability to attract or retain skilled workforces may impact all aspects of the reliability of the BPS. Cause: Various (e.g., financial, Human Performance, organizational workforce, competition, lack of engineering interest, or education offerings). | Negligible | Unlikely | 2 | Low | Likely | Low | Low | > 2 Months | < 5 Years | 12.4 | Medium | Accept
PER-002 | Personnel | Pandemic | Condition: Another pandemic is predicted in the next 25 years. Consequence: Leading to a peak 20% workforce absenteeism for 6 weeks, with "shoulder" absenteeism ranging from 5% to 20% in the weeks before and for months after the peak, up to one year. Operational Adequacy impact should be negligible. Cause: “In the future, it is predicted that pandemics will emerge more often, spread more rapidly, cause more damage to the global economy, and lead to greater global morbidity and mortality.” —World Health Organization. | Negligible | Very Unlikely | 1 | Low | Possible | High Moderate | Uncontrollable | > 2 Months | < Month | 13.5 | Medium | Accept
PHY-001 | Physical Security | Substation Sabotage | Condition: Substations, primarily unattended, are increasing in physical attacks and damage to facilities. Consequence: Although primarily financial loss, there is potential for increasing attack severity to stop operation of a substation for more than X (consider time or cascading as a potential threshold. i.e. 4+ hours is unacceptable) Cause: Primarily theft, vandalism, and potentially intended harm. | Minor | Possible | 12 | Medium | Possible | Low | Moderate | Hours | Overnight | 7.8 | Medium | Accept
PHY-002 | Physical Security | Drones and Unmanned Aircraft | Condition: The use of drones has increased exponentially in North America. Consequence: Easily bypass traditional security perimeters for 1. Surveillance and negative publicity 2. Injury to personnel 3. Attacks on infrastructure, or 4. Cybersecurity vulnerabilities. Cause: Curiosity and potential intended harm. | Minor | Likely | 13 | Medium | Likely | Low | Low | Hours | Overnight | 12 | Medium | Accept
RES-005 | GT: Resource Adequacy | Resource and Load Balance | Condition: Various contributors (Energy Policy, Rates/Programs, Resource Transition, Newer Large Loads, Technology, etc.) may impact the overall system resource and load balance, potentially impacting both the resource adequacy and operational adequacy of the BPS in the WI. Specifically, the overall regional/sub-regional resource and load balance, the dispatchable-to-non-dispatchable resource ratio, and load forecasts may contribute to the imbalance. Specific conditions may include, but are not limited to: 1) 1% deficit on WI Load or 1% DARH of total WI; 2) >65% of WI Non-dispatchable generation Consequence: Implementation of EEAs, up to and including load shedding. Cause: Energy Policy, Rates/Programs, Resource Transition, Newer Large Loads, Technology, and other changes in accordance with federal, state, and municipal laws and policies. | Moderate | Likely | 18 | High | [5 empty] | 1 | Low
Exported: 03/16/2026