WECC Modeling and Validation Work Group

Load Model Data Tool

Version 3A – May 2011, Updated March 2012

This document is to help provide step by step instructions on how to use the epcl programs to create “cmpldw” model records with default data, and the opportunity to customize parameters based on your specific system.  Be sure you are using the latest version of PSLF.

Files included:

See the LID Instructions document for the description of the load Long IDs (LIDs).

“RemoveSpacesFromBusNames.p”

Purpose: Replace blank spaces with underscore in bus names.

Steps:

- Load a base case with “getf” command

- Run epcl “RemoveSpacesFromBusNames.p”

- Save the base case with “savf” command

Example:

“LONG LK” will be changed to “LONG_LK”

The load data, including load bus names, will be extracted from the base case to a coma separated file during the following steps of creating load model records. Although quotation marks are used with the bus name during the data export, the coma-separated file may be edited using Excel, which will strip the quotation marks when a coma-separated file is saved. When an epcl reads data from a file, both comas and blank spaces are interpreted as delimiters. Therefore a bus name with a blank space in the middle will be read as two entrees, causing a data error.

42035, “LONG LK”, 115.0 will be read as three variables

42035, LONG_LK, 115 will be read as three variables

42035, LONG LK, 115 will be read as four variables, with LK interpreted as base voltage

“LMDTWECC-0 - Check Long IDs v3a.p”

Purpose: Check for invalid and missing LIDs in a given case.

Prerequisite – a case has the LID data.

In pslf, run epcl “LMDTWECC-0 - Check Long IDs v3a.p”

Select the case you want to check (e.g. 12hs4a.sav) as the Powerflow Base Case with Climate Data (*.sav)

The output file in this example is defaulted to “Check_Long_IDs.csv”.

Click OK.

This will create a log of loads with invalid or blank LIDs, in csv format.

“LMDTWECC-0 - Copy Climate Zone Data v3a.p”

Purpose: Copy LID information from one case and to another.

Prerequisite – a case has the LID data.

In pslf, run epcl “LMDTWECC-0 - Copy Climate Zone Data v3a.p”

Select the case that has LID information as the original powerflow file with Climate Data (*.sav)

Select the case that does not have LID information as the New Powerflow File (*.sav)

Click OK.

This will create a log of loads not found and not copied over to new powerflow file.

The case in the active window will now have LID column populated.

The epcl does not automatically save the new case. Use “savf” command if you want to save the new case with LIDs.

“LMDTWECC-1 - Extract Load Records v3a.p”

Purpose: Create a file with the load model data to be used to create the “cmpldw.dyd”:

Prerequisite:

- a base case with LIDs populated

- coma-separated file with default data

Result:

- file with load model data – distribution equivalent and load composition

Default settings are saved in INI configuration file:

LMDTWECC-1 Extract_Load_Records_3a.ini

"12hs4a.sav"                     			% BaseCase

"LMTF Data Defaults-00.csv"			% File with Default Load Model Data

"Load Model Database-00.dat"     			% OUTPUT: Load Model Data File

5.0							% MW Threshold

40.0							% Minumum KV to add transformer

0.95							% Minumum PU voltage to add a load

0.87							% Minumum Power Factor to add a load

In pslf, run epcl “LMDTWECC-1 - Extract Load Records v3a.p”

Powerflow base case has to include climate zone identifiers in LID column.

“LMTF Data Defaults-00.csv” includes

- Column A – climate zone identifier

- Columns B to O – distribution transformer model data

- Column P – substation shunt capacitor

- Columns Q to X – feeder model data

- Columns Y to AD – motor model identifiers

- Columns AE to AS – load composition data

- Column AT – reporting level

Select “Y” ins “Save New Set-Up in INI File”, if you want to save the current set-up and over-write file “LMDTWECC-1 Extract_Load_Records_3a.ini”

Click OK.

Output file is “Load Model Database-00.dat”, which contains the data that will be used to create the composite load records. The data includes distribution equivalent (transformer and feeder) and load composition data. The data is taken from the default data file “LMTF Data Defaults-00.csv” by matching load LID with a corresponding climate zone identifiers. All loads with the same LID will have the same model data. File “Load Model Database-00.dat” is a coma-separated file and can be viewed and edited in Excel.

“LMDTWECC-2 - Add Bus Specific Load Composition v3a.p”

Purpose: Use load-specific distribution and load composition information.

“LMDTWECC-1 Extract_Load_Records_3a.p” populates models with area defaults based on LIDs. If specific information is available, such as distribution transformer MVA or load composition, this information can replace the defaults.

Prerequisite:

- Load model data file, e.g. “Load Model Database-00.dat”

- coma-separated file with load-specific data, e.g. “BusSpecificLoadComposition.dat”

Result:

- Updated load model data file, e.g. “Load Model Database-01.dat”

In PSLF, run epcl “LMDTWECC-2 - Add Bus Specific Load Composition v3a.p”

Click OK.

“BusSpecificLoadComposition.dat” file includes:

- Columns A to K – load bus, name, identifiers, MW, etc

- Columns L to R – distribution equivalent data (-1 means no change)

- Column S – flag whether to over-write the load composition data (1 = yes)

- Columns T to AN – specific load composition data

- Column AO – reporting level

Use file “BusSpecificLoadComposition.dat” as a template.

“LMDTWECC-3 - Create CMPLDW DYD Record v3b.p”

Purpose:

- Create a dyd file with the composite load model (cmpldw) data records

Prerequisites:

- Load model data file (with distribution and load composition data), e.g.  “Load Model Database-00.dat”

- File with motor dynamic data, e.g. “LoadDataA.csv”

Result:

- Dyd file with cmpldw records

Default settings are saved in INI configuration file:

LMDTWECC-3 Create_DYD_Records_3a.ini

"Load Model Database-00.dat"             % LMT Data Input File

"LoadDataA.csv"                          % dynamic model data

"cmpldw1a.dyd"                           % CMPLDW DYD output file

In pslf, run epcl “LMDTWECC-3 - Create CMPLDW DYD Record v3a.p”

Click OK.

This epcl uses the information created in “Load Model Database-00.dat” and motor data in “LoadDataA.csv” to create the dynamics file with composite load models for each of the loads in “cmpldw1a.dyd”.

“LoadDataA.csv”

Includes parameters for the 3-phase motors, air conditioner types, and electronic load.

Motor models:

- MA –  3-phase motor model representative of commercial compressors (5 to 20 hp)

- MB –  motor model representative of small fans (less than 50 hp)

- MC – motor model representative of pumps (less than 50 hp)

- IA – industrial compressors

- IB – large industrial fans

- IC – large industrial pumps

Air conditioner models:

- A# – air-conditioners, air-conditioner stall voltage “Vstall“ is increased with ambient temperature

Electronic load:

- PE – power electronic load data