Western Electricity Coordinating Council

Load Composition Model – “Light” version

Version 1C – October 2011

DRAFT

This document is to develop to provide background and technical reference for the Load Composition Model developed by WECC Load Modeling Task Force. The purpose of the Load Composition model is to provide the initial estimates of load model fractions for the composite load model.

- WECC Composite Load Model

WECC Load Modeling Task Force (LMTF) has led the development and implementation of the composite load model. Currently, the load model is implemented in GE PSLF, Siemens PTI PSS®E, PowerWorld grid simulators. Conceptually similar model is implemented in PowerTech’s TSAT.  The model was shown to be capable of capturing the phenomenon of fault-induced delayed voltage recovery [1] and allowing a very good match of inter-area power oscillations in the West.

Figure 1 shows the composite model structure. We would like to highlight the two salient features of the model:

- The model represents electrical distance from the transmission bus to the end-use bus by including a substation transformer and some type of a feeder equivalent

- The model represents the diversity in characteristics of electrical end-uses by having four motors, power electronic loads, and a static component

The load components are:

- Motor A – three-phase motor with constant torque load, representative of compressor motors found in commercial air-conditioners and refrigerators

- Motor B – high inertia motor with speed-dependent load, representative of motors driving fans

- Motor C – low inertia motor with speed-dependent load, representative of motors driving pumps

- Motor D – residential air-conditioners and heat pumps

- Power electronic loads, representative of variable frequency drives and computing

- Static load representative of lights, resistive space and water heating

Figure 1: composite load model

It is essential to have reasonable estimates of the load model fractions for power system stability studies. Load model fractions are also recognized as one of the most challenging pieces of the data, as load composition is greatly affected by many factors such as climate, feeder type, season, time of day, ambient conditions, etc.

Power system planning studies are done for a variety of system conditions, most common are – summer peak, super-peak and off-peak, shoulder peak and off-peak, winter peak and off-peak. Specific conditions may be of interest for model validation studies. We expect Load Composition Model to provide the load composition estimates for the variety of loading conditions.

- Information Sources

The following information and data sources are used to derive load model fractions:

- 2006 California Commercial End-Use Survey – a detailed survey of commercial loads in California, provide load composition and shapes for various types of commercial buildings (office, grocery, retail, education, etc) for fifteen climate zones,  including normal, hot, cold and weekend days.

- 1983-1990 End-Use Load and Consumer Assessment Program (EPCAP) provides an overview of residential consumption patterns in residential homes in the Pacific Northwest

- 2002 Florida Solar Energy Center, Research highlights from a large scale residential monitoring study in a hot climate (FSEC-PF-369-02) provides load shapes and load composition for residential homes in Florida

- 2002 Lawrence Berkeley National Laboratory report “Electricity Use in California: Past Trends and Present Usage Patterns” (LBL-47922) provide load shapes and composition for California for on-peak summer day

- BPA data collected residential load shape and HVAC data in Ashland, OR

- 5-minute and hourly SCADA data was provided to verify the calculated load shapes

- Residential and commercial load shapes published by Southern California Edison

- Detailed Load Composition Analysis

David Chassin, PNNL, developed a detailed Load Composition Model.

The detailed LCM inputs are climate conditions, as shown in Figure 2. A user can download TMY data for 24 cities in the Western US. A user can also enter specific data to study sensitivities or specific conditions of interest.

Figure 2: Load Composition Model climate input sheet

The detailed Load Composition Model has detailed models for various building types:

- Residential

  - Single family

  - Multi family appartments and condominuims

- Commercial

  - Large office

  - Small office

  - Retail

  - Lodging, Hotels

  - Grocery

  - Restaurant

  - Education

  - Health care

To calculate load composition, a user needs to provide the number of each type of building, as shown in line 34 Figure 3. The LCM, then, uses the building models to calculate the hourly energy demand for each end-use in a building. Next, the LCM maps end uses to the composite load model components, and presents the data in the table, lines 12-24 in Figure 3. Finally, the numbers are added up and the fractions are calculated.

Figure 3: Load Composition Model calculation sheet

The detailed LCM can also make load shape and load composition plots. It has been a great tool to use for understanding load composition factors.

While the LCM calculation engine is very detailed, we found limitations with respect to the input data. 1980’s and 1990’s ELCAP data was used for residential buildings, and it certainly looked out of date with a simple examination. Commercial building data was “extrapolated” from 2006 California CEUS to other regions in the West. Certainly, the input data needs to be updated, and the calculated load shapes need to be validated versus the actual load shapes for known feeder. Assumption on gas versus electric cooking, space and water heatings are also generically applied to a region. In reality these numbers can greatly vary within a city depending on the construction year and the availability of natural gas / propane.

WECC LMTF recommends using the detailed LCM when specific studies are required, e.g. fault-induced delayed voltage recovery. A utility needs to provide information on uilding types and historic feeder load data to coduct substation-specific load composition analysis and to develop substation-specific load composition data. Because of many variables involved in the analysis, it is very helpful to work directly with Dave Chassin and his team.

WECC LMTF aslo recognizes that many utilities would like to use default data sets. The detailed LCM was very useful in developing the understanding of the factors affecting load composition. Once the principles are understood, WECC LMTF developed a “light” version of the Load Composition Model for creating default load component fraction for the composite load model.

- Climate Zones

We divided WECC into twelve climate zones:

| ID | Climate Zone | Representative City |
| --- | --- | --- |
| NWC | Northwest Coast | Seattle, Vancouver BC |
| NWV | Northwest Valley | Portland OR |
| NWI | Northwest Inland | Boise, Tri-Cities, Spokane |
| RMN | Rocky Mountain North | Calgary, Montana, Wyoming |
| NCC | Northern California Coast | Bay Area |
| NCV | Northern California Valley | Sacramento, Fresno |
| NCI | Northern California Inland |  |
| SCC | Southern California Coast | LA, San Diego |
| SCV | Southern California Valley | LA, San Diego |
| SCI | Southern California Inland | LA, San Diego |
| DSW | Desert Southwest | Phoenix, Riverside, Las Vegas |
| HID | High Desert | Salt Lake City, Albuquerque, Denver, Reno |

- Substation/feeder Types

For each climate zone, we considered four types of substations/feeders:

- Residential – representative of suburban residential substations

- Commercial – representative of substations in metro areas

- Mixed – mix of commercial and residential loads

- Rural – rural / agricultural loads

In addition to conventional load classes (Residential, Commercial, Industrial, and Agricultural), we added:

- “Data” to capture the increasing load in data centers, and

- “Utility” to represent city services such as street lighting, and power consumption by utilities

| ID | Substation Type | Res | Com | Ind | Agr | Data | Utility |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RES | Residential | 0.7 | 0.2 | 0.05 | 0 | 0 | 0.05 |
| COM | Commercial | 0.2 | 0.65 | 0 | 0 | 0.1 | 0.05 |
| MIX | Mix | 0.45 | 0.4 | 0.05 | 0 | 0.05 | 0.05 |
| RAG | Rural | 0.3 | 0.2 | 0.1 | 0.4 | 0 | 0 |

Percentages of load classes (Res, Com, … ) will vary as a fraction of the total feeder load. The commercial loads peak earlier in the day, about 14:00-15:00, while the residential loads peak later, about 18:00-19:00. As a result, their ratios change during the day. Figure 4 is calculated by the detailed LCM to illustrate the point.

Figure 4: Variation of load class fractions during a summer day as calculated by the detailed Load Composition Model

Therefore, we reference the load class fractions to a specific hour – the total system peak at 16:00.

That said, the load class fractions vary not only daily, but seasonally. Residential loads are more sensitive to temperature variations than commercial loads, and therefore the ratio will shift to residential loads during temperature extremes. Table below summarizes studies done for Sacramento with the detailed Load Composition Model.  Ratios of residential versus commercial load were calculated for a different seasons and different temperatures, while the number of building types remained the same in all cases.

| Month | July | July | July | April | October | January | January |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature at 16:00 | 89 | 105 | 85 | 75 | 83 | 59 | 45 |
| Residential % | 59 | 60 | 56 | 55 | 55 | 58 | 60 |
| Commercial % | 41 | 40 | 44 | 45 | 45 | 42 | 40 |

We observed that the seasonal changes in load class fractions at 16:00 usually do not exceed 5%, which is well within the accuracy of the available data and models. Rather than focusing on getting “precise” estimates, our goal is to get “reasonable” estimates of load composition and do sensitivity studies around them.

In the powerflow program, we use “LongID” field to specify the climate zone and feeder type. For example, a residential feeder in Seattle is designated as “NWC_RES”, and a commercial feeder downtown Phoenix as “DSW_COM”

Large industrial loads are usually fed dedicated substations, and identified explicitly. Large industrial loads include paper mills, steel mills, petro-chemical plants, aluminum smelters, semiconductor plants, and computer server farms.

- Commercial Load Composition

2006 California Commercial End-Use Survey was used to estimate commercial load composition in the West.

Figure below shows climate zones used in CEUS.

Figure: climate zones in California CEUS

The load shape and load composition data is available from Itron’s web-site. The following load composition data sets are provided for each climate zone:

- Seasons – summer, winter, spring and fall

- Day – typical (for that season), hot, cool, and typical weekend

- Type of commercial load – total, office, grocery, retail, warehouse, etc

Figure below shows a profile of the commercial load in Riverside area for a typical summer day.

Figure: example of load shape and composition profiles

California data was “extrapolated” to other regions within WECC, using mapping described below.

Column 1 = WECC Climate Zones, decribed in section IV

Column 2 = corresponding CEUS climate zone, see CEUS report

Column 3 = CEUS season: 1=winter, 2=spring, 3=summer, 4=fall

Column 4 = CEUS day type: 1=typical, 2=hot, 3=cool,4=weekend

Column 5 = WECC day type: 1= summer normal peak, 2=summer hot peak (heat wave), 3=summer cool day, 4=shoulder normal day, 5=winter normal day

Column 6 = scale factor for cooling load

Column 7 = scale factor for heating load

| # WECC Climate | CEUS Climate | CEUS Season | CEUS Day | WECC Day | Scale Cool | Scale Heat |
| --- | --- | --- | --- | --- | --- | --- |
| # Normal Summer |  |  |  |  |  |  |
| NWC_COM | FCZ05 | 3 | 3 | 1 | 1 | 1 |
| NWV_COM | FCZ04 | 3 | 3 | 1 | 1 | 1 |
| NWI_COM | FCZ03 | 3 | 3 | 1 | 1 | 1 |
| RMN_COM | FCZ04 | 3 | 3 | 1 | 0.7 | 1 |
| NCC_COM | FCZ05 | 3 | 1 | 1 | 1 | 1 |
| NCV_COM | FCZ03 | 3 | 1 | 1 | 1 | 1 |
| NCI_COM | FCZ04 | 3 | 1 | 1 | 1 | 1 |
| SCC_COM | FCZ08 | 3 | 1 | 1 | 0.5 | 1 |
| SCV_COM | FCZ08 | 3 | 1 | 1 | 1 | 1 |
| SCI_COM | FCZ08 | 3 | 1 | 1 | 0.7 | 1 |
| DSW_COM | FCZ10 | 3 | 1 | 1 | 1 | 1 |
| HID_COM | FCZ10 | 3 | 3 | 1 | 1 | 1 |
| # Hot Summer |  |  |  |  |  |  |
| NWC_COM | FCZ05 | 3 | 1 | 2 | 1 | 1 |
| NWV_COM | FCZ04 | 3 | 1 | 2 | 1 | 1 |
| NWI_COM | FCZ03 | 3 | 1 | 2 | 1 | 1 |
| RMN_COM | FCZ04 | 3 | 1 | 2 | 0.7 | 1 |
| NCC_COM | FCZ05 | 3 | 2 | 2 | 1 | 1 |
| NCV_COM | FCZ03 | 3 | 2 | 2 | 1 | 1 |
| NCI_COM | FCZ04 | 3 | 2 | 2 | 1 | 1 |
| SCC_COM | FCZ08 | 3 | 2 | 2 | 0.5 | 1 |
| SCV_COM | FCZ08 | 3 | 2 | 2 | 1 | 1 |
| SCI_COM | FCZ08 | 3 | 2 | 2 | 0.7 | 1 |
| DSW_COM | FCZ10 | 3 | 2 | 2 | 1 | 1 |
| HID_COM | FCZ10 | 3 | 1 | 2 | 0.8 | 1 |
| # Cool Summer |  |  |  |  |  |  |
| NWC_COM | FCZ05 | 3 | 3 | 3 | 0.2 | 1 |
| NWV_COM | FCZ04 | 3 | 3 | 3 | 0.3 | 1 |
| NWI_COM | FCZ03 | 3 | 3 | 3 | 0.3 | 1 |
| RMN_COM | FCZ04 | 3 | 3 | 3 | 0.1 | 1 |
| NCC_COM | FCZ05 | 3 | 3 | 3 | 1 | 1 |
| NCV_COM | FCZ03 | 3 | 3 | 3 | 1 | 1 |
| NCI_COM | FCZ04 | 3 | 3 | 3 | 1 | 1 |
| SCC_COM | FCZ08 | 3 | 3 | 3 | 0.5 | 1 |
| SCV_COM | FCZ08 | 3 | 3 | 3 | 1 | 1 |
| SCI_COM | FCZ08 | 3 | 3 | 3 | 0.7 | 1 |
| DSW_COM | FCZ10 | 3 | 3 | 3 | 1 | 1 |
| HID_COM | FCZ10 | 3 | 3 | 3 | 0.5 | 1 |
| # Normal Soulder |  |  |  |  |  |  |
| NWC_COM | FCZ05 | 1 | 3 | 4 | 0.2 | 2 |
| NWV_COM | FCZ04 | 1 | 3 | 4 | 0.3 | 2 |
| NWI_COM | FCZ03 | 1 | 3 | 4 | 0.3 | 2 |
| RMN_COM | FCZ04 | 1 | 3 | 4 | 0.1 | 5 |
| NCC_COM | FCZ05 | 1 | 1 | 4 | 1 | 1 |
| NCV_COM | FCZ03 | 1 | 1 | 4 | 1 | 1 |
| NCI_COM | FCZ04 | 1 | 1 | 4 | 1 | 1 |
| SCC_COM | FCZ08 | 1 | 1 | 4 | 0.5 | 1 |
| SCV_COM | FCZ08 | 1 | 1 | 4 | 1 | 1 |
| SCI_COM | FCZ08 | 1 | 1 | 4 | 0.7 | 1 |
| DSW_COM | FCZ10 | 1 | 1 | 4 | 1 | 1 |
| HID_COM | FCZ10 | 1 | 3 | 4 | 0.5 | 1 |
| # Normal Winter |  |  |  |  |  |  |
| NWC_COM | FCZ05 | 2 | 3 | 5 | 0.5 | 2 |
| NWV_COM | FCZ04 | 2 | 3 | 5 | 0.5 | 2 |
| NWI_COM | FCZ03 | 2 | 3 | 5 | 0.5 | 2 |
| RMN_COM | FCZ04 | 2 | 3 | 5 | 0.2 | 5 |
| NCC_COM | FCZ05 | 2 | 1 | 5 | 1 | 1 |
| NCV_COM | FCZ03 | 2 | 1 | 5 | 1 | 1 |
| NCI_COM | FCZ04 | 2 | 1 | 5 | 1 | 1 |
| SCC_COM | FCZ08 | 2 | 1 | 5 | 0.5 | 1 |
| SCV_COM | FCZ08 | 2 | 1 | 5 | 1 | 1 |
| SCI_COM | FCZ08 | 2 | 1 | 5 | 0.7 | 1 |
| DSW_COM | FCZ10 | 2 | 1 | 5 | 1 | 1 |
| HID_COM | FCZ10 | 2 | 3 | 5 | 0.5 | 1 |
| # |  |  |  |  |  |  |

Let’s look at the first line:

| NWC_COM | FCZ05 | 3 | 3 | 1 | 1 | 1 |
| --- | --- | --- | --- | --- | --- | --- |

Northwest coast load, Seattle WA or Vancouver BC, (“NWC” in Column 1) on a typical summer day (“1” in Column 5)  will have similar load composition to loads in Bay Area (“FCZ05” in Column 2) on a cool (“3” in Column 4) summer (“3” in Column 3) day. Cooling and heating loads are mapped 1 to 1.

Conversion files can be found in directory “Commercial Load Composition”:

GE PSLF EPCL file:

“Map CEUS Data to WECC Climate Zones rev2.p”

Input data file with mapping: “Map CEUS Data to WECC Climate Zones - rev2.dat”

CEUS data files with California load composition data:

“FCZ01.csv”, “FCZ02.csv”, …

Output file with load profiles and composition data for WECC regions:

“Map CEUS Data to WECC Climate Zones - rev2.csv”

Although the absolute kW data is in the output file is not correct, the load shape and load composition should be representative of a WECC climate region.

- Residential Load Composition

We used a model to construct the residential load composition. The model included the following components:

- Space heating

- Space cooling

- Ventilation

- Electric water heating

- Electric cooking

- Refrigeration

- Lighting (internal and outside)

- Electronics

- Appliances

We found that ELCAP water heating data is more than double of the water-heating demand measured in 2002 Florida study. Therefore, we multiplied ELCAP data for water heating by 0.5.

We also found that ELCAP cooking data is higher than cooking measured in 2002 Florida study. Therefore, we multiplied the ELCAP data for cooking by 0.7.

Refrigeration profile was assumed to be constant at 175 W in summer and 150 W in winter.

We believe that lighting data in ELCAP is also on high side, and multiplied ELCAP data by 0.5.

Appliance data was taken directly from ELCAP.

Electronic load profile was added.

Cooling loads are calculated using the following formula:

kW = ACmax * Use *

Max (0,  Min(1, (0.6 * (Tb– Tk)/Tc + 0.3 * (Tb – Tk-1)/Tc + 0.1 * (Tb – Tk-2)/Tc) ) ) *

(1 + 0.2*(Tk-80)/30)

Where

ACmax  is air-conditioner size (from 2 kW in northern parts to 4kW in the south)

Use is the percentage of households that have and use air-conditioner for a given day

Tb = “balance” temperature

Tk = ambient temperature at this hour

Tk-1 = ambient temperature at the previous hour

Tc = maximum delta temperature at which an air-conditioner runs continuously

The second line calculates the air-conditioner duty-cycle.

The third line calculates the increase in load factor with ambient temperature.

Heating load is calculated similarly.

Ventilation is assumed to be 15% of the air-conditioning load during cooling periods.

We used Ashland data for sanity check of our model and made assumptions. Load profiles were generated for the total load and for a non-HVAC load.

- WECC Load Model Composition Data

We used the following process for creating load composition data.

For residential / commercial loads:

- The load shapes are loaded for 12 climate zones, 24 hours and 5 seasonal conditions (e.g. sheet: “RES_Inp” and “CEUS”)

- The load shapes are normalized so that the 1 per unit load occurs at 16:00 (sheets “RES_Data” and “COM_Data”)

- Rules of association map the end-uses to the load model components (sheets “RES_RofA” and “COM_RofA”)

- Rules of association are applied to the load normalized shapes (sheets “RES_MOD” and “COM_MOD”)

Small Industrial, agricultural, data and service load shapes are entered explicitly in terms of load model components, and remain the same for all seasons and all climate zones.

A user can plot load shapes and load composition in “PLOT” tab. A user needs to enter the data highlighted by the yellow background:

- the climate zone, as described above in section IV

- load class fractions: residential, commercial, small industrial, agricultural, data and services

- day: 1=normal summer, 2=hot summer, 3=cool summer, 4=shoulder, 5=winter

The program will plot the load shape and load composition. Please note that the load shape plot is normalized to 25MW load at 16:00.

A user can generate load composition data in the “MODEL” tab. A user needs to enter the data highlighted by the yellow background:

- day: 1=normal summer, 2=hot summer, 3=cool summer, 4=shoulder, 5=winter

- Pacific Time (please note that time in Mountain zones is adjusted automatically)

The tab also requires a user to specify load class fractions for residential / commercial / mixed and rural substations. The following fractions are currently used.

| Load Mix | Res | Com | Ind | Agr | Data | Service |
| --- | --- | --- | --- | --- | --- | --- |
| RES | 0.75 | 0.23 | 0 | 0 | 0 | 0.02 |
| COM | 0.2 | 0.73 | 0 | 0 | 0.05 | 0.02 |
| MIX | 0.45 | 0.48 | 0 | 0 | 0.05 | 0.02 |
| RAG | 0.4 | 0.2 | 0.15 | 0.25 | 0 | 0 |

The PSLF output data is generated in the “PSLF” tab. The data includes:

- Long IDs for climate zones and substation types – Column A

- Substation transformer data, including reactances, load factors, taps – Columns B through O

- Data to calculate the distribution feeder equivalent – Columns P through X

- IDs for the motors in dynamic model data file “MotorDataA.dyd” – Columns Y through AD (see section IX for details)

- Load composition data copied from “MODEL” tab – columns AE through AS. Load composition is copied only for residential/commercial/mixed/rural substations, the data for industrial/agricultural/power plant auxiliaries remains unchanged

- Reporting level – column AT

This sheet can be copied into a separate file for further use by the Load Model Data Tool in creating the composite load model data records.

- Motor Characteristics

The following convention is used in LCM:

- Motor MA – 3-phase compressor motor with low (0.1 sec) inertia and constant torque load, representative of commercial air-conditioning and refrigeration

- Motor MB – small to medium size motor with high (0.5 sec) inertia and speed-dependent torque, representative of fans

- Motor MC – small to medium size  motor with low inertia (0.1 sec) and speed-dependent torque, representative of pumps

- Motor A# - single-phase air-conditioner and refrigerator represented with “performance” model, # corresponds to stall voltage threshold

- Motor IA – 3-phase industrial compressor

- Motor IB – 3-phase large motor with high inertia (1.0 sec) and speed-dependent torque, e.g. driving fans

- Motor IC – 3-phase large motor with low inertia (0.2 sec) and speed-dependent torque, e.g. driving pumps

- Power Electronic load PE – commercial and consumer power electronics, such as computers, data servers, etc

- Power Electronic load PI – industrial variable frequency drives

- Contacts

WECC Load Composition Model and data:

- Dmitry Kosterev, BPA, dnkosterev@bpa.gov

- Stephanie Lu, PSE, stephanie.lu@pse.com

- Donald Davies, WECC, Donald@wecc.biz

Detailed Load Composition Model and specific substation / feeder analysis:

- Dave Chassin, PNNL, David.Chassin@pnl.gov