WECC Modeling and Validation Work Group

Load Model Data Tool

Version 4A – October 2012

This document provides step by step instructions on how to use GE PSLF EPCL programs to create CMPLDW load model records.  GE PSLF version 18.1 is required.

Files included:

“WECC Load Composition Model – ver4A.xlsx”

Purpose: Create load composition data for each climate zone and feeder type based on season and hour of the day.

A PSLF base case needs to have Long IDs (LIDs) populated. See the LID Instructions document for the description of the load Long IDs (LIDs).  LIDs represent the climate zone and substation/feeder type of the load.

Open the file “WECC Load Composition Model – ver4A.xlsx”

Select “MODEL” tab,

Enter a type of study season in cell “I2”, where

1=normal summer

2=hot summer

3=cool summer

4=shoulder season

5=winter

Enter Hour (in Pacific Time) of the day in cell “J2”. The program adjusts time for climate zones located in Mountain Time Zone.

This updates the load model data to correspond with the desired study scenario.  In this example, a heavy summer day at 4 pm has been modeled.  The data in the PSLF tab is also updated when these changes are made.  The PSLF tab data is in the PSLF dyd format.

Select “PSLF” tab.

Load composition data is copied to “PSLF” tab.

The columns are:

- Column A – climate zone and substation type identifier (LID)

- Columns B to O – distribution transformer model data

- Column P – substation shunt capacitor

- Columns Q to X – feeder model data

- Columns Y to AD – motor model identifiers

- Columns AE to AS – load composition data

- Column AT – reporting level

- Column AU – voltage at which residential air-conditioners stall

A user need to adjust the AC stall voltage in Column AU based on the study conditions. The default data is for normal summer condition during on-peak hours. For shoulder season and off-peak hours, set “Vstall” to 0.5 per unit.

Copy the PSLF tab into a new file and save as a .csv file.

To do this, right click on the PSLF tab, select Move or Copy …, change in the To book: field to “(new book)” and check the box to “Create a copy”, and click OK.  Then go to File, Save As…, and save the file as a csv with a file name such as “LMTF Data Defaults-HS16.csv”, where the HS16 describes the season and hour.

If a Transmission Planner (TP) wants to use load composition data different from default data, TPs can add new records to the list of records in the load composition file (“LMTF Data Defaults-HS16.csv”). Make sure that LID in the file agrees with LIDs in the powerflow base case.

“LMDTWECC-4-0 - Check Long IDs.p”

Purpose: Check for invalid and missing LIDs in a given case.

Prerequisite – a powerflow base case with LID data populated.

Run EPCL “LMDTWECC-4-0 - Check Long IDs.p”

Select the case to check (e.g. “12hs4a_Rev3.sav”) as the Powerflow Base Case with Climate Data.

Select a file with load composition defaults (“LMTF Data Defaults HS-16.csv”)

Set thresholds for adding load models, such as minimum MW level (5MW default), voltage and load power factor.

The output file in this example is defaulted to “LMDT_Check_Long_IDs.csv”.

Click OK.

This will create a log of loads with invalid or blank LIDs, in csv format, based on the thresholds provided.

When viewing the “LMDT_Check_Long_IDs.csv” file:

If the “Climate_Feeder” column is blank, there is a missing LID.

If the “Climate_Feeder” column is populated, the LID is not valid.

“LMDTWECC-4-0 - Copy Climate Zone Data.p”

Purpose: Copy LID information from one case to another.

Prerequisite – a case with LID data populated.

Run EPCL “LMDTWECC-4-0 - Copy Climate Zone Data.p”

Select the case that has LID information as the Original Powerflow File with Climate Data (e.g. “12hs4a_Rev3.sav”).

Select the case that does not have LID information as the New Powerflow File (e.g. “12ls1a.sav”).

Click OK.

The case in the active window will now have the LID column populated.  This can be verified by viewing the load table, which is accessed through the “edit” function, “load” selection.

The epcl does not automatically save the new case. Use “savf” command to save the new case with LIDs.

Loads for which LIDs are not found are listed in “LMDTWECC-4-0 Loads_Not_Found.log”

“LMDTWECC-4-1 - Create Default DYD Records.p”

Purpose:

- Create a file with default / template  load model data records

Prerequisites:

- CSV file with load composition defaults, e.g.  “Load Model Defaults HS-16.csv”

- File with motor dynamic data, e.g. “MotorDataP1a.csv”

Result:

- LDY file with load model records, e.g. “hs16P1a.ldy”

“MotorDataP1a.csv” file includes motor parameters and protection data. Motor models include:

- MA –  3-phase motor model representative of commercial compressors (5 to 20 hp)

- MB –  motor model representative of small fans (less than 50 hp)

- MC – motor model representative of pumps (less than 50 hp)

- IA – industrial compressors

- IB – large industrial fans

- IC – large industrial pumps

Air conditioner models:

- AC – air-conditioners, air-conditioner stall voltage “Vstall“ is increased with ambient temperature

Electronic load:

- PE – power electronic load data (mostly commercial and residential)

- PI – dive and electronic load in industrial facilities

In PSLF, run EPCL “LMDTWECC-4-1 - Create Default DYD Records.p”

Click OK.

The EPCL merges load composition data in “Load Model Defaults HS-16.csv” with dynamic model data in “MotorDataP1a.csv” to create a file with composite load model definition for each Long ID.

Template file “hs16P1a.ldy” has the same data structure as a CMPLDW data records, only climate zone is used in a header instead of a bus number identifier.

“LMDTWECC-4-2 - Create CMPLDW Records.p”

Purpose: Create a file with the load model data to be used to generate the composite load model records.

Prerequisite:

- a WECC powerflow base case with LIDs populated (e.g. “12hs4a_Rev3.sav”)

- a template with load model data (e.g. “hs16P1a.ldy” – 88 KB)

Result:

- PSFL files with CMPLDW load composition data (“hs16P1a.ldy” – 8 MB)

Default settings are saved in the configuration file

“LMDTWECC-4-2 - Create CMPLDW Records.txt”

"12hs4a_Rev3.sav"	% BaseCase

"hs16P1a.ldy"		% File with Default Load Model Data

"hs16P1a.dyd"		% OUTPUT: Load Model Data File

5				% MW Threshold

40				% Minumum KV to add transformer

0.93				% Minumum PU voltage to add a load

0.82				% Minumum Power Factor to add a load

In PSLF, run EPCL “LMDTWECC-4-2 - Create CMPLDW Records.p”

To save the current set-up and over-write the INI configuration file, change “N” to “Y” in the “Save New Set-Up in INI File” field.

Click OK.

The EPCL creates CMPLDW bus records by matching Long IDs in a powerflow base case with climate zone definitions for the template data

MW, voltage and power factor filters are applied to the loads.

Also, for loads connecting at voltages below 40-kV, the transformer is not modeled by setting the transformer impedance to zero.

Appending the composite load models to the dyd file

WECC dynamic data file may include the “motorw” and “blwscc” records associated with an interim load model.

Step 1: remove “motorw” records associated with the interim load model from DYD file

Step 2: remove “blwscc” records from DYD file

Step 3: you can either:

- Add composite load model data to the end of the modified dynamic data file

- Read the modified dynamic data file and the composite load model file sequentially

To combine the dyd records into one file, append the composite load model records to the end of the master dynamics file.