Bonneville Power Administration

Power Plant Model Validation Application

Version 1B – November 2011

This document is to help provide step by step instructions to conduct power plant model validation studies using disturbance recordings. The set-up includes two epcl programs:

- “PPMVa_SetBaseCase_v1b.p” to create a validation base case with initial conditions matching those prior to a disturbance

- “PPMVa_RunValidation_v1b.p” to play in a disturbance event in PSLF model

Contacts:

- Dmitry Kosterev, BPA, 360-619-6836, dnkosterev@bpa.gov

- Steve Yang, BPA, 360-418-2946, hyang@bpa.gov

“PPMVa_SetBaseCase_v1b.p”

Purpose:

- create a validation base case with initial conditions matching those prior to a disturbance

Pre-requisites:

- a “template” file with power plant powerflow model (e.g. “GAS.sav”)

- a disturbance data file compatible with play-in format (e.g. “pmu-GAS-2010-09-27-1450.csv”)

- a SCADA file with generating unit status and loading, needed for multi-unit plants (e.g. “scada-GAS-2010-09-27-1450.dat”)

Result:

- Powerflow file with initial conditions matching those during the event (e.g. “GAS-2010-09-27-1450.sav”)

Steps:

- Run epcl “PPMVa_SetBaseCase_v1b.p”

- Select a powerflow template file

- Select a disturbance data file (*.csv)

- Select a SCADA data file with generator status and initial MWs and MVARs (not needed for a single unit plant, can enter “none”)

- Enter a powerflow file with initial conditions matching those during the event. The program will attempt to guess the powerflow file name from the disturbance file name

The information flow is shown in Figure below:

Epcl “PPMVa_SetBaseCase_v1b.p” performs a mini-state estimation. First, it sets the unit status and initial MW and MVAR using data in SCADA data file. Then, it makes generator MW and MVAR adjustments to match boundary conditions (kV, MWs, and MVARs) at the point of interconnection.

Example of Disturbance Data File

The file structure is as follows:

Row 1 – the number of data channels (columns)

Row 2 – channel (column) names – time, voltage, frequency, active and reactive power

Row 3 – scale factors, make sure scale factors are consistent with the actual values. In this example:

- bus voltage data is in KV, and the corresponding base / scale factor is 500;

- bus frequency is in Hz, and the corresponding base / scale factor is 60;

- active and reactive power are in MWs and MVARs, and the corresponding scale factors are set to unity

Row 4 – no offset is used in this case

Row 5 – no data filtering is used

Row 6 – min range for plotting

Row 7 – max range for plotting

Row 8 – flags for plotting

The data records are followed:

- Column 1 – time

- Column 2 – bus voltage

- Column 3 – bus frequency

- Column 4 – active power

- Column 5 – reactive power

It is necessary to ensure that the scale factors and the data records are matched for bus voltages and frequency.

For more information on data structure, please refer to PSLF manual “gthev” and “plnow”.

Example of SCADA Data File

Column 1 – PSLF bus number

Column 2 – PSLF bus name

Column 3 – Base kV

Column 4 – Generating Unit 2-character PSLF ID

Column 5 – Generating unit status 1=on-line, 0=offline

Column 6 – Generation unit MWs prior to an event

Column 7 – Generating unit MVARs prior to an event

Column 8 – Governor response B=baseload flag is set to 1, R=responsive and baseload flag is set to 0, <Blank>= baseload flag is unchanged from the template powerflow

“PPMVa_RunValidation_v1b.p”

Purpose:

- Perform play-in simulation of a disturbance event

Pre-requisites:

- a powerflow file with initial conditions matching those during the event (e.g. “GAS-2010-09-27-1450.sav”)

- a disturbance data file compatible with play-in format (e.g. “pmu-GAS-2010-09-27-1450.csv”)

- dynamic data file with a power plant model (e.g. “GAS.dyd”)

Result:

- channel file with disturbance data (e.g. “GAS-2010-09-27-1450.chf”)

Steps:

- Run epcl “PPMVa_RunValidation_v1b.p”

The settings from the previous run are saved in the file the configuration file “PPMVa_RunValidation_v1b.ini”. The settings will show up as defaults in the dialog box. To clear the entrées, click on “Cancel”

- Select a powerflow file matching a disturbance event

- Select a disturbance data file

- Select a dynamic data file with a power plant model

- Enter a channel file name

The information flow is shown in Figure below:

Epcl “PPMVa_RunValidation_v1b.p” performs disturbance simulations. Use PSLF plot program to display the simulation results and to compare the model with the actuals.

Plot program is used to compare the simulations with the actual recordings.