## Sheet1
WECC Interconnection Daily Status Report
Date: | 2024-07-26
Weather Information For RC Centers
|  | Folsom, CA |  | Calgary, AB |  | Vancouver, BC | Little Rock, AR
High: |  | 99.6 |  | 75.4 |  | 67.8 | 75.1
Low: |  | 65.7 |  | 45.5 |  | 54 | 68.8
Conditions: |  | Sunny |  | Sunny |  | Sunny | Moderate rain
Forecasted Simultaneous Peaks, Reserves and Generation Limitations
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Forecasted Reserves |  | Req. Reserves | Total Gen Outages
NW |  | 75680.6031 | 17 | 8977.9558 |  | 4919.2392 | 21747.7
Includes AESO, AVA, AVRN, BANC, BCHA, BPA, CHPD, DOPD, GCPD, GRID, GWA, IPCO, NVE, NWMT, PACE, PACW, PGE, PSCO, PSEI, SCL, TID, TPWR, WACM, WAUW & WWA
DSW |  | 24319.859 | 17 | 2083 |  | 1580.7908 | 8256.14
Includes AZPS, DEAA, EPE, GRIF, HARQ, IID, PNM, SRP, TEPC & WALC
CAMX* |  | 47140.8931 | 19 | 4567.91 |  | 3263.91 | 14470.31
Includes CFE, CISO & LDWP
WI TOTAL |  | 146266.6286 | 18 | 15719.078 |  | 8821.89 | 42954.15
Yesterday's Actual Simultaneous Peaks and Reserves
by Reserve Sharing Group (RSG) * BA's in California and Mexico that are not participants in an RSG
Area |  | Peak Load | Time | Actual Reserves
NWPP RSG |  | 80480 | 16 | 18086
SRSG |  | 26288 | 16 | 3855
CAMX* |  | 53238 | 17 | 5713
WI TOTAL |  | 159731 | 17 | 26336
WECC PATH LIMITATIONS
PATH NAME |  |  | Dir | Seasonal OTC |  | Path Limitations* | ETR
Path 1: (Alberta-BCHA) |  |  | E>W | 1000 MW |  | 1000 MW
|  |  | W>E | 1200 MW |  | 850 MW
Path 3: (PNW-BCHA) |  |  | N>S | 3150 MW |  | 2400 MW
|  |  | S>N | 3000 MW
Path 8: (Montana-PNW) |  |  | E>W | 2200 MW
|  |  | W>E | 1350 MW
Path 14: (Idaho-PNW) |  |  | E>W | 2400 MW
|  |  | W>E | 1200 MW
Path 15: (Midway-Los Banos) |  |  | N>S | 3265 MW
|  |  | S>N | 5400 MW
Path 26: (Northern-Southern California) |  |  | N>S | 4000 MW
|  |  | S>N | 3000 MW
Path 31: (TOT 2A) |  |  | N>S | 690 MW *
|  |  | S>N | not defined
Path 35: (TOT 2C) |  |  | N>S | 400 MW
|  |  | S>N | 580 MW
Path 46: (West Of River) |  |  | E>W | 11200 MW
|  |  | W>E | not rated
Path 49: (East Of River) |  |  | E>W | 10100 MW *
|  |  | W>E | not rated
Path 65: (Pacific DC Intertie) |  |  | N>S | 3210 MW
|  |  | S>N | 2200 MW
Path 66: (California- Oregon Intertie) |  |  | N>S | 4800 MW
|  |  | S>N | 3675 MW
Path 78: (TOT 2B1) |  |  | N>S | 625 MW
|  |  | S>N | 650 MW
Path 79: (TOT 2B2) |  |  | N>S | 250 MW
|  |  | S>N | 300 MW
*The individual OASIS sites should be consulted for exact times and path limits
Recent Unscheduled Flow (USF) Activity (previous 24 hours =>Level 4 Only):
WECC Reliability Coordinator
Date | Balancing Authority or Path Operator | Flowgate or Qualifying Path |  | Highest Level | Duration

## Map
Weather Information
Calgary, AB
High (F) | 75.4
Low (F) | 45.5
Sunny |  | 75680.6031 | 83.45% | 83.45% | 16.55% | 75,681 MW
|  | 24319.859 | 82.08% | 82.08% | 17.92% | 24,320 MW
Vancouver, WA |  | 11349 | 87.12% | 87.12% | 12.88% | 11,349 MW
High (F) | 82.6 | 47140.8931 | 76.78% | 76.78% | 23.22% | 47,141 MW
Low (F) | 47.6
Sunny
Billings, MT
High (F) | 90.1
Low (F) | 60.9
Patchy rain nearby
Loveland, CO
High (F) | 89.2
Low (F) | 63.4
Patchy rain nearby
Los Angeles, CA
High (F) | 79.5
Low (F) | 68.7
Sunny
Phoenix, AZ
High (F) | 105.5
Low (F) | 85
Patchy rain nearby
Salt Lake City, UT
High (F) | 90.4
Low (F) | 62.7
Patchy rain nearby
2020-04-26
2020-04-22
2020-04-23
2020-04-25
2020-04-25
75,681 MW
24,320 MW
47,141 MW
Left Bar: Represents required reserve
Right bar: Represents today's forecasted reserve
Pie represents today's forecasted load as a percentage of seasonal peak load
Represents today's projected peak load
Diagram Legend