## Question 1
1. Do you agree with the Drafting Team's language used in the addition of D.B.15. in the WECC Variance of the NERC Standard. Yes/No with a narrative explanation
Name | Organization | Comment
Kevin Conway | Western Power Pool | Yes, The WPP supports the language use in the addition of D.B.15 in the WECC Variance of the NERC Standard.
Casey Perry | TXNM Energy | Yes, PNM agrees with D.B.15.
Curtis Crews | WECC | Yes, The proposed change provides the proper incentive and guidance for a PC to develop Corrective Action Plans to support reliability when the UFLS program is not meeting performance criteria.
Cain Braveheart | Bonneville Power Administration | Yes, with the exception of the one suggested edit. Bonneville Power Administration (BPA) recommends modifying language used in requirement M.D.B.15.; replace “conducts” with “participates in” to match existing language used in D.B.15.
Marcus Bortman | Arizona Public Service | Yes
Tim Kelly | SMUD | Yes. SMUD agrees with the D.B.15 language that has been added by the Drafting Team.
Adrian Andreoiu | BC Hydro | BC Hydro appreciates the opportunity to review and offers the following comments. BC Hydro is unable to support the proposed language at this time. Per the proposed D.B.15 wording, a PC must develop a Corrective Action Plan (CAP) and a schedule for implementation by the UFLS entities. “Corrective Action Plan” is defined in the NERC Glossary of Terms as, “a list of actions and an associated timetable for implementation to remedy a specific problem.” In this context, the additional “schedule for implementation” required specification appears to be redundant with little if any reliability benefits. BC Hydro suggests that developing an adequate CAP that appropriately addresses the specific issues identified is sufficient to improve reliability, and recommends that the “schedule for implementation” requirement can be deleted. Alternatively, if there is an identified need that a CAP must include specific UFLS entity required actions, that should be outlined separately based on a documented technical justification.
Jennie Wike | Tacoma Power | No. Tacoma Power recommends more delineation of responsibilities for mitigating deficiencies to align with the practice of the Western Interconnection. See responses to Question 2.

## Question 2
2.The failure of the WECC Off Nominal Frequency Plan can be due to either an inadequate plan, or to individual UFLS entities failing to adequately implement the plan. Should the requirement D.B.15 separately address the need for both of these aspects? •All PCs shall participate in the revision of the WECC Off Nominal Frequency Plan •Individual PCs shall develop CAPs to implement changes within their Planning Coordinator area if there are deficiencies within their PC area.Yes/No with a narrative explanation
Name | Organization | Comment
Kevin Conway | Western Power Pool | No, D.B. 15 should not separately address requiring PCs to participate to the revisions of the WECC Off-Nominal Frequency Plan AND the develop CAPs individually implement changes to their PC area if there are deficiencies in their area.
Casey Perry | TXNM Energy | Yes, PNM agrees that there needs to be more clarity between the Corrective Action Plans related to the WECC Off Nominal Plan for their PC Area.
Curtis Crews | WECC | No- The suggestion appears to be out of scope of the SAR. The language provided in D.B.15 provides for PC areas failing the performance criteria (as documented in a coordinated UFLS design assessment) to create Corrective Action Plans to mitigate the issues. Other issues, that may or may not be inherent to other parts of the variance would need another SAR to address the concerns.
Cain Braveheart | Bonneville Power Administration | Question 2, bullet 1: All PCs shall participate in the revision of the WECC Off Nominal Frequency Plan Response: It is BPA’s position that the existing D.B.1. requirement already captures this. Question 2, bullet 2: Individual PCs shall develop CAPs to implement changes within their Planning Coordinator area if there are deficiencies within their PC area. Yes/No with a narrative explanation Response: It is BPA’s position that revised D.B.15. adequately covers this.
Marcus Bortman | Arizona Public Service | Yes
Tim Kelly | SMUD | Yes. The clarification should be added so that it is clear that CAPs apply to PCs and PC areas that show deficiencies, and the other PCs just need to continue participating in the UFLS/CAP process even if they do not have any required actions in the CAPs. This language helps demonstrate that UFLS plans, assessments, and reports, and any CAPs are jointly coordinated between all PCs in WECC.
Adrian Andreoiu | BC Hydro | Yes. BC Hydro is in agreement that all PCs must participate in the revisions of the WECC Off Nominal Frequency Plan, and that each PC must develop CAPs for deficiencies within their PC area. However, the proposed revisions to the D.B. Variance do not seem to be conducive to achieving the objective that PCs shall participate in the WECC UFLS Plan’s revisions.
Jennie Wike | Tacoma Power | Yes, in order to implement the SAR, Tacoma Power recommends additional editing of D.B.15 to tailor the R15 requirement to the unique circumstance within the WECC region. Within the WECC interconnection there are two distinct responsibilities: 1) developing the interconnection wide plan as a shared responsibility among all PCs, and 2) implementing the shared plan within the PC’s footprint. Tacoma Power suggests this possible revision to DB.15.1 and a new DB.15.2 to differentiate between these two responsibilities: DB.15.1 Each Planning Coordinator that participates in a UFLS design assessment under Requirement D.B.4 or D.B.12 and determines that the UFLS program does not meet the performance characteristics in Requirement D.B.3, shall develop a Corrective Action Plan and a schedule for creating and adopting a revised UFLS program. [VRF: High][Time Horizon: Long-term Planning] D.B.15.1.1. For UFLS design assessments performed under Requirement D.B.4, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement D.B.4, D.B.15.1.2 For UFLS design assessments performed under Requirement D.B.12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement D.B.12 DB.15.2 Each Planning Coordinator that participates in a UFLS design assessment under Requirement D.B.4 or D.B.12 and determines that UFLS entities within their Planning Coordinator area does not meet the performance characteristics in Requirement D.B.3 shall develop a Corrective Action Plan and a schedule for implementation by the UFLS Entities within its area, and developed by entities within the time line D.B.15.2.1, D.B.15.2.2, D.B.15.2.3 D.B.15.2.1. For UFLS design assessments performed under Requirement D.B.4, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement D.B.4, D.B.15.2.2 For UFLS design assessments performed under Requirement D.B.12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement D.B.12 D.B.15.2.3 For newly adopted UFLS plans, the Corrective Action Plan shall be developed within 6 months of revision to the UFLS plan.

## Question 3
3. Do you have any other comments or suggestions that the drafting team may not have thought of or included in this document? Yes/No with a narrative explanation
Name | Organization | Comment
Kevin Conway | Western Power Pool | The Drafting Team has done a good job staying within the bounds of the SAR by only focusing on CAPs. Language consistent with the main standard for reporting will help to quickly resolve the needed changes without WECC looking overly prescriptive or adding unneeded requirements.
Casey Perry | TXNM Energy | Yes, PNM request an updated WECC variant of the PRC-006 RSAW. The current WECC variant is embedded in the PRC-006-2 RSAW when PRC-006-5 is in effect. Request the PRC-006-6 RSAW include the WECC variant.
Curtis Crews | WECC | Yes- Header on Page 1 indicates PRC-006-6. Should that be PRC-006-5 ? If not remainder of document headers need changed to PRC-006-6. M.D.B15. language should change “conducts” to “participates” to match D.B.15. Requirement language. Suggest adding a period at the end of D.B.15 (i.e., “…..within its area.”) and at the end of M.D.B.15. (i.e., “….D.B.15.2.”).
Cain Braveheart | Bonneville Power Administration | BPA appreciates the efforts of the drafting team with no further suggested edits or revisions.
Marcus Bortman | Arizona Public Service | Yes – AZPS would like more clarification on how an individual PC, that needs to perform a CAP, will be identified. Also, if a CAP needs to be developed, will that require a re-study to determine whether or not the CAP is sufficient?
Tim Kelly | SMUD | SMUD has no other comments.
Adrian Andreoiu | BC Hydro | BC Hydro noted that the Requirement R15 uses the same language, and the associated R15 rationale in Appendix 1, clarifies that R15 was “in response to the directive from FERC Order No. 763, which raised concern that the standard failed to specify how soon an entity would need to implement corrections after a deficiency is identified by a PC assessment.” An argument can be made that having a CAP and a schedule for implementation does not meet the FERC Order, as the Standard still does not specify the timeline to implement corrections. Beyond the deadline for CAP development, there is no limitation as to how long its implementation can take.
Jennie Wike | Tacoma Power | Yes. The language in M.D.B.15 needs to be adjusted to match the language in D.B.15. Within WECC, each planning coordinator “participates” rather than “conducts” a UFLS assessment. The requirements in D.B.12 lack clarity as to whether all PCs must participate in a study if any single PC identifies a deficiency in WECC plan. Revising D.B.12 as shown would make it clear that all entities must participate: Proposed D.B.12: If any Planning Coordinator identifies UFLS program deficiencies per D.B.11, each Planning Coordinator shall participate in and document a coordinated UFLS design assessment of the UFLS program to consider the identified deficiencies within two years of event actuation.

## Additional Comments
Additional Comments Outside of Questions Asked
Name | Organization | Comment
Kevin Conway | Western Power Pool
Casey Perry | TXNM Energy
Curtis Crews | WECC
Cain Braveheart | Bonneville Power Administration
Marcus Bortman | Arizona Public Service
Tim Kelly | SMUD
Adrian Andreoiu | BC Hydro
Jennie Wike | Tacoma Power

## Kevin Conway
Submitted on Tue, 10/14/2025 - 15:27
Name
Kevin Conway
Organization(s):
Western Power Pool
Email address:
kevin.conway@westernpowerpool.org
Standards Project you are commenting on:
WECC-0157: PRC-006-5 Automatic Underfrequency Load Shedding, Update to the WECC Regional Variance
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
Yes, The WPP supports the language use in the addition of D.B.15 in the WECC Variance of the NERC Standard.
Response to question 2 (if applicable):
No, D.B. 15 should not separately address requiring PCs to participate to the revisions of the WECC Off-Nominal Frequency Plan AND the develop CAPs individually implement changes to their PC area if there are deficiencies in their area.
Response to question 3 (if applicable):
The Drafting Team has done a good job staying within the bounds of the SAR by only focusing on CAPs. Language consistent with the main standard for reporting will help to quickly resolve the needed changes without WECC looking overly prescriptive or adding unneeded requirements.

## Casey Perry
Submitted on Wed, 10/15/2025 - 15:50
Name
Casey Perry
Organization(s):
TXNM Energy
Email address:
casey.perry@txnmenergy.com
Standards Project you are commenting on:
WECC-0157: PRC-006-5 Automatic Underfrequency Load Shedding, Update to the WECC Regional Variance
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
Yes, PNM agrees with D.B.15.
Response to question 2 (if applicable):
Yes, PNM agrees that there needs to be more clarity between the Corrective Action Plans related to the WECC Off Nominal Plan for their PC Area.
Response to question 3 (if applicable):
Yes, PNM request an updated WECC variant of the PRC-006 RSAW. The current WECC variant is embedded in the PRC-006-2 RSAW when PRC-006-5 is in effect. Request the PRC-006-6 RSAW include the WECC variant.

## Curtis Crews
Submitted on Tue, 10/28/2025 - 09:40
Name
Curtis Crews
Organization(s):
WECC
Email address:
ccrews@wecc.org
Standards Project you are commenting on:
WECC-0157: PRC-006-5 Automatic Underfrequency Load Shedding, Update to the WECC Regional Variance
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
Yes, The proposed change provides the proper incentive and guidance for a PC to develop Corrective Action Plans to support reliability when the UFLS program is not meeting performance criteria.
Response to question 2 (if applicable):
No- The suggestion appears to be out of scope of the SAR. The language provided in D.B.15 provides for PC areas failing the performance criteria (as documented in a coordinated UFLS design assessment) to create Corrective Action Plans to mitigate the issues. Other issues, that may or may not be inherent to other parts of the variance would need another SAR to address the concerns.
Response to question 3 (if applicable):
Yes- Header on Page 1 indicates PRC-006-6. Should that be PRC-006-5 ? If not remainder of document headers need changed to PRC-006-6.
M.D.B15. language should change “conducts” to “participates” to match D.B.15. Requirement language.
Suggest adding a period at the end of D.B.15 (i.e., “…..within its area.”) and at the end of M.D.B.15. (i.e., “….D.B.15.2.”).

## Cain Braveheart
Submitted on Tue, 10/28/2025 - 09:41
Name
Cain Braveheart
Organization(s):
Bonneville Power Administration
Email address:
rcbraveheart@bpa.gov
Standards Project you are commenting on:
WECC-0157: PRC-006-5 Automatic Underfrequency Load Shedding, Update to the WECC Regional Variance
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
Yes, with the exception of the one suggested edit. Bonneville Power Administration (BPA) recommends modifying language used in requirement M.D.B.15.; replace “conducts” with “participates in” to match existing language used in D.B.15.
Response to question 2 (if applicable):
Question 2, bullet 1: All PCs shall participate in the revision of the WECC Off Nominal Frequency Plan
Response: It is BPA’s position that the existing D.B.1. requirement already captures this.
Question 2, bullet 2: Individual PCs shall develop CAPs to implement changes within their Planning Coordinator area if there are deficiencies within their PC area. Yes/No with a narrative explanation
Response: It is BPA’s position that revised D.B.15. adequately covers this.
Response to question 3 (if applicable):
BPA appreciates the efforts of the drafting team with no further suggested edits or revisions.

## Marcus Bortman
Submitted on Thu, 10/30/2025 - 13:24
Name
Marcus Bortman
Organization(s):
Arizona Public Service
Email address:
marcus.bortman@aps.com
Standards Project you are commenting on:
​WECC-0155: PRC-006-WECC-CRT-4, Underfrequency Load Shedding
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
Yes
Response to question 2 (if applicable):
Yes
Response to question 3 (if applicable):
Yes –
AZPS would like more clarification on how an individual PC, that needs to perform a CAP, will be identified.
Also, if a CAP needs to be developed, will that require a re-study to determine whether or not the CAP is sufficient?

## Tim Kelley
Submitted on Thu, 10/30/2025 - 16:20
Name
Tim Kelley
Organization(s):
SMUD
Email address:
tim.kelley@smud.org
Standards Project you are commenting on:
WECC-0157: PRC-006-5 Automatic Underfrequency Load Shedding, Update to the WECC Regional Variance
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
Yes. SMUD agrees with the D.B.15 language that has been added by the Drafting Team.
Response to question 2 (if applicable):
Yes. The clarification should be added so that it is clear that CAPs apply to PCs and PC areas that show deficiencies, and the other PCs just need to continue participating in the UFLS/CAP process even if they do not have any required actions in the CAPs. This language helps demonstrate that UFLS plans, assessments, and reports, and any CAPs are jointly coordinated between all PCs in WECC.
Response to question 3 (if applicable):
SMUD has no other comments.

## Adrian Andreoiu
Submitted on Thu, 10/30/2025 - 18:13
Name
Adrian Andreoiu
Organization(s):
BC Hydro
Email address:
adrian.andreoiu@bchydro.com
Standards Project you are commenting on:
WECC-0157: PRC-006-5 Automatic Underfrequency Load Shedding, Update to the WECC Regional Variance
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
1. Do you agree with the Drafting Team's language used in the addition of D.B.15. in the WECC Variance of the NERC Standard. Yes/No with a narrative explanation
Narrative Explanation
BC Hydro appreciates the opportunity to review and offers the following comments.
BC Hydro is unable to support the proposed language at this time. Per the proposed D.B.15 wording, a PC must develop a Corrective Action Plan (CAP) and a schedule for implementation by the UFLS entities. “Corrective Action Plan” is defined in the NERC Glossary of Terms as, “a list of actions and an associated timetable for implementation to remedy a specific problem.” In this context, the additional “schedule for implementation” required specification appears to be redundant with little if any reliability benefits.
BC Hydro suggests that developing an adequate CAP that appropriately addresses the specific issues identified is sufficient to improve reliability, and recommends that the “schedule for implementation” requirement can be deleted. Alternatively, if there is an identified need that a CAP must include specific UFLS entity required actions, that should be outlined separately based on a documented technical justification.
Response to question 2 (if applicable):
2. The failure of the WECC Off Nominal Frequency Plan can be due to either an inadequate plan, or to individual UFLS entities failing to adequately implement the plan. Should the requirement D.B.15 separately address the need for both of these aspects?
• All PCs shall to participate in the revision of the WECC Off Nominal Frequency Plan
• Individual PCs shall develop CAPs to implement changes within their Planning Coordinator area if there are deficiencies within their PC area. Yes/No with a narrative explanation
Narrative Explanation
Yes. BC Hydro is in agreement that all PCs must participate in the revisions of the WECC Off Nominal Frequency Plan, and that each PC must develop CAPs for deficiencies within their PC area.
However, the proposed revisions to the D.B. Variance do not seem to be conducive to achieving the objective that PCs shall participate in the WECC UFLS Plan’s revisions.
Response to question 3 (if applicable):
3. Do you have any other comments or suggestions that the drafting team may not have thought of or included in this document?
BC Hydro noted that the Requirement R15 uses the same language, and the associated R15 rationale in Appendix 1, clarifies that R15 was “in response to the directive from FERC Order No. 763, which raised concern that the standard failed to specify how soon an entity would need to implement corrections after a deficiency is identified by a PC assessment.” An argument can be made that having a CAP and a schedule for implementation does not meet the FERC Order, as the Standard still does not specify the timeline to implement corrections. Beyond the deadline for CAP development, there is no limitation as to how long its implementation can take.

## Jennie Wike
Submitted on Fri, 10/31/2025 - 22:39
Name
Jennie Wike
Organization(s):
Tacoma Power
Email address:
jwike@tacoma.gov
Standards Project you are commenting on:
WECC-0157: PRC-006-5 Automatic Underfrequency Load Shedding, Update to the WECC Regional Variance
Comment period:
Posting 1 for Comment
Response to question 1 (if applicable):
No. Tacoma Power recommends more delineation of responsibilities for mitigating deficiencies to align with the practice of the Western Interconnection. See responses to Question 2.
Response to question 2 (if applicable):
Yes, in order to implement the SAR, Tacoma Power recommends additional editing of D.B.15 to tailor the R15 requirement to the unique circumstance within the WECC region. Within the WECC interconnection there are two distinct responsibilities: 1) developing the interconnection wide plan as a shared responsibility among all PCs, and 2) implementing the shared plan within the PC’s footprint. Tacoma Power suggests this possible revision to DB.15.1 and a new DB.15.2 to differentiate between these two responsibilities:
DB.15.1 Each Planning Coordinator that participates in a UFLS design assessment under Requirement D.B.4 or D.B.12 and determines that the UFLS program does not meet the performance characteristics in Requirement D.B.3, shall develop a Corrective Action Plan and a schedule for creating and adopting a revised UFLS program. [VRF: High][Time Horizon: Long-term Planning]
D.B.15.1.1. For UFLS design assessments performed under Requirement D.B.4, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement D.B.4,
D.B.15.1.2 For UFLS design assessments performed under Requirement D.B.12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement D.B.12
DB.15.2 Each Planning Coordinator that participates in a UFLS design assessment under Requirement D.B.4 or D.B.12 and determines that UFLS entities within their Planning Coordinator area does not meet the performance characteristics in Requirement D.B.3 shall develop a Corrective Action Plan and a schedule for implementation by the UFLS Entities within its area, and developed by entities within the time line D.B.15.2.1, D.B.15.2.2, D.B.15.2.3
D.B.15.2.1. For UFLS design assessments performed under Requirement D.B.4, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement D.B.4,
D.B.15.2.2 For UFLS design assessments performed under Requirement D.B.12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement D.B.12
D.B.15.2.3 For newly adopted UFLS plans, the Corrective Action Plan shall be developed within 6 months of revision to the UFLS plan.
Response to question 3 (if applicable):
Yes. The language in M.D.B.15 needs to be adjusted to match the language in D.B.15. Within WECC, each planning coordinator “participates” rather than “conducts” a UFLS assessment.
The requirements in D.B.12 lack clarity as to whether all PCs must participate in a study if any single PC identifies a deficiency in WECC plan. Revising D.B.12 as shown would make it clear that all entities must participate:
Proposed D.B.12: If any Planning Coordinator identifies UFLS program deficiencies per D.B.11, each Planning Coordinator shall participate in and document a coordinated UFLS design assessment of the UFLS program to consider the identified deficiencies within two years of event actuation.