## Slide 1: Protection System Operations
Correct operation of a Protection System clearing a fault
Correct operation of a Protection System during certain abnormal conditions
  Swings
  Generator loss of field
  Not for control operations
Unintended operation of a Protection System
Failure of a Protection System to operate for a fault within its intended coverage

## Slide 2: Protection System
Protection Systems are to be analyzed as Composite Protection Systems
  Partial failures within a Composite Protection System that correctly clears a fault within its intended coverage do not constitute misoperations
  The Composite Protection System of a transmission line include all equipment used to clear faults on that line. Equipment located at all terminals comprise one Composite Protection System.

## Slide 3: Examples
A permanent fault occurs on Line A. Both end trip and reclose to Lockout: one operation
Line A
Line B
Line C
Line D

## Slide 4: Examples
Permanent fault occurs on Line B. Line B breakers trip correctly, but a breaker on Line C trips incorrectly. 2 operations, one correct, one misoperation.
Line A
Line B
Line C
Line D

## Slide 5: Examples
A breaker on Line D trips due to a failed relay with no fault. One Misoperation.
Line A
Line B
Line C
Line D

## Slide 6: Breaker Failure Example A
Three Correct Operations
Line A
Line B
Line C
Line D

## Slide 7: Breaker Failure Example B
115kV Bus 1
115kV Bus 2
Transmission Lines
Generator
500kV
Generator
35 Miles
Three Correct Operations
Remote Line
Protection trips

## Slide 8: Breaker Failure Example C
115kV Bus 1
115kV Bus 2
Transmission Lines
Generator
500kV
Generator
35 Miles
Two Correct Operations
BF relaying transfer trips
remote line terminal

## Slide 9: Questions?